## RMW Report- All
Tracking # | Region | Community | Trip Completed By | Start | End | Trip Type | Transportation Cost | Per Diem Cost | In-Kind Contribution | Type of In-Kind | Mode of Transportation | Personal Vehicle | Mileage | Trip Contact 1 | Trip Contact 2 | Trip Contact #3 | Trip Contact #4 | Trip Contact #5 | Trip Contact #6 | Trip Contact #7 | Trip Contact #8 | Trip Contact #9 | Trip Contact #10 | Purpose | Trip Summary | On the job Training Hours Provided | Critical Observations 1 | Critical Observations 2 | Critical Observations 3 | Critical Observations 4 | Critical Observations 5 | Noted Deficiencies 1 | Reoccurring? | Noted Deficiencies 2 | Reoccurring? | Noted Deficiencies 3 | Reoccurring? | Noted Deficiencies 4 | Reoccurring? | Noted Deficiencies 5 | Reoccurring? | Recommended Follow Up Activities | Entity to Follow Up | Recommended Follow Up Activities | Entity to Follow Up | Recommended Follow Up Activities | Entity to Follow Up | Recommended Follow Up Activities | Entity to Follow Up | Recommended Follow Up Activities | Entity to Follow Up | Other Information | Attachments | OASys Documents | Submitted
RMWTR-1290 | MHC | Kiana | Jeff Luther | 2016-07-07 | 2016-07-08 | Routine | $180 | $114 |  |  |  | No |  | Name: Richard Teel Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Darold Title/Position: Other Accompanied By? No Telephonic Contact? No | Name: Brandon Title/Position: Other Accompanied By? No Telephonic Contact? No | Name: Seth Title/Position: Other Accompanied By? No Telephonic Contact? No | [6 empty] | Water Storage Tank cleaning | Cleaned Water Storage tank, used bypass line to keep us from losing water pressure in town. | 5 | none |  |  |  |  | none | No |  | No |  | No |  | No |  | No | fill water tank back up & disinfect | Operator | [9 empty] | N/A | Other Documents | 2016-07-12 16:24
RMWTR-1291 | DEC | Gulkana | Floyd Murphy | 2016-07-05 | 2016-07-08 | Routine |  |  |  |  | Company Truck | No |  | Name: John Dys Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Angelia Vermillion Title/Position: Tribal Administrator Accompanied By? No Telephonic Contact? No | [8 empty] | Assist operator with seperating fuel line for the Emergency Generator and boiler. Work with operator on the MIEX operation and maintenance. | 7/5/16 I departed anchorage for Gulkana at 730 am, arriving in Gulkana at noon. I stopped and had lunch. 1 pm I stopped by the tribal office and met with the Tribal Administrator, Angelia Vermillion. I informed her my plant to train the water plant operator on plumbing the fuel lines for the boilers and the emergency generator. Angelia and I discussed the Best Practice Scoring and Preventative maintenance plan and forms for the operator to fill out to increase the Best Practice scores. I met John Dye at the water treatment plant. We discussed the best way to make the fuel line separation for the emergency generator and boiler. After several ideas we settled on black iron pipe to separate the piping. John had been having problems with a light switch in the water plant overhead lighting. He was not comfortable working on electricity to make the necessary repairs, I showed John that on the light switch that the breaker panel and breaker numbers were on the switch cover. The panel was located, breaker shut off and the bad light switch was disconnected and removed. The new light switch was installed and cover replaced. The breaker was turned back on and the lights tested. They worked as they should. After completing this project we went through the Operation and Maintenance Manual for the Water Treatment Plant created by ANTHC June 2013. The manual is on hard copy along with along with a computer disc copy from ANTHC. John needs to fill out the Gulkana Water Treatment Operations form along with the Gulkana Treatment Plant Daily Operations Check Sheet, The ADEC Water Report form along with the monthly operating record. At the beginning of the following month a copy of the ADEC Water report form should be sent to ADEC. A copy of the ADEC and monthly reporting forms and completed Preventative Maintenance forms given to Angelia Vermillion, Tribal Administrator along with sending copies sent to the Remote Maintenance Worker, electronically to floyd.murphy@alaska.gov or Fax 269-7509 Attn: Floyd Murphy. Look over the Watering Monitoring Summary and see what additional testing is required for the month, call your laboratory if additional testing is needed. Set up a Sanitary Survey when required 7/6 - 8/16 Make measurements for pipe to be cut to length for instillation for the dedicated fuel line to the emergency generator. Dismantle existing fuel supply line from the emergency generator and boilers. Reassemble boiler fuel line. Get pipe cut for dedicated fuel line to the emergency generator. We were unable to locate a 3 inch to ½ inch fitting to install the new line for the emergency generator, so we made a hole in the 3 inch fitting to insert the fuel line into the tank. After this was accomplished we silicone the pipe so moisture wouldn’t be allowed into the tank through the hole for the pipe. John should apply more sealant on the fitting when the initial application dries. I departed Gulkana at 10 am arriving in Anchorage around 2:00 PM. | 16 | None at this time |  |  |  |  | None at this time | No |  | No |  | No |  | No |  | No | Observe the emergency generator upon filling of the day tank to make sure it doesnt leak or draw air upon filling day tank. | Operator | Make copies of monthly reports and logs for the Tribal Administrator and Sent copies to the RMW electronically at foyd.murphy@alaska.gov Send ADEC copies to ADEC befor the 10th of each month. | [8 empty] | Attachments | Other Documents | 2016-07-19 14:57
RMWTR-1293 | TCC | Circle | Fred Kameroff | 2016-07-07 | 2016-07-07 | Routine | [5 empty] | No |  | Name: Jesscia fields Title/Position: Tribal President Accompanied By? No Telephonic Contact? No | Name: anjela Ludwick Title/Position: Tribal Administrator Accompanied By? No Telephonic Contact? No | Name: Lawrence Crow Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: dennis carroll Title/Position: Other Accompanied By? No Telephonic Contact? No | Name: Wes shales Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | [5 empty] | We arrived at Circle at 11:30 am and met with Mrs. Jessica Fields at the tribal hall. Mrs. Fields than contacted Mr. Lawrence Crow Jr of our arrival. Mrs. Fields also asked me to check on the dryers to see what was wrong with them. Mr. Lawrence Crow Jr came by and he and Mr. Wes Shales started to remove the old toilet while I install the new utility sink. The new toilet I brought up was not the right type needed for Circle washsetria, but Mr. Crow and Mr. Shales used the top half and installed it in the old toilet and made it work. Once the work was done on the toilet and the utility sink I turned to the dryers and found three of the four dryers the rollers for the drum were worn out, and one with no heat. Mr. Crow did not have any parts on hand to make the repairs. | Parts are ordered for the dryers, once Mr. Crow receives them I will make another trip up to Circle to make the repairs. I contacted Frontier plumbing and told them the bottom half of the toilet was wrong type and asked if I can return it and they said I can as long as it was not used and still have the receipt. | 4 | dryers are in need of repair |  |  |  |  | none | No |  | No |  | No |  | No |  | No | water operator and RMW | RMW | [9 empty] | N/A | Other Documents | 2016-07-11 15:07
RMWTR-1294 | DEC | Yakutat | Kevin Schoneman | 2016-07-05 | 2016-07-08 | Routine |  |  |  |  | Air | No |  | Name: Ron Beatty Title/Position: Public Works Director Accompanied By? No Telephonic Contact? No | Name: Samson Demmert Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Michael Jensen Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Ronda Coston Title/Position: City Official Accompanied By? No Telephonic Contact? No | Name: John Erickson Title/Position: City Manager Accompanied By? No Telephonic Contact? No | Name: Gary Greenburg Title/Position: Consultant Accompanied By? No Telephonic Contact? No |  |  |  |  | To work with the WWT Operator on compliance and reporting, assist with new chemical injection equipment and new lift station control panel installation. | I arrived in Yakutat 1130 Tuesday July 5, I was met at the airport by Public Works Director Ron Beattie, we then drove to the Public Works Office/ Planning Department. Ron had arranged to have Water and Waste Water Operator, Samson Demmert meet us at the office. Also at the office at the office was City Planner, Ronda Coston and Gary Greensburg with Akmapco. The city is currently working on a project that would map all of the utilities in the City and Borough. Samson and I started working on the Discharge Monitoring Reports we spent the rest of the afternoon reviewing several months of wastewater laboratory results and applying those results. Ron Beattie arrived back at the Public Works Office he and I headed out to the old FAA complex near the airport in Yakutat. We looked at the old FAA waste water lagoon. The lagoon is approximately one half of an acre equipped with a submerged aeration distribution system. We then after a tour of the lagoon headed back to the Public Works Department. The next day Wednesday I met Samson at the public works department and we began his usual daily rounds. We first headed to the Water Treatment Plant for chlorine residual check and collect data readings. We then headed to the waste water treatment plant and started with the daily tasks there such as cleaning the rotating screening equipment and collection totes, checking the chemical injection pumps and mixing the chemical batches. We then started the daily sewage lift station checks and rounds we began visiting each lift station checking the panel status, pumps and wet well levels. The last lift station visited was the Jensen lift station, when we arrived we noticed one of the pumps was tripped out on a overload condition. Samson explained that this lift station receives flow from both the city and the fish processing plant. We decide to go back to the wastewater plant and pick up supplies and the city sewage vacuum truck and then headed back to the lift station. For several hours we began removing the accumulated solids from the collection well, pumping the sludge out with the vacuum truck and then allowing liquids to refill the station. We repeated this several times until we felt that we had removed a majority of the sludge. We then put the lift station back into service. We then headed back to the public works office to talk to Ron about what we had found and what we had done. We then talked about possible solutions and options to help resolve the continued pump malfunctions and interrupted station service. Ron mentioned they had a replacement electrical control panel in his inventory. After much discussion we decided that the next day we would install the new panel. We then went over the new preventative maintenance program and the checklist for the operators to add to and fill out each day. We talked about modifying the preventative maintenance report form to custom fit the needs and equipment in Yakutat. The next morning I met with Ron and Samson back at the public works department, and Samson and I headed back to the Jensen lift station to begin with the replacement of the control panel. Ron also had arranged for the Assistant Public Works Director, Michael Jensen to work with us on the panel replacement. After several hours of removing the old panel and installing the new control panel,we also decide to check voltages of the incoming utility power during the start up process. We noticed that some of the readings we were getting seemed to be sporadic and somewhat uneven. Ron decided to call the crew at the power plant to ask about replacement fuses and the possibility of them checking the incoming power. Three of the power utility employees arrived at the lift station and began checking the utility meter base and the incoming power. After about one half hour of meter checks and opening the meter base they discovered that some of the internal components in the meter base had corrosion issues. After cleaning some of the terminals and tightening the lugs. We put the lift station back into full service. We watched the station cycle through several times and called it a day. The next morning I met with Samson and Ron at the public works shop, from there Samson and I went and checked on the Jensen lift station. Everything was operating normally. Ron Beatty and I decided to go to the City Offices to meet with the Borough Manager, Jon Erickson. We talked about the progress that was made during the work week. Ron and I headed to the airport for my departure. | 8 | None Noted |  |  |  |  | None Noted | No |  | No |  | No |  | No |  | No | Have either the electrical power utility or a electrician check the meter bases and supply power at all the lift stations, waste water plant and water treatment plant. | Engineer | [9 empty] | Attachments | Other Documents | 2016-07-27 10:00
RMWTR-1299 | MHC | Kivalina | Jeff Luther | 2016-07-18 | 2016-07-18 | Routine | $324 |  |  |  |  | No |  | Name: Joseph Swan Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Dennis Swan Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: Janet Mitchell Title/Position: City Administrator Accompanied By? No Telephonic Contact? No | [7 empty] | Inspect/Clean Raw Water Storage Tank & treated water tank | As I arrived, Joe picked me up & brought me over to the Raw water storage tank which he had draining for a while now to get the water level below the access door, after that was done we opened up the raw tank & there was just a very thin hairline layer of silt from the river, the operators had decided to wait another 2-3 years for more build up to clean the raw water storage tank, so we went over to the treated water tank(which was being emptied by customers) & open that up, it appeared to be very clean & we decided it didn't need to be cleaned. I went over to the city office to tell the administrator Janet the good news, she was very happy to hear that her tanks did not have to be cleaned. | 1 | none |  |  |  |  | none | No |  | No |  | No |  | No |  | No | none | Unknown | [9 empty] | N/A | Other Documents | 2016-07-19 08:14
RMWTR-1300 | DEC | Port Graham | Steve Evavold | 2016-07-13 | 2016-07-13 | Routine | $525 |  |  |  |  | No |  | Name: Patrick Norman First Chief Title/Position: Accompanied By? No Telephonic Contact? No | Name: Francis Norman Tribal Administrator Title/Position: Accompanied By? No Telephonic Contact? No | Name: Vivian Malchoff City Clerk Title/Position: Accompanied By? No Telephonic Contact? No | Name: Sean Driskill ANTHC Project Mgr. Title/Position: Accompanied By? No Telephonic Contact? No | Name: Brad Bigelow ANTHC Constr. Mgr. Title/Position: Accompanied By? No Telephonic Contact? No | Name: Chuck McCloskey ANTHC Constr. Super Title/Position: Accompanied By? No Telephonic Contact? No | Name: Ben Chadwick ANTHC Design PE Title/Position: Accompanied By? No Telephonic Contact? No | Name: Wes Breedlove WTP Operator Title/Position: Accompanied By? No Telephonic Contact? No |  |  | To assist with community familiarization, introductions, and discuss needed projects. The current funding is for replacement of the communities 11 hydrants and water/sewer service connections via the ANTHC's scattered sites program. | The group arrived and met with Fran and Patrick in the community center to go over plans and hydrant locations. We inspected the distribution system and the hydrants to be replaced. Most of the hydrants will need extensions and/or mechanical joints on installation. Missing bolts and gaskets for the existing new hydrants on a pallet were discovered. Two other projects were discussed; outfall consolidation, and a new septage lagoon. We drove to those sites for comment. The water plant upgrade project included a new polymer feed assembly, IFE turbidimeters, plumbing, tubing, and valves. The warrantee period ending so a final inspection was completed with Wes, the operator. Wes said he was having a problem with one of the "Step" Eone residential lift stations installed and may need assistance in resolving an alarm issue. | 0 | Nothing noted this trip. |  |  |  |  | the 5 existing community septic tanks are collapsing and the outfall lines connected to them are separating and causing septage on the beaches until "Band aid" repairs are made. The solids lagoon is past it's life expectancy and needs to be retired for a new lagoon to be constructed. | Yes |  | No |  | No |  | No |  | No | A trip should be scheduled this fall to assist operator with a lift station issue, condition assessment of community's pumper truck, and outfall inspection. | RMW | [9 empty] | Attachments | Other Documents | 2016-07-22 10:00
RMWTR-1301 | DEC | Nanwalek | Steve Evavold | 2016-07-13 | 2016-07-13 | Routine | $525 |  |  |  |  | No |  | Name: John Kvasnikoff IRA First Chief Title/Position: Accompanied By? No Telephonic Contact? No | Name: Jerry Demas IRA Utility Manager Title/Position: Accompanied By? No Telephonic Contact? No | Name: Wally Kvasnikoff IRA Council member Title/Position: Accompanied By? No Telephonic Contact? No | Name: Sean Driskill ANTHC PM Title/Position: Accompanied By? No Telephonic Contact? No | Name: Brad Bigelow ANTHC CM Title/Position: Accompanied By? No Telephonic Contact? No | Name: Chuck McClowsky ANTHC Job Super Title/Position: Accompanied By? No Telephonic Contact? No | Name: Ben Chadwick ANTHC Design Eng Title/Position: Accompanied By? No Telephonic Contact? No |  |  |  | Project familiarization and community introductions. | Arrived in Nanwalek after a short trip to Port Graham and met with John and Jerry at the Community Center. Introductions were made and we all set out to inspect the distribution system at sites where water and sewer services were to be connected, rerouted, or other. Another leak had been repaired recently and more are suspected. The distribution system has a large area with 2", 3", and 4" Schedule 40 PVC still in use. A large leak can drain the system and tanks in a short time. I was not able to meet with the water plant operator this trip. The reservoir water level remains low, but supply seems steady. One discussion topic was cleaning/enlarging the reservoir. Over the years erosion has reduced storage capacity by 25%. Before leaving I talked with John and Wally about returning with Kevin Schoneman, new RMW, and spending time in the plant. We also need to schedule a septic tank pumping when convenient. The new septic tanks, installed 2 years earlier, had not been pumped yet. | 0 | The reservoir has been reduced in capacity by erosion on the "Uphill" side of the impoundment. This needs to be addressed. |  |  |  |  | Nanwalek has always had eminent water shortage issues. This summer is already a concern. There are over 80 students in school this year, and an overall population of 275 people. The reservoir is undersized, and supply isn't consistent. | Yes |  | No |  | No |  | No |  | No | Another trip will be scheduled to work with RMW and operator before winter. | RMW | [9 empty] | Attachments | Other Documents | 2016-07-26 15:44
RMWTR-1302 | TCC | Circle | Fred Kameroff | 2016-07-19 | 2016-07-19 | Routine | [5 empty] | No |  | Name: Lawrence Crow Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Jessica Feilds Title/Position: Tribal President Accompanied By? No Telephonic Contact? No | [8 empty] | Check on hot water heater | Mr. Lawrence Crow Jr contacted me on 07/15/16 stating the hot water heater was tripping out and didn’t know why, I told him I could be there on 07/19/16 to diagnose the problem. I arrived at Circle on 07/19/16 and met Mr. Crow at the water plant. Mr. Crow stated that the hot water heater did not trip out this time and I told him I’m going to look at the burner unit. I then removed the drawer assembly and made adjustments to the electrodes and checked the other components. Once I was done inspecting the burner I reinstalled the drawer assembly and placed the heater back in service. Mr. Crow asked me to look at the Continental Girbau washer, I asked him what was wrong with it and he said he does not know, he then went to go get the manual from the tribal office and the keys to get it running. Once we looked at the code on the display settings we found the door had failed and would not lock once the machine was on. We then placed it out of service until we can get a new door lock assembly. Mr. Crow also said the speed queen washer was not taking any tokens and asked me to take a look at it. I removed the coin slide and made a little adjustment and reinstalled it and the washer was back in service. RECOMMENDATIONS/CONCLUSION I contacted automated laundry and talked with a service tech on the Continental washer on the door and he stated it sounds like they need a new door lock assembly, I than talked with a sale person on getting a price quote on the door lock assembly. | 4 | Continental Girbau out of order |  |  |  |  | none | No |  | No |  | No |  | No |  | No | once parts are order I will return to Circle to make the repairs. | RMW | [9 empty] | N/A | Other Documents | 2016-07-21 09:18
RMWTR-1311 | NSHC | Gambell | Bryant Koonooka | 2016-07-09 | 2016-07-20 | Routine | $1,060 | $762 |  |  | Bering Air | No |  | Name: Joel James Title/Position: Mayor Accompanied By? No Telephonic Contact? No | Name: Debra Apatiki Title/Position: Vice-Mayor Accompanied By? No Telephonic Contact? No | Name: Ramona Tungiyan Title/Position: Utility Clerk Accompanied By? No Telephonic Contact? No | Name: Paul Apangalook Title/Position: Tribal President Accompanied By? No Telephonic Contact? No | Name: Virgil Soonagrook Title/Position: Tribal Council Member Accompanied By? No Telephonic Contact? No | Name: Richard Koozaata Title/Position: Tribal Council Member Accompanied By? No Telephonic Contact? No | Name: Archie Ungwiluk Title/Position: Tribal Council Member Accompanied By? No Telephonic Contact? No | Name: Clement Ungott Title/Position: Tribal Council Member Accompanied By? No Telephonic Contact? No | Name: Rueben Tungiyan Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Gary Kaningok Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Well house piping cleaning,500,000 & 212,000 tank cleaning. | Well house; Cleaned 2-inch piping and valves,pulled out the 0.5 horse pumps and cleaned the pumps and the 1 1/2 pipe that is connected to the pumps.pigged transmission line 5 times supply and return.Went from 20 gpm to 32.2 gpm after cleaning piping and pigging transmission line. 500,000 water tank; Looked at both man ways and opened up south man way.3 studs were spinning so cut one and drilled out the remaining two.The level on the panel showed 3.6 feet but cracked the door and lots of water came out.Went up and measured tank it was at 6 feet,panel is off by 2.4 feet.Drained tank using 2-2 inch sump pump and 1 smaller sump pump,and started cleaning tank.Look like the sediment had 4 different layers.Made a chlorine solution in bucket to disinfect our boots before entering the water tank. Used squeegee,broom and M-30 jetter to clean tank. Jetted the fill line of the water tank. Sanitized water tank after cleaning was done with 1% chlorine solution.Painted the rusty door with epoxy paint.Closed up tank and torqued bolts. 212,000 Grinded rust off the bolts to opened up north man way on 212,000 water tank.Opened up tank and seen a absorbent pad hanging from the center column.Drained water tank using 2-2 inch sump pumps and a smaller sump pump.Made a chlorine solution in bucket to disinfect our boots before entering the water tank. Used squeegee,broom and M-30 jetter to clean tank.Jetted fill line of water tank. Sanitized water tank after cleaning was done with 1% chlorine solution.Closed up tank and torqued the bolts. | 64 | Rusted hatch on 212,000 on south side.Rusted hatch on 500,000 on north side. |  |  |  |  | Rusted hatch on 212,000 on the south side.Rusted hatch on 500,000 on north side. | No |  | No |  | No |  | No |  | No | Take rust off and Paint rusted hatches on both tanks. | Operator | Jetter well piping every year. | Operator | Clean 1.3 million tank. | Operator | [5 empty] | Attachments | Other Documents | 2016-07-22 10:52
RMWTR-1319 | MHC | Kobuk | Jeff Luther | 2016-07-22 | 2016-07-22 | Routine | $360 | $57 |  |  |  | No |  | Name: Chris McKay Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Quentin Horner Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Richard Teel Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [7 empty] | Clean Water Storage Tank | Emptied out water from water storage tank, shoveled out sediment build up from the bottom of tank, pressure washed the walls of tank, scrubbed the walls with push brooms, gathered all sediments & pump out of tank with 3" trash pump | 3 | none |  |  |  |  | none | No |  | No |  | No |  | No |  | No | send water samples from distribution loops | Operator | [9 empty] | N/A | Other Documents | 2016-07-25 08:05
RMWTR-1320 | YKHC | Emmonak | Billy Westlock | 2016-07-04 | 2016-07-08 | Emergency | $54 |  |  |  | Personal truck | Yes | 10 miles | Name: Arthur Redfox Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Jamie Agwiak Title/Position: Wastewater Operator Backup Accompanied By? No Telephonic Contact? No | [8 empty] | Repair water main break Recharge water loops due to low water | I received a call from wpo Redfox wanting assistance repairing a water leak on w-2 which drained the water storage tanks. When I met with wpo Redfox we repaired a water main break in a reoccurring spot on w-2 which the repair band broke loose and drained the storage tanks. After the repair we then went to the water plant where we began recharging the header due to only 3 feet on the tanks and the header is 6 feet above the bottom of the tanks. While making more water we recharged the water header and got the town back online at about 4 p.m., but with such low water we shut down the whole village till we gained about a foot then recharged the water header again. Over the next few days we lost prime to the header several times due to the community and the fisheries using more than we could produce, so we had watched the water plant 24 hours a day 7 days a week just to keep up with demand. We will make sure that the plant is pumping the most it can treat which is about 70 gpm and over the next few days I will keep an eye on it to make sure we are gaining and not losing. | 6 | We need to keep good watch over how much water is being used and try not to lose water again in such quantity. |  |  |  |  | None | No |  | No |  | No |  | No |  | No | I will watch the plant to make sure we don't loose prime. | RMW | [9 empty] | N/A | Other Documents | 2016-07-27 07:51
RMWTR-1321 | MHC | Ambler | Jeff Luther | 2016-07-26 | 2016-07-26 | Routine | $360 | $57 |  |  |  | No |  | Name: Roy Ramoth Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Tony Ticket Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Preston Sheldon Title/Position: Local Laborer Accompanied By? No Telephonic Contact? No | [7 empty] | Scope out washeteria line with sewer cam | While waiting for access to the washeteria Roy had concerns about his lift station pump VFD having issues, he ran his pump & it ran for 2-3 minutes fine before it faulted out, pump overheated, he thought the alarm had something to do with the wiring when it was actually something stuck on the impeller of the pump, so we pulled the pump & cleared the impeller turned it on & it ran fine. After gaining access to the washeteria we opened up a floor drain & ran the camera the whole length of 200' of the camera line we had & it was all clear, only the toilet was backed up in the building, we saw the service line turned into the sewer main. I did inspect the sewer cover that was causing all the problems they had last winter, it wasn't seated properly leaving a 3" gap to where kids can throw materials down including rocks/gravel/trash etc.. And I did see the contents they pulled out from the sewer line near by from the lid not being seated right | 3 | seat sewer cover |  |  |  |  | clean out lift station bottom when lift station is pumped out | No |  | No |  | No |  | No |  | No | clean out lift station & seat sewer cover | Operator | [9 empty] | N/A | Other Documents | 2016-07-27 08:29
RMWTR-1322 | DEC | Larsen Bay | Kevin Schoneman | 2016-07-21 | 2016-07-22 | Training/Meeting | [5 empty] | No |  | Name: Leigh Hubbard Title/Position: ANTHC Engineer Accompanied By? No Telephonic Contact? No | Name: Dave Beveridge Title/Position: ANTHC Engineer Accompanied By? No Telephonic Contact? No | Name: David Harmes Title/Position: Mayor Accompanied By? No Telephonic Contact? No | Name: Bill Nelson Title/Position: Public Works Director Accompanied By? No Telephonic Contact? No | Name: Sam Kenoyer Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Hugh Kennen Title/Position: VSW Engineer Accompanied By? No Telephonic Contact? No | Name: John Johnson Title/Position: Accompanied By? No Telephonic Contact? No |  |  |  | Final Inspection of the Water Treatment Plant and Septic Lagoon Site Visit. We were invited by Leigh Hubbard of A.N.T.H.C. Engineering Project Manager to attend the inspection of the Larsen Bay WTP. | I arrived at the Anchorage airport at 4:35 a.m. I checked in at Alaska Airlines for the 6:30 a.m. departure to Kodiak and headed for the gate. At the gate I met up with Leigh Hubbard, David Beveridge with A.N.T.H.C. and John Johnson D.E.C. We departed Kodiak at 8:40 a.m. and arrived in Larsen Bay at 9:30 am. We were met at the airport by Public Works Director and Vice Mayor Bill Nelson. We all headed to the Water Treatment Plant. At the WTP the group joined, including in attendance. Leigh Hubbard ( ANTHC Engineering Project Manager), David Beveridge( ANTHC Engineering Project Manager), John Johnson ADEC ( RMW Program Manager) David Harmes ( City of Larsen Bay Mayor), Bill Nelson( City of Larsen Bay Vice Mayor and Public Works Director), Sam Kenoyer, ( Operator) Hugh Kennen, (Operator) and myself. Leigh started the meeting by handing out the meeting agenda, and stating the topics we would be covering in the meeting. Leigh gave the group summary of the Larsen Bay Water Treatment Plant Upgrade Project. We talked about the revised scope punch list that was remaining from previously funded projects and reviewed the items on the list. There was agreement of the group that those items were complete. We then moved to Non- scope items that were added to the list and were in the process of completion. Some of the items on the list the city has agreed to complete and some of the items on the list ANTHC will complete at a later date. Leigh explained that ANTHC would be transferring the project pick-up truck to the community. Leigh explained that once the documents were signed, that the project would enter the warranty period. One topic that was a majority of the discussion was the acquisition of the septic pumping trailer, Leigh explained the difficulties that were encountered through the first bid process with time restraints and specifications. It was discussed and the next course of action would be that the city would pay a portion of the funds needed to restart the process and possibly be reimbursed as other phases of the project were finished. This was very well received and was satisfactory with the city. Leigh also talked about some of the future needs and improvements for the next few years. We then left the Water Treatment Plant to tour the Septic Sludge Treatment Lagoon, Water Impoundment and the Water Distribution System. We first stopped by the Septic Treatment Lagoon that had been recently completed. Everyone agreed that the end result was excellent. We then headed up to the Water Impoundment to look at some of the improvements that were needed such as the intake structure and spillway. On our way back to the city office Leigh gave us a tour of the distribution system and talked about some of the difficulties that the city has encountered in the past with the aging system. We stopped at the city office so Leigh and David could finish up with some of required paperwork. We then headed back to the airport to meet the plane for Leigh and David's return flight. John and I met back up with Bill Nelson to look at some of the projects he was working on the past few months . One of which he was clearing a trail to well #2 for a back up water source. Originally 3 wells were drilled for Larsen Bay, well number 1 has always been the primary source but after several dry summers and some shortages he decided that options were needed. We also looked at the area of town that in the future may be added to the gravity sewer system. The next morning we met Bill at the city offices to go over the template for Larsen Bay Preventative Maintenance Program, and also look at some of the as-built drawings of the Larsen Bay Water and Waste Water systems. John and I then drove up to the WTP to meet with the operators Hugh Kennen and Sam Kenoyer. We spent the remainder of the day at the WTP with the operators discussing the required water quality testing. We also talked about the items that they were working on in the plant mainly the fuel line for the back-up generator. We talked to both operators about the Preventative Maintenance Program, both operators were very receptive to the plan and would contribute to seeing it completed. Later in the day John and I headed to the airport for our flights back to Anchorage. | 2 | Water Storage Tank has several leaks. | Back-up Source to Well #1 |  |  |  | Back-up for Well Number 1 | No |  | No |  | No |  | No |  | No | The City may choose tighten or replace some of the bolts on the Water Storage Tank( Bill talked to John about this action) The Public Works Director is currently working on a route and back-up line from well # 2 | Engineer | [9 empty] | Attachments | Other Documents | 2016-08-02 10:12
RMWTR-1323 | DEC | Larsen Bay | John Johnson | 2016-07-21 | 2016-07-22 | Routine | $651 | $120 |  |  | Alaska Air, Island Air | No |  | Name: Leigh Hubbard Title/Position: ANTHC Engineer Accompanied By? Yes Telephonic Contact? No | Name: David Beveridge Title/Position: ANTHC Engineer Accompanied By? Yes Telephonic Contact? No | Name: Kevin Schoneman Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: David Harmes Title/Position: Mayor Accompanied By? Yes Telephonic Contact? No | Name: Bill Nelson Title/Position: Vice-Mayor Accompanied By? Yes Telephonic Contact? No | Name: Sam Kenoyer Title/Position: Water Operator Accompanied By? Yes Telephonic Contact? No | Name: Hugh Kennen Title/Position: Water Operator Accompanied By? Yes Telephonic Contact? No |  |  |  | Kevin Schoneman (DEC-RMW) for the community of Larson Bay and myself were contacted by Liegh Hubbard (Senior Engineering Project Manager DEHE, ANTHC) in regards to attending the final trip for the Larson Bay Water Treatment Plant Upgrade project. We accepted the invitation and made flight arrangements to Kodiak via Alaska Airlines and Leigh had made arrangements for all attending to catch a flight from Kodiak to Larson Bay with Alaska Air Lift. We departed Kodiak on Alaska Air Lift at 8:40am and arrived in Larson Bay at 9:30am. We were met at the Airstrip by Vice Mayor Bill Nelson and Water Plant Operators Sam Kenoyer and Hugh Kennen. We had a brief introduction then headed to the WTP where the Mayor David Harmes joined us. | Leigh past out the meeting agenda and gave a brief overview of the entire scope of the project and that this was the final inspection and thus the 1 year warranty period would start on this date. Leigh took us through the agenda and there were very few questions as most issues were thoroughly vetted before this point. The large item remaining on the table was the procurement and shipment of a trailer mounted septic pumper unit. Due to the balance of the project funds ANTHC was unable to award the contract for the septic pumper. To navigate the issue the city offered to pay a portion of the cost of the unit to get the contract awarded and get the unit built and shipped ASAP. ANTHC accepted there offer and will re distribute the RFQ and award to the lowest prospective bidder. The project pick up truck was also turned over to the community at this meeting. We then departed the WTP to look at the newly constructed sludge treatment lagoon facility. This was constructed by a contractor and Larson Bay and ANTHC were very happy with the performance and final product. We then went to the water impoundment to address the need for rehabilitation of the spillway and intake structure. Leigh and David departed at 1:00pm and Kevin and I stayed over to continue to work with the operators and the public works director the remainder of the day and the following day. Kevin delivered a sample PMP to the community and would also email the template for them to use as they develop there PMP and start quarterly submittals. | 2 | The steel 283,000 gallon Water Storage Tank has been leaking for some time and has as many as twenty seeps to spraying steams of water visible at different times of the year. We looked in the man way access on the roof and could see the tank is very clean and the floor of the tank was completely visible with a water elevation at the time of inspection of fifteen feet (full tank). |  |  |  |  | Water Storage Tank leaks. The leaks may be repaired by installing new bolts and torqueing them to the manufacturers recommendation. Additional steps could be taken if that procedure doesn't eliminate the issue. | No | 4" plastic water main throughout the community has reached its life expectancy and has continued to fail in shallow burry areas in the winter. The line is very fragile and is a high maintenance item for the city. Leigh discussed the possibility of getting the project funding and will pass on the information gathered to the PM that's taking over that community. | Yes |  | No |  | No |  | No | At some point in the future when the tank needs cleaned we could try and re-torque the bolts at the leaking areas. at this point most likely the bolts would shear off and new bolts would need to be installed and torqued to manufactures specifications. The WST does not have an insulation package, so attempting to tighten and or replace the bolts as the tank is drained should be fairly straight forward. | Operator | [8 empty] | The project has also purchased a new variable frequency drive for the well pump control to reduce heat produced in the well control panel. ANTHC will send out a licensed Journeyman Electrician to complete the install during the warranty period. The project also provided the city with a new pitless adapter for the well along with bentonite clay mixture and the city will be responsible for that installation. Also provided were two hydrant reducing fittings that the city will use to install two new flushing hydrants. | N/A | Other Documents | 2016-07-29 14:26
RMWTR-1324 | NSHC | Shishmaref | Bryant Koonooka | 2016-07-27 | 2016-07-28 | Startup | $432 | $150 |  |  | Bering Air | No |  | Name: Darin Barts Title/Position: ANTHC Engineer Accompanied By? No Telephonic Contact? No | Name: Alfred Ningalook Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Ken Orrison Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: Bill Jones Title/Position: Vice-Mayor Accompanied By? No Telephonic Contact? No | Name: Jane Kakoona Title/Position: Tribal Administrator Accompanied By? No Telephonic Contact? No | [5 empty] | Help with Start up pumping water.And train water plant operators. | Water plant: Darrin,Alfred and Ken had started making water couple hours before i made it in.Had to use a 3200 honda generator Cause of some corrosion issues on the transformer and wires that connect power to the well.Darrin dialed in the instruments on the panel.While I had Alfred show me around the water plant and well house.Corrosion on the transformer was so bad the bottom was not there anymore.Got some tools together and wire nuts and cut and reconnected the wires together with Darrin.Still no power going to the the well.But got power to two of the leads,Little over 100 volts.We gave the operators training on how to back wash and filter to waste. Darrin Gave them a list of sequences for the process.I Had them do a back wash later on than evening. Well house: Went to go check if power made it thru the wires after the cut and reconnected the wires.Cleaned the well pump it clogged up with algae.Put oil in the generator which had turned off during the night cause low oil.Gassed it up and began pumping again.There was a transformer by the well house where they might get power from Alaska village Electric company straight to to well.Would solve the rusted transformer at the water plant. | 17 | Rusted Square D transformer Style No 12151-12625-005 Cat No 7SIF and transformer wiring. |  |  |  |  | Rusted Square D transformer Style No 12151-12625-005 Cat No 7SIF and transformer wiring. | No |  | No |  | No |  | No |  | No | Replace transformer and Wiring at the water plant,and maybe transformer at the well house.Or have avec hook up well house to the transformer by the well house. | Unknown | Fix leaks in the water plant. | [8 empty] | Attachments | Other Documents | 2016-08-02 09:50
RMWTR-1330 | TCC | Circle | Fred Kameroff | 2016-08-02 | 2016-08-03 | Routine | [5 empty] | No |  | Name: Lawrence Crow Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Jessica Feilds Title/Position: Tribal President Accompanied By? No Telephonic Contact? No | Name: Angela Ludwick Title/Position: Tribal Administrator Accompanied By? No Telephonic Contact? No | [7 empty] | Remove Door Lock assembly on Continental washer Clean shower coin operated timer | I contacted Mr. Lawrence Crow Jr to tell him I was heading up to Circle to remove and inspect the door lock assembly and inspect what has been damaged on it. I arrived at Circle at 11:45 am and was greeted by Mr. Crow and escorted to the water plant.Mr. Crow and I started to remove the front panel on the washer. Once we had removed the panel we removed the locking bitron and inspected for damage and found what looks like the locking assembly had some burned pins. Mr. Crow did not have any spare parts for the washer at the time. The washer has been placed out of service until a new locking assembly can be ordered and delivered. Mr. Crow also stated he was having trouble with the Monarch coin operated timer for the ladies shower. Mr. Crow said the coins would not go through the coin drop and asked me to take a look at it. We then removed the coin drop and inspected it and found it needed to be cleaned. I asked Mr. Crow if he had Rubbing Alcohol and Q-tips to clean the coin slide assembly. Once we cleaned out the coin slide we replaced the part and tested it, and to our finding the coin started to accept the coins and we placed the shower back to normal operation. RECOMMENDATIONS/CONCLUSION The dryer parts were ordered and I forwarded the door lock assembly price quote to Circle council to order, once the parts get up to circle I will head back up to make the necessary repairs on dryers and the continental washer. | 6 | washer/dryers down |  |  |  |  | none | No |  | No |  | No |  | No |  | No | once parts have been received I will travel back up to Circle to make the repairs. | RMW | [9 empty] | N/A | Other Documents | 2016-08-04 11:41
RMWTR-1337 | DEC | Newhalen | Floyd Murphy | 2016-08-01 | 2016-08-03 | Routine | $460 |  |  |  | Airplane | No | 9.7 miles | Name: Paul Askoak Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Kathleen Gust Title/Position: City Clerk Accompanied By? No Telephonic Contact? No | Name: Theodore Missig Title/Position: Project Superintendant Accompanied By? No Telephonic Contact? No | Name: James Lamont Title/Position: Other Accompanied By? No Telephonic Contact? No | [6 empty] | Meet operator, become familiar with the water and wastewater systems, inspect progress on the new lift station project and work with the operator on the Preventative Maintenance plan. | Newhalen August 1-3, 2016 8/1/16 I departed Anchorage for Iliamna / Newhalen on Iliamna Air Taxi Inc. at 8:00 am arriving at 9:00 am. I was met by Newhalen resident, James Lamont Sr. who gave me a ride to Newhalen. We went to the lift station and observed the work on the new lift station, I met the ANTHC Project superintendent Theodore Missig. The crew was working on forms for the lift station building. Plans were to replace the force main to the sewage lagoon once the lift station was completed. 8/2/16 8:00 am meet Paul Askoak Water Plant Operator, at the water plant. We went through the water treatment process from the wells to the distribution system. Well pump #1 was not operational because the magnetic starter had failed it appeared to have shorted as there were burn marks where it is grounded to the control panel box. We located a spare magnetic starter but it was for a 3 to 5 horse power, the pump is a ¾ HP pump and this would not work. The water level controller would not work on automatic. Paul was instructed on making a new tank level controller using wire. Paul made a spare controller and was instructed to make another before installing the spare. The water storage tank holds 18,000 gallons it meets the needs of the customers but does not provide fire protection. The water plant has black mold inside on the walls and ceiling. Paul said the walls and ceiling were scrubbed down last year, but the mold returned. 8/3/16 Paul and I drove through the community, isolation valves were installed to all customers so they can be shut off for lack of payment. ANTHC is working on a new lift station and force main, this new system will make it easier to operate and maintain. The old system is a wet well dry well system, the dry well is a confined space problem, and at times would flood with wastewater. I departed Iliamna around 4:00 pm arriving in Anchorage around 5:00 pm. Operator training consisted of Preventative Maintenance plan, electrical troubleshooting of the magnetic starter and water level control wireing. | 14 | None at this time |  |  |  |  | The exhisting water storage is 18 thousand gallons that meet the demand of the community but do not meet fire protection. | No | Black mold in the water plant. | No |  | No |  | No |  | No | Inspect new lift station and force main when completed. | RMW | [9 empty] | Attachments | Other Documents | 2016-08-05 14:49
RMWTR-1340 | YKHC | Pitka's Point | Billy Westlock | 2016-07-26 | 2016-07-26 | Routine | $300 |  |  |  | Ravn aviation | No |  | Name: Paul Lamont Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | [9 empty] | Take a look at the chlorine line, repair the cracked flow switch on the transmission line going to the holding tank. | I received a call from wpo Lamont wanting assistance with repairing the chlorine line for the raw water, also the flow switch cracked pipe for the water line going to the holding tank. When I arrived we first took a look at the chlorine line which wpo Lamont was concerned that the water was feeding back into the chlorine room, we traced the line out and found that one of the check valves was damaged, we repaired it and chlorine feed is back to normal. The other repair needed was that the threads for the flow switch on the raw water line was cracked probably due to over tightening, we found some fittings that matched, cut out the broken section and repaired it, now the flow switch is no longer leaking. | 4 | None |  |  |  |  | None | No |  | No |  | No |  | No |  | No | None | Unknown | [9 empty] | N/A | Other Documents | 2016-08-08 09:05
RMWTR-1341 | YKHC | Pilot Station | Billy Westlock | 2016-07-27 | 2016-07-27 | Training/Meeting | $0 |  |  |  | Ravn aviation | No |  | Name: Rodney Alick Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | [9 empty] | Assist with set up for lagoon pump out | I received a call from administrator Ruth Borromeo want me to assist with set up with the lagoon pump. When I arrived the back up operator Rodney Alick and I went and took a look at the set up for the lagoon pump which the operators almost completed already before I arrived, but the only question was where to let the discharge go in to the river. Wpo Alick had a few questions about a few testing areas, and I mentiined to him to look at the testing procedures that the lagoon test kit came with and just follow the instructions. The village didn't think that it was a good idea to discharge the lagoon until fishing both subsistence and commercial was completed, due to fisherman concerns about sewage going onto the fish. So at a later date the operators know what to do when it comes time to start discharging, and testing when fishing is over. | 3 | I will call the operators of when they start to discharge and when they are completed |  |  |  |  | None | No |  | No |  | No |  | No |  | No | I will call or they will call when they start discharging the lagoon | RMW | [9 empty] | N/A | Other Documents | 2016-08-08 10:01
RMWTR-1342 | YKHC | Eek | Bob White | 2016-08-08 | 2016-08-08 | Routine | $260 |  |  |  | Raven Air | No |  | Name: steve Wilson Title/Position: Project Superintendant Accompanied By? No Telephonic Contact? No | Name: James Dullinger Title/Position: Plumber Accompanied By? No Telephonic Contact? No | Name: Michael Vincente Title/Position: Environmental Health Officer Accompanied By? Yes Telephonic Contact? No | Name: Adolf Carter Title/Position: Wastewater Operator Accompanied By? No Telephonic Contact? No | [6 empty] | Inspect substance removed from water tank. inspect pipe installation to date. Inspect work done under RAVG. | WPO Adolf and I walked to the Washeteria and discussed the tank cleaning and recent work done at the plant. WE then looked over the building heat supply pump changes and the other boiler work done under RAVG. The controls for the boiler are still not wired correctly for the Tekmar to work in Auto. The new LED lights really brighten the place up and the Belimo actuators are working great. We then looked at the water tank deposits that were removed and discussed the solutions that had been passed around with the operator. After looking at the lagoon and the terminal manhole we then walked some of the new piping in the upper part of the village. At the river we looked at the new intake piping from the new intake structure to the water level of the river and then discussed the underwater configuration. We finished our time by visiting with the construction Superintendent and talking about the progress made and there current time line. | 4 | The water storage tank seems to have been very clean except for pitting on tank. | Some settling needs to be addressed along pipe that are buried. | Pipe alignment seems to be a issue on several service connection coming off the sewer forcemain. |  |  | Water storage tank needs lined or re epoxy coated. | No |  | No |  | No |  | No |  | No | Regrade sink holes along buried pipe to prevent water puddling. | Construction Project | Secure power mast at River intake better as it is pulling loose from the clamps. | Construction Project | improve alignment on arctic pipe connections. | Construction Project | Follow up on tank corrosion and create plan to correct | Engineer |  |  |  | Attachments | Other Documents | 2016-08-09 07:34
RMWTR-1348 | DEC | Hydaburg | Steve Evavold | 2016-08-01 | 2016-08-03 | Routine | $850 | $200 |  |  |  | No |  | Name: Anthony Christianson Mayor Title/Position: Accompanied By? No Telephonic Contact? No | Name: Donald Bell Water Plant Operator Title/Position: Accompanied By? No Telephonic Contact? No | Name: Natasha Peele City Administrator Title/Position: Accompanied By? No Telephonic Contact? No | Name: Stacia Miller City Clerk Title/Position: Accompanied By? No Telephonic Contact? No | [6 empty] | A trip in May found part of the instrumentation panel for turbidimeters and controllers had no power. Inspection determined a power outage had caused the damage to a power switch and two of the SC200 HACH controllers that displayed IFE turbidity for filters 1, 2, and 3. That resulted in incomplete data being recorded by the Honeywell data logger. This trip was a continuation of working with the operator; and repairing the data retrieval and storage capability of correct turbidity data. | Arrived in Hydaburg and met with Donald at the water plant. The instrumentation was as we left it in May. The plant was still producing potable water at 0.03ntu's with an entry point Chlorine residual being maintained above 0.6 mg/l. The working turbidimeters were monitoring filters #2 and #3, raw, and Combined filter Effluent. The turbidimeter for Filter #1 was working but the output signal from the 1720E circuitry is wired to the shorted out SC200, thus no display or data retention in the Honeywell for that filter. When Kevin Schoneman(RMW), and I visited in May for introduction and utility inspection, we found a shorted power switch and two of 3 SC200's(left to right on the panel), with no display. The 3rd SC200 was still functioning and displaying Raw and CFE turbidities. We bypassed the power switch and regained activation to the middle SC200 for filters 2 and 3 via the breaker in the control panel. The SC200 controller for Filter #1 and on/off switch needs replacing. Time was limited so we left with that achievement. The scope for this trip was to move the raw water turbidimeter over to Filter #1, change parameters, inputs, and regain IFE monitoring for all 3 filters and the data logged by the Honeywell MultiTrend per DEC requirements. I moved the head assembly for the raw 1720E over to the reservoir for filter #1 and saw that turbidity displayed dropped from 0.60ntu's to 0.03ntu's. I changed the output configuration in the SC200 to display "filter1". On the Honeywell I de-activated the pen for "Raw" water and reactivated the pen(graphing ability), for Filter 1, and ran into problems. The Honeywell was programmed with 15 other inputs, water flows in and out, UV, SCD set point and PV, Polymer pump % stroke, etc., plus inputs from the 5 turbidimeters. Wiring into the Honeywell is cumbersome. To troubleshoot the input problem from filter 1, I deactivated all inputs until just turbidities were involved. I reset all analog signals, ranges, scales, etc. I called ANTHC, TUS consultant Darrin Bartz, who assisted in eliminating possible problems with the SC200 controller. The next morning I traced wiring for the controllers to the input strips on the back of the Honeywell and found that I had been configuring the wrong "Pen". When switched over, IFE for filter 1 was displayed. I monitored outputs, displays, and made sure the information was being continuously logged. As of Wednesday 8/3 at 10 am, effluent controls and data retention for that part of the water plant are working. Changing the 1720E for "raw" over to Filter 1 effluent data, is a loss for the plant. Though not regulatory required, Operators and RMW's statewide depend on raw water data to predict the workload for the water plant on a daily basis. Higher raw water ntu values will use more polymers, chlorine, and cause more frequent backwashing. I asked Donald to work through a filter backwash. The drain down, air scour, and backwash instructions are followed without deviation. When done, the filter-to-waste cycle was not completed until effluent turbidity was well below the recommended level for reinstating water to service. I commended Donald on his work ethic and attention to detail. I noted that the plastic head on the polymer pump is leaking on the outlet side. We checked the SCD operation by changing from auto, to manual, and back to auto function. The bearing and clevis pin(needs replacing on occasion), for the probe assembly are fine. Donald knows how to disassemble and clean the probe and contacts. I also noted that a couple of times a day the power to the plant dims for a bit and comes back up. This is hard on the instrumentation. We finished with cleaning the raw water flow meter. It had been showing 0 flow. The contacts needed brushing. | 14 | The SC200 HACH controllers are of the original model. This model does not have the capability of graphing the recent outputs. That would be beneficial if/when the Honeywell data logger stopped working. |  |  |  |  | The water plant now needs 2 SC200's and a 1720E spare. | Yes |  | No |  | No |  | No |  | No | More assessment of the water intake is needed with study for design. RMW and TUS involvement. | Engineer | Assistance with installation and programming of new monitoring instrumentation needed. TUS and RMW involvement recommended. | [8 empty] | Attachments | Other Documents | 2016-08-12 14:19
RMWTR-1349 | MHC | Ambler | Jeff Luther | 2016-08-10 | 2016-08-11 | Training/Meeting | $468 | $122 |  |  |  | No |  | Name: Roy Ramoth Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Preston Sheldon Title/Position: Local Laborer Accompanied By? No Telephonic Contact? No | Name: Council Members Title/Position: City Official Accompanied By? No Telephonic Contact? No | [7 empty] | Meet with Operator during the day & attend council meeting in the evening | Met with the operator Roy & his laborer Preston, found out that the lower lift station had been down due to rags in the lift station well, got the operator & laborers to hook up a 3" trash pump along with 300' of discharge hose to pump the lift station well to the manhole above the lift station that it pumps into, told the operator to clean the bottom of the well once they got it pumped down but there were some sludge preventing it from happening, they will continue to use the pump to clean the bottom of the well until the 500gallon sludge pump tire comes in so that they can pump the sludge out of the lift station well. Also went out to view the new lagoon & upper lift station for inspection, everything seemed to be in working order as well as in the WTP. Attend the evening City Council meeting, Chris introduced me to the council and answered any questions that were asked about work being done out there | 3 | lower lift station |  |  |  |  | lower lift station | No |  | No |  | No |  | No |  | No | keep lower lift station pump operable by cleaning the impeller of the pump clear of any obstructions | Operator | [9 empty] | N/A | Other Documents | 2016-08-11 13:55
RMWTR-1350 | MHC | Kobuk | Jeff Luther | 2016-08-15 | 2016-08-15 | Routine | $504 | $57 |  |  |  | No |  | Name: Kris McKay Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [9 empty] | Pressure switch issues | Met with Kris the operator, he had the pressure pumps running on hand, he thought there were some issues with the pressure switches, he left me alone at the plant, I got my voltmeter out & 'diagnosed' the control panel thinking that something in the control panel there would be an issue to keep the switches from operating normally, nothing wrong there so I turned the pressure pump switch from Hand to Auto to see what would happen, the pressure switches are operating right & are capable of keeping the system pressurized on auto, however, the diaphragm's on the pressure switches are rated at 1hp & the pumps are 3hp, they will be changed on my next trip out. | 1 | none |  |  |  |  | 1hp pressure switches | No |  | No |  | No |  | No |  | No | change pressure switches | RMW | [9 empty] | N/A | Other Documents | 2016-08-16 08:58
RMWTR-1353 | YKHC | Tuntutuliak | Bob White | 2016-08-11 | 2016-08-11 | Routine |  |  |  |  | Raven Air | No |  | Name: Michael Vincente Title/Position: Environmental Health Officer Accompanied By? Yes Telephonic Contact? No | Name: Kameron Hartvigson Title/Position: TUS Accompanied By? No Telephonic Contact? No | Name: John White Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [7 empty] | To help with the RAVG Installation. To check condition of the water plant and operations. To look at possible new route for waste heat piping. | When we arrived at the plant we were met by WPO White and Kameron. They were in the middle of preparing light fixtures for conversion to LED. We discussed the progress of the installation and what remained to be done. Then as WPO White took lunch I walked out and marked a possible new route for the Waste Heat lines. The realignment would use much higher ground and avoid most of the wet areas. When WPO returned from lunch he headed to the airport to pick up freight they were expecting. I then started to drain the pressure tanks and reset the air level. I then installed the new pressure switch and replaced several pressure gauges. We then tested the pressure pump system to see it performed properly. When WPO White returned with only plywood Kameron called to locate the other freight and found out it had not left Anchorage yet. With little left to do with out the parts I worked with WPO White on questions about his Washing machines, which he then had me explain to the Tribal office staff. When our flight arrived we departed to the airport. | 6 | The plant seems to be in good condition for its age WPO white is doing a good job of keeping things up. |  |  |  |  | GAC filter needs replacing. | Yes |  | No |  | No |  | No |  | No | RAVG will need to do a follow up trip once parts arrive. | Other | I will look into filter vessel option for the GAC filter. | [8 empty] | N/A | Other Documents | 2016-08-15 08:53
RMWTR-1354 | NSHC | Shaktoolik | Bryant Koonooka | 2016-08-09 | 2016-08-10 | Routine | $504 |  |  |  | Bering Air | No |  | Name: Ralph Takak Title/Position: Local Laborer Accompanied By? No Telephonic Contact? No | Name: Dave Ortega Title/Position: Electrician Accompanied By? No Telephonic Contact? No | Name: Edward Jackson Title/Position: Water Operator Accompanied By? No Telephonic Contact? No |  | Name: Vernon Rock Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: Shawn Evan Title/Position: Local Laborer Accompanied By? No Telephonic Contact? No | Name: Jeff Beattie Title/Position: Project Superintendant Accompanied By? No Telephonic Contact? No | Name: `George Sookiayak Title/Position: Other Accompanied By? No Telephonic Contact? No | Name: Matilda Hardey Title/Position: Tribal Council Member Accompanied By? No Telephonic Contact? No | Name: Edgar Jackson Title/Position: City Council Member Accompanied By? No Telephonic Contact? No | Site visit and see how the project is going. | Water plant: Project just get started up,Dave Ortega was doing inventory to see if they had every thing.Jeff Beatty showed me where the back wash pond was going to be.Shawn Evan was digging up The sewer service to water plant and a house next door.They are having grease issues the previous tenants had drained a bunch of grease down the drains.Jeff needed to change out a leaking 1 inch gate valve.He went over to the city to tell them he was going to turn to water off to change the valve.None of the isolation gate valves work.The 800,000 water tank needs to be sand blasted and painted. | 12 | Grease issues at the teacher housing.Due to the grease the washeteria had back up problems. |  |  |  |  | Teacher housing sewer service was going to be changed.Due to reverse grade on it half way down the pipe. | No |  | No |  | No |  | No |  | No | Clean Water Tank | Operator | [9 empty] | Attachments | Other Documents | 2016-08-19 11:22
RMWTR-1356 | NSHC | Wales | Bryant Koonooka | 2016-08-11 | 2016-08-20 | Startup | $474 | $225 |  |  | Bering Air | No |  | Name: Zachary Milligrock Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Stanley Milligrock Title/Position: Local Laborer Accompanied By? No Telephonic Contact? No |  | Name: Sherman Richards Title/Position: Mayor Accompanied By? No Telephonic Contact? No | Name: Jo-Ann Keyes Title/Position: Tribal Administrator Accompanied By? No Telephonic Contact? No | Name: Kelly Anangazuk Title/Position: City Clerk Accompanied By? No Telephonic Contact? No | Name: Terry Crisci Title/Position: Other Accompanied By? No Telephonic Contact? No | Name: Lenora Sereadlook Title/Position: City Council Member Accompanied By? No Telephonic Contact? No | Name: Matilda Crisci Title/Position: City Council Member Accompanied By? No Telephonic Contact? No | Name: Debra Seetook Title/Position: City Council Member Accompanied By? No Telephonic Contact? No | Clean water tank,Change parts at well house that were on a earlier report and start up pumping water. | Water tank: Opened up water tank and found 7 to 8 inches of ice in the tank.The water tank only had Few inches of water.The tank looked clean so cancelled tank cleaning. Well House: Gathered parts and tools and went up to well to change out parts.Changed parts and started to make solution to sanitize the transmission line.Put in 35 gallons of 2% solution to transmission line.Started up water pumps to send it thru the line.Zachary walked the line to bleed out air while the solution made its way down to the water plant.Stanley and I went to the bridge to open up a valve so the air can escape the line.When the solution made it there headed over to the wtp to finish sanitizing the transmission line.Went back to well house to turn off pumps.Let the solution have contact time of 12 hours in the transmission line. Water treatment plant: After 12 hours we made sure the WTP and water tank was ready to start making water.Opened up all the valves to the water tank,but not to the distribution system.We found no leaks.Went to go start up both water pumps at the well house.We were making 40 gallons a minute.Looked thru the add heat system.One of the add heat Pumps was not working.Found a replacement and changed it out.The boiler had only 7 psi.Added glycol to to 16 psi,found leak on a old site glass on a high spot.Found parts and replaced it with a coupling and a union.After we had 4.5 feet of water we send the water thru the distribution system.Called maintenance workers for the clinic and the school to bleed out their systems and start up their circulating pumps.Started up heat add system,bleed out the air thru the heat exchanger. Made sure it was working,had a replacement but dielectric unions were rusty.Need to be replaced before new Heat exchanger is to be replaced. | 24 | Solid ice in the water tank. |  |  |  |  | Site glass on the glycol line.Few more on the line might need changing as the start leaking. | No |  | No |  | No |  | No |  | No | Make sure heat add is working to melt the ice.Look thru glycol line to look for leaks. | Operator | [9 empty] | Attachments | Other Documents | 2016-08-17 16:56
RMWTR-1362 | TCC | Arctic Village | Fred Kameroff | 2016-08-10 | 2016-08-11 | Startup | [5 empty] | No |  | Name: Robert Erick Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Clinton McMillan Title/Position: Plumber Accompanied By? No Telephonic Contact? No | Name: Daniel Tyczkowski Title/Position: Other Accompanied By? No Telephonic Contact? No | Name: Bill McDonald Title/Position: Electrician Accompanied By? No Telephonic Contact? No | Name: Debra Addie Title/Position: VSW Engineer Accompanied By? Yes Telephonic Contact? No | Name: Bernard Walker Title/Position: Other Accompanied By? Yes Telephonic Contact? No |  |  |  |  | New Water Plant Start Up | Ms. Debbie Addie emailed me stating the start up will be on 08/10/16 and asked if I can be there, I told her that I will make it up to Arctic Village for the start up. We arrived in Arctic Village on 08/10/16 at 11 am and were escorted to the water plant by a resident. We met with Mr. Clinton McMillan outside the water plant and he introduced us to Mr. Daniel Tyczkowski. Mr. Robert Erick was down at the river bank setting up the water pump to start pumping water into the new conventional water treatment system. Once Mr. Erick was done setting up the water pump, water started to flow into the flocculation and sedimentation chambers and filling both chambers up. As that was happening, Mr. Bernard Walker Trained Mr. Erick on what to look out for on the streaming current detector (SCD). First once water starts to flow through the probe on the SCD then it is OK to power up the SCD. Once the SCD is on it detects a charge that exists in suspended liquid and sets the correct dosage on the coagulant pump. Once the SCD was set on the correct dosage we started to notice small floc in the flocculation chamber forming. After 4 to 5 hours run time the media started to fill up with water and as it filled up to the top the effluent pump was turned on and the bypass valve opened and the water pumped out to waste until the turbidity was at 0.2 NTU. Water was being treated by injecting chlorine but still pumping out to waste until Arctic Village is approved to operate by ADEC. By next morning 08/11/16 Mr. Erick started the river pump and started to run water into the treatment system and still running water out to waste. Arctic Village is waiting on an approval to treat and pump water into the water storage tank. By mid afternoon the turbidity dropped down to 0.08 NTU which is well below the 0.2 NTU to start chlorinating the treated water. RECOMMENDATIONS/CONCLUSION By early afternoon Mrs. Racheal Lee send me a email stating that Arctic Village had a interim approval to operate and treat water into the water storage. | 8 | none |  |  |  |  | none | No |  | No |  | No |  | No |  | No | water plant operator | Operator | [9 empty] | N/A | Other Documents | 2016-08-18 10:46
RMWTR-1370 | NSHC | St. Michael | Bryant Koonooka | 2016-08-16 | 2016-08-17 | Routine | $504 |  |  |  | Bering Air | No |  | Name: Norbert Otten Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Alex Tom Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [8 empty] | Site Visit | Alex Tom was looking for a vacuum sewer leak when we arrived.They keep having constant vacuum sewer leaks every day.They are having problems with pipes sinking into the tundra in few water and sewer services from the homes.Some had pulled out of the arctic boxes.The pipes and some of the utilidor need leveling.One arctic box was even pulled off the building.They need more of the newer type valve assemblies to change out the older ones that are failing.But the home owners can't afford the newer ones.Vacuum pump piping was melting cause they are constantly running on high all the time.Due to vacuum leaks in the toilets that don't seat back after flushing.The AC store had hired there own plumber to hook up to the water and sewer services.AC had used the wrong parts according to Norbert. Aruc had cut the water plant operator hours.So its hard on WPO's to trouble shoot the problems and fix the Vacuum leaks with the hours they have now.There was a leaking 2 inch cast iron fitting that was leaking in valve room on the 400,000 gallon water tank.Its all rusted and ready to break apart.There is no way of isolating the water tank to change out that part with out draining the water tank first.The isolation valve is after the rusted 2 inch pipe. Water plant: The gauge for the 1.2 million gallon tank was not working.The fuel pump was not working due to a burned out fuse.They were pumping water into the water treatment plant at 6.76 gpm. They had a bunch of replacement bag filters. Well House: The fuel gauge was not working.The heat exchangers need cleaning.The well house is sinking on the lake side.Alex and Norbert had jacked it up but still sinking to that one side.Need to put more fill on that side and compact it to keep it from sinking anymore..The piping from the well to well house part of it had broken the band it had on and lifted off its supports. | 8 | Vacuum system always running on high speed,Due to vacuum leaks.Venting system pvc melting due to pump running all the time. |  |  |  |  | Arctic pipe sinking in the tundra.Need to level out the service lines and parts of the utilidor .Some arctic pipe even pulled out of the arctic boxes. | No |  | No |  | No |  | No |  | No | Change out older valve assemblies to the newer ones.They need 30 or 40 more new valve assemblies.Home owners can not afford the newer type.The assemblies reportedly costed over $700 a piece when they first came out.But they bought in bulk and the price went down to $250 a piece. | Operator | Change out the rusted 2 inch pipe coming out of the 400,000 water tank. | Operator | Level off the arctic pipe services,and parts of the utilidor. | Operator | Change the fuse for the fuel pump. | Operator |  |  |  | Attachments | Other Documents | 2016-08-24 12:01
RMWTR-1374 | DEC | Kasaan | Steve Evavold | 2016-08-03 | 2016-08-04 | Routine | $860 | $120 |  |  |  | No |  | Name: Della Coburn Mayor Title/Position: Accompanied By? No Telephonic Contact? No | Name: Bonnie Hamar City Administrator Title/Position: Accompanied By? No Telephonic Contact? No | Name: Tim Willis WTP Operator Title/Position: Accompanied By? No Telephonic Contact? No | [7 empty] | Trip was scheduled to familiarize myself with the water plant processes and to work with the operator on leak detection in the distribution system. | Arrived in Kasaan and met with Tim and Bonnie. The water plant is filtering and treating 0.6ntu raw water to 0.03ntu treated. No problems to report. I brought the RMW leak Correlator along to test the distribution system for leaks. ANTHC Project Manager asked for a preliminary study to combine with design an upcoming project. Most of Kasaan is piped with 4" ductile iron. Isolation valves for the system are not accessible, but hydrants are. There are sections of looped mains and some with dead-ends. Tim mapped out the system with hydrant locations and we started at the end of distribution by the boat harbor. There were 3 probable leaks as displayed by the Correlator. An old service connection to a cabin no longer lived in(by hydrant #3), was showing as leaking, and a hydrant(#12),at the end of the distribution system showed significant display. Another possible was along that same stretch of 4" ductile water main. In the morning Tim and I retraced the length's we had the day prior and found the same indications. I finished up with another inspection of the water plant and left for Craig. | 4 | Nothing noted at this time. |  |  |  |  | Tim and I discussed the possibility of adding a Honeywell Data logger to the recording capabilities of the plant. | Yes |  | No |  | No |  | No |  | No | Weekly check up. | RMW | [9 empty] | Attachments | Other Documents | 2016-08-29 10:37
RMWTR-1384 | DEC | Seldovia | Kevin Schoneman | 2016-08-15 | 2016-08-18 | Routine |  |  |  |  | State Truck/Air | No |  | Name: Tod Larson Title/Position: City Manager Accompanied By? No Telephonic Contact? No | Name: Tyler Tucker Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Randy Bond Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Jeremiah Campbell Title/Position: Project Superintendant Accompanied By? No Telephonic Contact? No | Name: Steve Evavold Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | [5 empty] | Leak Detection Study and New Water Plant Construction. | Monday August 15, 2016 RMW Steve Evavold and I departed Anchorage@ 0800 for Homer and on to Seldovia. We arrived in Seldovia@ 1330 after gathering our gear we headed to the city offices to meet with Tod Larson, City Manager of Seldovia. We discussed the work we had planned on accomplishing during the week, the New Water Plant Construction Project and the Sanitary Survey due by the end of the year 2016. We then headed to the Public Works Office to meet with the water operators, Tyler Tucker and Randy Bond. We discussed the plans for the remainder of the day and the upcoming week, as well as looked at some of the drawings of water and sewer systems in town. We left the public works shop and headed to the “filter building” to install the Siemens Sitrans S clamp-on flow meter as to get a better understanding of the water usage in Seldovia and check the accuracy of the in place meter. We also wanted to check and compare the readings from the chlorine building meter, on the hill near the water storage tank. The water meter in the chlorine building was recently replaced with a new in-stream meter. For the installation of the Siemens clamp on meter, we selected a straight horizontal run of 6” ductile iron pipe. This location is just inside the lower filter building just before water enters the distribution system. Before we could install the meter however, we had to clean the pipe which had substantial rust and pitting. Using the manufacturer’s instructions for device set-up we installed the meter and began recording data. After some minor realignment we started recording average flow of about 25 to 30 gpm. We left the meter installed for the duration of our stay in Seldovia. While were at the filter building we noticed a small stream of water that flowed from up the hill behind the filter building, while we looking at the stream we both Steve and I noticed the a chlorine odor. We left to check in at the B&B we would be staying at and grab something to eat, we decided to check the meters again later in the evening. Using 30 gpm and considering the population of Seldovia of approximately 300 people, would average out to 144 gallons of water per day, per person. The meter that is currently in use at the filter building normally records flows on average of about 60 gpm which would calculate out to 244 gallons of water per day/ per person @ a population estimate of 300. Considering the apparent disparity in data at this time, more investigation in to actual water flow to the distribution system in Seldovia would appear to be warranted. The next day we went to the public works office to meet up with Tyler and Randy and gather up some of the tools and equipment we would need for the day ahead. During our morning conversation we asked the operators about the stream we noticed the day before near the filter building. They both stated that “the small stream”, appeared early in the summer not to long after the construction of the new water plant started. We all left and agreed to meet at the filter building to check the flow meters and the operators could start their daily rounds. We checked the meter we had installed the previous day, the operators arrived at the filter building, we then all went up to the water storage tank and the new water plant. As we made our way up the hill we decided to back track the source of the water that was flowing near the filter building. About half way up the road to the water tank the stream crosses the road through a culvert, we decided to track the stream on foot. We followed the stream to the point we were able to see parts of the new project site at this point we were forced to turn around and head back to the road due to the underbrush. We arrived at the construction site and water storage tank, we looked at the new flow meter that was installed at the chlorine building there did appear that there was a difference of about 100,000 gallons per day compared to the readings at the filter building. Steve and I introduced ourselves to Jeremiah Campbell the construction superintendent, Jeremiah gave us a tour of the construction site, he pointed out the location of the clarifier tank and explained how they filled and compacted around the tank, we looked at the concrete pour they were getting ready for that morning. The construction site was very well organized and very busy that morning as the crew was getting ready for the concrete pour. We then headed up to the reservoir. The dam inspector completed his inspection earlier in the summer and found only a couple minor deficiencies. After a short stop at the reservoir we decided to head back down and get started with the leak detection study on the distribution system. We started the leak study on Main Street and the area of Airport Ave. /Fulmor, we were able to find several curb stops and isolation valves as well as hydrants. In order to get a good connection on some of the valves we used the city vacuum truck and a shop vacuum to remove water, sand, mud. We continued to hopscotch down Main Street for the remainder of the day including the area of Harbor View Drive, Lipke Lane and Seldovia Street. We used both the FCS Correlator and the LD- 12 leak detectors, in two separate locations we noted a possible area of concern. The first location being near the intersection of Airport Ave. and the second one was near the Harbor View Intersection. We spent the remainder of the day setting the correlator up in different configurations in these areas. We made arrangements with the operators to meet at the public works building the next day as their shift ended. Steve and I continued to look for leaks in the area at the end of the day we set the correlator up at the end of Main Street and the end of C Street spanning the slough. For this shot we also saw an interesting return midway in the slough that should be looked at further, distance is a major concern here and difficult to be certain of exact measurements required for the Correlators accuracy. We then decided to head back to the filter building to check the flow meters and charge the batteries on the equipment. The next morning we went to the Public Works building to meet up with the operators and plan the day, we all decided to start at the filter building check the flow meters again. When we arrived at the filter building the stationary flow meter was registering about 60 gallons per minute, and the Siemens clamp on meter was registering about 51 gallons per minute. We all agreed we should use the Correlator on the 10” line from the filter building to the chlorination building above, so we all headed up to set the transmitter on the upper end of the line and calibrate the Turbidimeter at the same time. When we returned to the filter building the stationary flow meter was reading was registering 249 gpm and the Siemens meter was reading 170 gpm. This kind of had us wondering what might be going on since the readings changed so drastically within an hour time span. Tyler the water operator made some phone calls and found out that they were filling the swimming pool in town. We finished setting the Correlator up and began receiving data from the two receivers but the signal was very poor and weak, we figured most likely due to the trees, brush and distance. Randy collected a sample of the water seeping from the hillside and check it for chlorine and got a result of 0.19 at the filter building. In the afternoon we decided to take a tour of the wastewater system we looked at the lift stations and septic tank, outfall line. The slough lift station #1 appears to be without any significant problems, the operator did think one of the pumps made a little more noise than the other but both pumps work very well. We observed MH- C12 while the lift station was pumping and noticed some surcharging. We then headed to Lift Station number 1 which discharges into the septic tank. The discharge line on pump number one, leaks while the pump is in operation and needs repair. We measured the sludge level in the septic tank it has approximately 4 feet of solids in the bottom of the tank, there is a broken scum layer on the surface. We then headed to MH D2 which is the final manhole before the septic tank effluent is discharged. The effluent appears to flow out of the manhole through an overflow line from the manhole. The next day went over some of the testing requirements for the remainder of the year and looked at the operators CEU obligations. We headed to the airport to catch our flight back to Homer and on to Anchorage. | 7 | The septic tank has not been pumped in several years, the brush is grown up around the tank and cleared to give easier access to the tank. | Discharge piping on the Septic Tank Lift Station should be repaired. | Leak in the 10" Thin Wall Steel Line between the Chlorine Building and the Filter Building. |  |  | Septic Tank Pumping | Yes |  | No |  | No |  | No |  | No | Septic Tank Pumping | Operator | Discharge Piping on Septic Tank Lift Station | Construction Project | Repair of 10" TWS Line from WST to Filter Building | Construction Project | [5 empty] | Attachments | Other Documents | 2016-09-06 13:32
RMWTR-1385 | TCC | Rampart | Lee Meckel | 2016-07-20 | 2016-07-22 | Routine | [5 empty] | No |  | Name: Ben Newman Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Wesley Shales Title/Position: RMW Accompanied By? No Telephonic Contact? No | [8 empty] | Address the missing well cap found during sanitary survey. | We were able kill the power to the well pump and install the new Well cap purchased by the Tribe. The old well cap had not been put back on due to a gaggle of excess wires that had been stuffed down the casing. The wiring was not only to long it was also compromised through the cracks in the insulation. The wire was a definite health risk. Mr. Shales showed me how to check for power at the pump control box breaker to insure the power was off before we moved on to cutting the excess out and splicing with new wire connections and proper grounding of the heat trace and high power lines. We also had to build our own vent to sit in the well cap. Once the wiring was done we seated the cap and tightened to insure no contaminants could taint the ground supply from the well head. | 16 | Build the box lid of the well head up a bit so the new well cap vent does not interfere with current design. |  |  |  |  | I would also look into adding some metal flashing to the exterior of the box or at the very least staining the existing particle board. | No |  | No |  | No |  | No |  | No | I would also look into adding some metal flashing to the exterior of the box or at the very least staining the existing particle board. | Operator | [9 empty] | N/A | Other Documents | 2016-08-22 16:14
RMWTR-1387 | TCC | Minto | Lee Meckel | 2016-07-18 | 2016-08-19 | Routine | [5 empty] | No |  | Name: Wesley Shales Title/Position: RMW Accompanied By? No Telephonic Contact? No | Name: Dudley Smith Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [8 empty] | Fix pressure pump. | We found that one out of two remaining system pressure pump motors had totally failed. Ultimately it was found that on that setup a pump seal had failed as well. No replacement pumps or rebuild kits for that assembly model etc. were on hand. The operator had said he had trouble getting any parts and when we went online the pump was found to be “obsolete”. | 16 | Another problem we addressed was a failed operation at the backup generator day tank. It was not transferring fuel from the tank farm. A solenoid proved to be operating correctly. Ultimately a failed pump head on the transfer pump was diagnosed as having failed. Part numbers were taken down and we will assist Minto in obtaining replacement parts…. |  |  |  |  | Dudley was told to remove the third failed pressure pump and that at a later date I might end up assisting him in installing one of those other “retired” pressure pumps if they check out ok. Those models were apparently installed in the mid-nineties and one or two of the remaining motors had possibly been replaced before they were mothballed. The plant still retained manuals on them and if parts can be found they could live again. | No |  | No |  | No |  | No |  | No | Address all issues in prior text. | Operator | [9 empty] | N/A | Other Documents | 2016-08-22 15:41
RMWTR-1388 | TCC | Stevens Village | Lee Meckel | 2016-07-25 | 2016-07-29 | Training/Meeting | [5 empty] | No |  | Name: Don Green Title/Position: Other Accompanied By? No Telephonic Contact? No | Name: Brian Menghini Title/Position: Other Accompanied By? No Telephonic Contact? No | [8 empty] | Participate in A.N.T.H.C. energy upgrades at the water plant. | We were able to install many useful new components including new l.e.d. lights threw out the entire water plant. We cleaned the boilers were able to trouble shoot a soot up on the main boiler being used. Once we cleaned it ran like it was intended to. We also insulated the entire well house and added new zone valves to the base board heaters in the laundromat. We fixed two of the leaky mixing valves in the showers. | 32 | We (Don) also noticed during Mr. Smoke’s cl testing that he was using a color wheel for his cl testing and should probably upgrade to a digital Hack DR 900, they can be purchased online. |  |  |  |  | color wheel, and boiler was so dirty is was shooting chunks of ash/ soot out the stack that were the size of corn flakes. Huge co issue but we took care of it. co detectors would be a good idea to prevent a potential co poisoning in the event of another soot up. | No |  | No |  | No |  | No |  | No | It would be beneficial for the plant operator and its users if a portion of the savings could be used to purchase new Tools that are needed to complete routine and preventive maintenance such as a new Hach digital cl tester. Great job to everyone involved. | Community | [9 empty] | N/A | Other Documents | 2016-08-22 16:03
RMWTR-1390 | TCC | Rampart | Lee Meckel | 2016-07-11 | 2016-07-15 | Training/Meeting | [5 empty] | No |  | Name: Don Green Title/Position: Other Accompanied By? No Telephonic Contact? No | Name: Tim Eby Title/Position: ANTHC Engineer Accompanied By? No Telephonic Contact? No | [8 empty] | Assist in the training of new water operator as well as participate in ANTHC energy upgrades at the water plant. | We were able to install many useful new components including new LED light fixtures throughout the entire water plant. We installed a couple of new burners on the boilers and also added new boiler high limit and low limit controls that will drastically reduce the amount of fuel used for heating systems. We also added a programmable setback thermostat that will reduce the air temp when the facilities are closed or unoccupied. We also noticed upon reviewing Mr. Newman’s daily logs that his Cl readings had started to drop over the last few days we were there. When asked about it Mr. Newman had reported that he had noticed the deficiency and had adjusted the diaphragm pump to help increase the concentration of chlorine in the water. We checked it and found that it was still low despite the adjustment. Mr. Green of A.N.T.H.C. suggested that we look at both the components of the pump including the injection point. We did and immediately noticed that there was build up clogging the injection point so no chlorine could enter the raw water line. We cleaned it and monitored the level of Cl over the next couple days until it was as it should be. | 40 | That money that will be saved after this project is completed is undeniable. It would be beneficial for the plant operator and its users if a portion of the savings could be used to purchase new tools that are needed to complete routine and preventive maintenance. |  |  |  |  | cl was low but was corrected. | No |  | No |  | No |  | No |  | No | Finish the job. | Engineer | [9 empty] | N/A | Other Documents | 2016-08-22 16:22
RMWTR-1393 | MHC | Kobuk | Jeff Luther | 2016-08-22 | 2016-08-22 | Routine | $504 | $57 |  |  |  | No |  | Name: Kris McKay Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Alex Wood Title/Position: Local Laborer Accompanied By? No Telephonic Contact? No | [8 empty] | pump sludge out of sludge tanks | Worked on 500 gallon vacuum tank, opened up the engine to free the valves that were stuck from last winters use, pump had no spark so we worked on the on/off switch & put a new spark plug on there, we worked on modifying the loader's hitch so that we can tow the vacuum tank with the loader. We started pumping tank 2 at the farm & the operator & laborer will continue to empty the tank 1 once tank 2 is finished. | 4 | none |  |  |  |  | none | No |  | No |  | No |  | No |  | No | none | Unknown | [9 empty] | N/A | Other Documents | 2016-08-23 09:17
RMWTR-1394 | DEC | Seldovia | Steve Evavold | 2016-08-15 | 2016-08-18 | Routine | $250 | $210 |  |  |  | No |  | Name: Todd Larson City Administrator Title/Position: Accompanied By? No Telephonic Contact? No | Name: Tyler Tucker WTP Operator Title/Position: Public Works Director Accompanied By? No Telephonic Contact? No | Name: Randy Bond City Maintenance Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Jeremiah Campbell CRW Consultants Title/Position: Project Superintendant Accompanied By? No Telephonic Contact? No | [6 empty] | RMW program was requested for assistance with leak detection and estimation of water loss by VSW project manager. While there we were to do inspection of the Reservoir, monitor flow through the "Filter" building, and check on WTP progress. | Arrived in Seldovia and met with Tyler and Randy, operators of the water utility. We talked about historical data, water use, and daily procedures. Seldovia was "Grandfathered in" with filtration avoidance. That is going to change with the new direct filtration-polymer add water plant being constructed. We discussed the changes and new requirements. We hope to inspect the Port Graham water plant(nearby community), with Tyler and Randy this winter. That plant is very similar in treatment and procedure. Kevin and I inspected the distribution system to formulate a plan for leak correlation in the morning and installed the Siemens FP1010 portable flow meter in the filter building. Flow monitoring over the years has been considered inaccurate. In the morning we drove up to the reservoir. The "Gates" for the reservoir supply from the dam are installed so that depending on the time of year the operators can take water from near the surface, or deeper; in mid-column. There hasn't been a water shortage in recent memory, but if the penstock supply were to fail, the reservoir level would drop in short time. There have been a few repairs in the pipe in the last 10 years and current leaks are suspected. On the way down from the reservoir we stopped in to visit with Jeremiah Campbell, CRW project Superintendent. The project is moving ahead on schedule. Concrete for the water plant foundation was being poured. We discussed the break in the transmission line down hill from the water storage tank and above the filter building. Early estimates relayed were about 100,000 GPD. The water is flowing on the surface just above the filter building. There is a HACH SC100 controller with a 1720E turbidimeter up in the altitude building. We took time to show Tyler and Randy how to clean and calibrate the unit. The new plant with have 5 turbidimeters to maintain. Kevin and I set up the Correlator to work Main street from the boardwalk on the south end, northward to the post office. We made several attempts with various contacts over the day and concluded that there is a strong possibility of a leak under the intersection of airport way and main street. There were other smaller indications, but may have been service line usage. We correlated across the estuary, hydrant to hydrant. On a previous trip the operator and myself had isolated that part of town and determined, by the flow meter in the filter building, the GPM's had dropped. The Correlator did display a spike in the center indicating leakage, but not at the level I had hoped for. The next day we retraced the previous days attempts and found the same reactions/displays with the Correlator. We set up the unit to try and pinpoint the leak below the storage tank, but weren't able to get a defined response from the Correlator. We inspected the lift stations, septic tank, and located the terminal manhole for the outfall. The septic tanks is a large concrete structure that rarely gets pumped. The manhole on the outlet side of the tank was partially plugged and will need to be pumped down. The terminal manhole leading to the outfall had debris in it also. Kevin suggested flushing that part of the discharge system more regularly. The boardwalk lift station (south end), was operational. The north end lift station, pump #2, has a blown gasket on the discharge side and sprays half the capacity back out into the well. Pump #1 is used almost continuously. When finished for the day, I detached the portable flow meter in the filter building. The flow averaged 20gpm less than the SeaMetrics FT 420 that has been in operation for years. Overnight for a 15 hour period the Siemens FP1010 showed a flow only 28,000 gallons. The leak between the Altitude building and the Filter building is significant, but if that carrier pipe is not to be used as transmission from new water plant, no repair is necessary. | 8 | The gasket for pump #2 in the north end lift station needs replacing. The operators have a plan in place. As it is a "Confined Space", equipment for safe environment will be needed. |  |  |  |  | Nothing noted at this time. The new water plant will take care of prior deficiencies. | No |  | No |  | No |  | No |  | No | The operators have asked for a visual tour of the neighboring water plant in Port Graham. This will be scheduled sometime after January 1st. | RMW | [9 empty] | Attachments | Other Documents | 2016-09-12 15:20
RMWTR-1399 | MHC | Kivalina | Jeff Luther | 2016-08-23 | 2016-08-23 | Training/Meeting | $180 |  |  |  |  | No |  | Name: Joseph Swan Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Dennis Swan Title/Position: Local Laborer Accompanied By? No Telephonic Contact? No | Name: Ikey Hank Title/Position: Local Laborer Accompanied By? No Telephonic Contact? No | [7 empty] | PMPlan introductions/inspect boiler 2/washer in washeteria | Test boiler 2, was inoperable because the primary control was bad & kept it from running it's normal cycles, adjust temperature settings on boiler 1 & 2, checked one of the washers that was bad in the washeteria, cleaned the screen on the drain pump. Switch was bad & the washer would quit running at drain/spin cycle. Went to the water intake & ran the pump for a while, was losing power from sediments in the impeller & suction hose letting air in, after cleaning impeller housing & changing suction hose pump was operating normal again. | 4 | none |  |  |  |  | change primary control on boiler | No |  | No |  | No |  | No |  | No | change primary control on boiler | Operator | [9 empty] | N/A | Other Documents | 2016-08-24 08:31
RMWTR-1400 | NSHC | Wales | Bryant Koonooka | 2016-08-23 | 2016-08-23 | Training/Meeting | $450 | $75 |  |  | Ravn air/Bering air | No |  | Name: Oscar Menendez Title/Position: VSW Engineer Accompanied By? No Telephonic Contact? No | Name: Debra Addie Title/Position: VSW Engineer Accompanied By? No Telephonic Contact? No | Name: John Herman Title/Position: Consulting Engineer Accompanied By? No Telephonic Contact? No | Name: Lena Mathlaw Title/Position: RUBA staff Accompanied By? No Telephonic Contact? No | Name: Frank Oxereok Title/Position: City Council Member Accompanied By? No Telephonic Contact? No | Name: Lena Sereadlook Title/Position: City Council Member Accompanied By? No Telephonic Contact? No | Name: Kelly Anungazuk Title/Position: City Clerk Accompanied By? No Telephonic Contact? No | Name: Serman Richards Title/Position: Mayor Accompanied By? No Telephonic Contact? No | Name: Sean Komonaseak Title/Position: Tribal Council Member Accompanied By? No Telephonic Contact? No | Name: Ralph Anungazuk Title/Position: Tribal Council Member Accompanied By? No Telephonic Contact? No | Meeting with the community that VSW and CRW has about the new water plant.Talk about the proposed location of the site and a new site. | Meeting John Herman and Oscar Menendez showed plans about where the community wanted to build the new WTP in a previous meeting(site 2).Showed them predictions of future erosion would do if they built it on the old WTP site.That it would be costly if they have to put a sea wall around the WTP at the old site. John and Oscar showed them where they wanted to build it on.It is away from the shore and would be away from the erosion problems.(site 3)This site would have a surface water coming from village creek and would have a lot better water than the well they have now. But the surface water needs to be filtered and treated. WTP would have cartridge filters about 4 up to 6 filters.They would have to chlorinate too while they are pumping water.They were planning to but in a septic tank or a lagoon on the draining side.The community asked if a life water system would work on the WTP/washeteria. After the meeting, we talked to the city council about the best practices score.The city council will do their part on raising the score.Lena Mathlaw ARUC has been working with Kelly Anungazuk City clerk.Lena is helping Kelly and the city on that part of the score.I mentioned to the council they need to hire a WPO alternate and send Zackary WPO to go to training.That there is a training schedule in the State of Alaska website.And the city/WTP must have a preventive Maintenace plan. Water plant: Water level on water storage tank at 21.5 feet.Heat exchanger is working,ice is a little thinner.Ice was 7 to 8 inches when we first started pumping now it is 4 to 5 inches thick. School is filling their water tanks too. Zackary did not receive parts for installing the new heat exchanger. Changing out the old one would help a lot with thawing out the ice in the water tank and keep from future freezing problems.Told Zackary that he needs to start doing PM and do his daily checklist. | 1 | Ice is melting in the WTP but need to change out the heat exchanger. |  |  |  |  | There is a few site glass parts that might need changing. | No |  | No |  | No |  | No |  | No | Change out heat exchanger. | Operator | Replace sight glass parts with coupling and a piece of pipe and union. | [8 empty] | Attachments | Other Documents | 2016-08-26 14:36
RMWTR-1407 | TCC | Circle | Wes Shales | 2016-07-07 | 2016-07-07 | Routine | [5 empty] | No |  | Name: Fred Kameroff Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Jessica Fields Title/Position: Other Accompanied By? No Telephonic Contact? No | Name: Angela Ludwig Title/Position: Tribal Administrator Accompanied By? No Telephonic Contact? No | Name: Lawrence Crow, Jr. Title/Position: Other Accompanied By? No Telephonic Contact? No | Name: Dennis Carroll Title/Position: TUS Accompanied By? No Telephonic Contact? No | [5 empty] | Assist with diagnosing washeteria equipment malfunctions, and assist with installing a new sink and toilet. | We arrived in Circle for this day trip and first met with Mrs. Jessica Fields. We were able to accomplish the installation of the new sink and toilet/parts but found that the treatment plant had no extra parts for the dryers which was initially a misunderstanding. | 2 | Circle is one of Fred’s RMW communities and his is assisting Mr. Crow with obtaining the correct repair parts for the dryers. |  |  |  |  | Spare parts/supplies. | No |  | No |  | No |  | No |  | No | Circle is one of Fred’s RMW communities and his is assisting Mr. Crow with obtaining the correct repair parts for the dryers. | RMW | [9 empty] | N/A | Other Documents | 2016-08-24 14:03
RMWTR-1408 | TCC | Kaltag | Wes Shales | 2016-07-11 | 2016-07-13 | Training/Meeting | [5 empty] | No |  | Name: Racheal Lee Title/Position: Environmental Health Officer Accompanied By? Yes Telephonic Contact? No | Name: Emily Cunis Title/Position: Environmental Health Officer Accompanied By? Yes Telephonic Contact? No | Name: Jeremy Semaken Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Conrad Semaken Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: Richard Burnham Title/Position: Consultant Accompanied By? No Telephonic Contact? No | [5 empty] | Provide site specific training as well as additional training on Hach water testing equipment. In addition, provide assistance with the water plant maintenance. | Training on the use of the Hach DR 820 and 900 as well as a Hach Portable Turbidimeter and how to properly calibrate it was provided to Jeremy, Conrad, and Richard. Racheal and Emily assisted and provided valuable input during the training. Jeremy, Racheal and I spoke about the need and availability for (outside) training, certification, and possible funding for that as well. In addition, a video on the proper maintenance and calibration of the water plant Hach 1720E in-line turbidimeter was used as training material. It was found that the plant didn’t have the calibration equipment or the formazin calibration standard(s). The plant did have some expired formazin standards for the 1720E calibration process. No written material on maintenance or operation of the unit or plant was located either. Before I left for Kaltag I couldn’t locate an O&M manual for the Kaltag plant either. I did find an O&M manual for the mothballed fluoride system though. We went over the daily routine maintenance and provided input and discussed some maintenance concerns and took notes on replacement parts and supplies the plant needs as well. Jeremy, Conrad and I also took a field trip to the water plant well and I took notes. | 8 | Overall I found the water plant to be well maintained and provided for. Jeremy did order some supplies while we were there that we found needed ordering. Also, I am going to research some part numbers and availability and get back to him. In addition, I will assist with locating a source of calibration equipment and supplies for the plant turbidimeter and help ensure that it is sent out to the community. A possible O&M manual will be hopefully located and sent to the community. |  |  |  |  | Overall I found the water plant to be well maintained and provided for. Jeremy did order some supplies while we were there that we found needed ordering. Also, I am going to research some part numbers and availability and get back to him. In addition, I will assist with locating a source of calibration equipment and supplies for the plant turbidimeter and help ensure that it is sent out to the community. A possible O&M manual will be hopefully located and sent to the community. | No |  | No |  | No |  | No |  | No | See critical observations/noted deficiencies. | RMW | [9 empty] | N/A | Other Documents | 2016-08-24 14:19
RMWTR-1409 | TCC | Rampart | Wes Shales | 2016-07-20 | 2016-07-22 | Emergency | [5 empty] | No |  | Name: Lee Meckel Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Floyd Green Title/Position: Tribal Administrator Accompanied By? No Telephonic Contact? No | Name: Ben Newman Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [7 empty] | Respond to recently discovered issue of chafed/knicked wire at well casing/install new sanitary seal. | We traced the routing of the wire feed from the well pump control panel all the way to the well casing. Power was killed to the pump at the pump control panel and verified that it was dead at the well casing. Inspection of the over excess of wire revealed both chaffed and knicked wire with bare copper conductor showing at some locations. The damaged wire was isolated to the approximately 15 + extra feet of well pump feed wire that had been crammed into the top of the casing and had prevented the former sanitary seal from properly seating on the top of the pipe. The excess damaged wire was removed and waterproof splicing was performed on the power feed. In addition, a heat trace for the well casing was “cleaned up”, and a new sanitary seal was installed on the well casing. Also, assistance was provided with maintenance of a water fountain and the rebuilding of handicap ramp walk way at the entrance of the washeteria. Right at the end of our trip in Rampart it was discovered at the point Ben was going over a walk thru of his routine with Lee and I that the older lift station pump was not operating. Even though it was wracking up time on the counter but it was not drawing any amps on the control panel nor did it show to be drawing amps with a portable hand held. Proper voltage was indicated at the control panel and at a tap box in the lift station room with the multimeter. It had not tripped out at the control panel. Ben was told that he needed to get the motor raised out of the lift station. Unfortunately the cable to raise the motor/pump was attached to the other working pump and was “stuck” to it. A series of steps needed to be taken to completely diagnose the situation. Possible problem areas Ben was told could be a compromised splice that was located in a area that sat into the sewage at a near full level. Otherwise, the pump/motor had failed and needed replacement. | 2 | A box covering the well casing needs to be enlarged/replaced to properly fit over the pipe as well as the material it was constructed from needs to be better weather proofed. A replacement lift station pump should be ordered as soon as possible. |  |  |  |  | See critical observations. | No |  | No |  | No |  | No |  | No | Rampart is on of Lee Meckel's RMW communities. | RMW | [9 empty] | N/A | Other Documents | 2016-08-24 14:30
RMWTR-1410 | TCC | Minto | Wes Shales | 2016-07-18 | 2016-07-19 | Routine | [5 empty] | No |  | Name: Lee Meckel Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Dudley Smith Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [8 empty] | Assist with troubleshooting/repair/and or replacement of failed water system pressure pump. | We found that one out of two remaining system pressure pump motors had totally failed. Ultimately it was found that on that setup a pump seal had failed as well. No replacement pump or rebuild kits for that assembly model etc. were on hand. The operator had said he had trouble getting any parts and when we went online the pump was found to be “obsolete”. While inquiring about possible replacement pumps/parts we went out to look in a storage trailer and I about tripped over three assembled pump/motor combinations. The three were quickly measured and motor data was compared with the existing setup(s) inside the water treatment building. They were compatible! A j-box and flexible liquid tight conduit was installed for a new length of wire to feed the motor with. Previous wire had “burnt” up that was routed thru conduit near the old motor head. The replacement pump was sanitized and primed. A quick shot of grease was added to the motor zerk fittings. The motor windings were checked to see if they were grounding out. A bump test was performed and the assembly proved to operate successfully. The pump was put into operation and observed. It had extremely acceptable amp readings and performed flawlessly. While speaking with one of the retired operators Dudley was told that those pump/motor combo’s had been removed and replaced with upgraded models over 10 years ago. Another problem we addressed was a failed operation at the backup generator day tank. It was not transferring fuel from the tank farm. A solenoid proved to be operating correctly. Ultimately a pump head on the transfer pump was diagnosed as having failed. Part numbers were taken down and we will assist Minto in obtaining replacement parts. | 6 | None |  |  |  |  | None | No |  | No |  | No |  | No |  | No | Dudley was told to remove the third failed pressure pump and that at a later date I might end up assisting him in installing one of those other “retired” pressure pumps if they check out ok. Those models were apparently installed in the mid nineties and one or two of the remaining motors had possibly been replaced before they were mothballed. The plant still retained manuals on them. | RMW | [9 empty] | N/A | Other Documents | 2016-08-24 14:40
RMWTR-1411 | TCC | Dot Lake | Wes Shales | 2016-08-11 | 2016-08-12 | Routine | [5 empty] | No |  | Name: Dan Drake Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Marylou Paul Title/Position: TUS Accompanied By? No Telephonic Contact? No | [8 empty] | Troubleshoot hot water tank heating issues, heating system control issues, and boiler analyzer training. | The supply and return loops for the washeteria domestic hot water tanks originate/terminate at the main system supply manifold . Under conditions of high demand and incorrect or lack of proper valving and circ pump operation customers experience no hot water issues at the washeteria. During cold weather periods the village heat loop circ pumps maintain reliable flow thru the loop and proper valving and operation of boiler and loop circ pumps are of a different concern. Dan was experiencing no hot water issues. The only way he could get hot water from the hot water tanks was to operate the village loop circ pumps. After extended observation and manipulation of the heating system components we were able to maintain consistent and adequate hot water. I cleaned up some exposed wiring issues as well as reconnected the proper supply wires for a boiler circ pump and demonstrated to Dan how to maintain a more personalized control of the boiler circ pumps under various conditions. Also, while on location, I inquired with Dan if he had ever performed any exercise or test of the fire pump system and he informed me that no written procedure existed there at the plant. I took down info on the fire pump and its control panel. I also demonstrated to Dan how to operate a Bacharach Boiler combustion gas analyzer. (Model 60) | 4 | An informative operations/maintenance manual for the washeteria boiler system, unit and baseboard heating, and the various heat loop systems or the fire pump was not available at the plant. In addition, no wiring diagrams or schematics were available. As soon as practical Dan and I will write down a step by step procedure for the both the operator control and isolation of the heat loops system and an operations and monthly testing of the washeteria fire pump. |  |  |  |  | See critical observations. | No |  | No |  | No |  | No |  | No | See noted deficiencies. | RMW | [9 empty] | N/A | Other Documents | 2016-08-24 14:50
RMWTR-1412 | YKHC | Akiachak | Bob White | 2016-08-24 | 2016-08-24 | Routine |  |  |  |  | YKHC Boat | No |  | Name: Henery Pasitnick Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Ronald Knoes Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Jonathan Lomack Title/Position: Tribal Administrator Accompanied By? No Telephonic Contact? No | [7 empty] | To help make a chemical pump replacement parts list. Troubleshoot pressure pump controls. Plan water line replacement under old Washeteria. | When I arrived Henry picked me up at the river and we headed to the water plant, once we were there we looked over some repairs they had made in the plant to fix some water leaks. We then sat down in the office with the list of current chemical pumps and discussed what kind of pumps they would like to use. We settled on a peristaltic pump that has worked well in Nunapitchuk. After we looked up the appropriate size pumps we made a list of pumps and spare parts that need ordering. We then looked at the recent work they had done with the pressure pump controls and found that the contacts had welded on the mag starter for pump #2. We then freed up the contacts on mag starter and rewired it to avoid the burnt contact. With this completed pump #2 worked as it should and we put it back into service. We then made the same repair on pump #3. New mag starters are on order but this will keep everything operational until they arrive. We then looked at the alignment under the old washeteria of the water and sewer lines and created a plan to repipe them in arctic pipe as the building is planned to be torn down. The Operators will gather the parts and do the realignment before winter. | 6 | The operators have repaired the leaks on the solder joints in the pressure tank manifold. |  |  |  |  | The hot water heater is leaking. | No | Some of the automated valves need replacement. | Yes | Terminal lift station only has one operational pump. | Yes |  | No |  | No | Notify me if you need help when the mag starters arrive. | Operator | Order chemical pumps. | Operator | Order the parts and do the realignment of the water and sewer under the old washeteria. | Operator | [5 empty] | N/A | Other Documents | 2016-08-29 08:33
RMWTR-1422 | NSHC | Elim | Bryant Koonooka | 2016-09-17 | 2016-09-19 | Emergency | $942 | $225 |  |  | Bering Air | No |  | Name: David Nakarak Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: Roy Daniels Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Donald Davison Title/Position: Local Laborer Accompanied By? No Telephonic Contact? No | Name: Emily Murray Title/Position: City Council Member Accompanied By? No Telephonic Contact? No | Name: Christine Amaktoolik Title/Position: City Manager Accompanied By? No Telephonic Contact? No | [5 empty] | Patch up their leaking WST. | Water treatment plant: Prepped up to start on WST cleaning and repair.Roy Daniels hooked up a 2-inch suction hose to keep the water flowing to the distribution,While we did the WST cleaning and repair.The draw gate valve to the WST does not close all the way. There are a lot of pin holes in the copper piping all thru out the WTP. Water Storage Tank: 9/17/16 Cleaned and drain water storage tank.We took out a lot of rust,took us long time to clean the WST out.Side wall brackets all rusted up.The nuts on the bottom all rusted up too.There was a lot of holes on the bottom too.There is a couple nuts that are almost completely rusted thru. 9/18/16 We started patching up the WST using EP-200 Epoxy Putty.I used a heat gun to keep the epoxy tubes warm.That helped cause once they cool down hard to mix well.We used a torch to dry up the holes and a wire brush to clean the rust off to patch up the holes.We got all the ones that have rusted thru,and some of the deep divets.We ran out of epoxy but we got the main parts that were leaking.Gave the epoxy time to dry.Had Roy Daniels (WPO) mix up 40 gallons. 1% solution to disinfect the WST.Suited up and sprayed the solution on the wall,center post and bottom of the WST.After I was done David Nakarak and Donald Davison closed up the man ways.Did not start filling WST till the next day.Giving the solution contact time of 12 hours. | 24 | Draw gate valve does not close all the way. |  |  |  |  | Rust issues in the WST.Water storage tank needs to be replaced. | No | Pin holes in the copper plumbing in the water plant.WTP needs an upgrade.Change out copper pipes to pvc. | No |  | No |  | No |  | No | Patch up the rest of the divets in WST and or Replace WST.Lots of rust issues in the WST. | Unknown | Replace copper pipes in WTP. | [8 empty] | Attachments | Other Documents | 2016-09-21 16:32
RMWTR-1423 | NSHC | Unalakleet | Bryant Koonooka | 2016-08-29 | 2016-09-01 | Emergency | $504 | $300 |  |  | Bering Air | No |  | Name: John Johnson Title/Position: Other Accompanied By? No Telephonic Contact? No | Name: Steven Evervold Title/Position: RMW Accompanied By? No Telephonic Contact? No | Name: Kolt Garvey Title/Position: Electrician Accompanied By? No Telephonic Contact? No | Name: Dwayne Johnson Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Ken Melton Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No |  | Name: Roger Nicholas Title/Position: Wastewater Operator Accompanied By? No Telephonic Contact? No | Name: Martin Paniptchuk Title/Position: Wastewater Operator Accompanied By? No Telephonic Contact? No | Name: Shannon Hough Title/Position: City Manager Accompanied By? No Telephonic Contact? No | Name: Annette Erickson Title/Position: City Clerk Accompanied By? No Telephonic Contact? No | Calibrate turbidity meters,Fix electrical panel at powers creek,look for leaks on water mains/ services. | Water plant: Cleaned and Calibrated turbidimeters.Changed out SCD probe assembly on the streaming current detector.So that the chemical feed pump could run on auto. Steven Evavold (RMW) installed a flow meter to see how much flow is going into the water storage tank.It was slightly different from what was going into the filters.Steven and John Johnson (RMW supervisor) have been working on the Sc200 and the honey well data logger to get them to read right. Leak detection: We Took the H2O correlator and went to the happy valley loop to see if we can locate any leaks on the water services or water main.We had a few spikes but could not confirm if they were actual leaks as the wind was blowing.Dwayne Johnson (WPO) showed us a leak at the fish plants water service line. Meeting: Shannon Dough (city manager) and Anette Erickson (city clerk) meet with us at the city building.We discussed what we found and what we were doing.Told them about the best practice scoring.That they needed to get the score up to qualify for future upgrades and future projects.Shannon got with Leroy Seppilu (Ruba) and gained another 30+ points.Ken Melton (alternate WPO) got scheduled to go to an operator certification training class. Powers creek: Dwayne Johnson has set up a generator for alternate power so we can keep pumping water as the breaker panel is being replaced.Kolt Garvey (Senior journeyman electrician) arrives with the parts needed to replace the Breaker panel.He starts labeling the wires and seeing where each wire goes.We head back to the water plant to finish up there.Kolt and Donald Johnson stayed to finish up at powers creek. The 10 horse power pump needed heavier gauge wire to keep from tripping.Dwayne found some 8 gauge wire and Kolt went to wire it up.Gained 21.3 gpm over the 7.5 horse power pump. | 30 | Happy valley lift station needs a lot of work.They thought the upgrade was going to start this year. |  |  |  |  | Water leak on the water service for the fish plant.There is probably a lot more leaks here and there. | No |  | No |  | No |  | No |  | No | Calibrate and clean Turbidity meters every month. | Operator | Repair broken Electric service line to powers creek. | Operator | Change out leaking pipe at the fish plant. | Operator | [5 empty] | Attachments | Other Documents | 2016-09-07 13:21
RMWTR-1426 | DEC | Ouzinkie | Steve Evavold | 2016-08-24 | 2016-08-25 | Emergency | $750 | $90 |  |  |  | No |  | Name: Dan Clarion Mayor Title/Position: Accompanied By? No Telephonic Contact? No | Name: Cliff Panamarioff WTP Operator Title/Position: Accompanied By? No Telephonic Contact? No | Name: Robert Katelnikoff Alt WTP Operator Title/Position: Accompanied By? No Telephonic Contact? No | [7 empty] | Trip was scheduled as a response to a water plant failure and at the request of the operator for immediate assistance. | Arrived in Ouzinkie and met with Cliff. Cliff has been "Chasing" the correct dosage of soda ash needed to bring up the pH in treated water for months. The problem had escalated to the point where he needed assistance before he shut down the plant. Ouzinkie's raw water has a significant level of TOC, a precursor to disinfection by-products. To treat this, a Ferric Chloride solution is injected as a coagulant, and then filtered. Once filtered, a soda ash solution is injected to bring up or neutralize the ph before sending it on to the storage tank. We started with a filter backwash, the operator was backwashing every other day. I noticed a build-up of mud-balls through the observation window afterwards and suggested that we do another backwash procedure and be more aggressive with the air scour and increase the backwash flow to maximum flow. This time we could visually see the media in the filter lift and mix, floating the sediment to where the backwash could flush it out. Even so when done there was still 4-5 inches of mud-ball buildup. We agreed a more aggressive backwash will be necessary for filter performance and a longer filter run. We cleaned and calibrated the HACH 1720E turbidimeters. The treated effluent leveled out at 0.03ntu's. The Milton Roy pump used for soda ash addition hadn't been working properly in months and Cliff was having a difficult ime with pH adjustment. There was a new ECC(Electronic Capacity Controller), in a box. The ECC controls the soda ash injection by increasing or decreasing stroke strength. The thought was either to recalibrate the existing unit or replace it and see if the stroke feature of the pump returns. I changed out the ECC and had no corrective reaction. I reinstalled the old ECC. I removed the plate covers to the oil reservoirs to watch the adjustment apparatus as I manually turned the stroke percentage knob. I saw movement giving indication that something mechanical was broke, and drained the reservoir. The connecting rod assembly had snapped. It controls the stroke % for the pump. ANTHC, TUS, had purchased the manufacturer recommended list of critical spare parts for the water plant; the rod assembly was on the list. We repaired the pump to normal mechanical operation, but with removal of the ECC, a recalibration will be required. The pump can be operated in manual mode to 30%. I cleaned and calibrated the 1720E turbidimeters and departed to Kodiak. | 8 | The Electronic Capacity Controller for the soda ash pump needs to be calibrated before full automatic function can return. | Aggressive backwashing with air scour can break up the mud balls, and in turn give the operator a longer filter run. |  |  |  | Nothing noted this trip. | No |  | No |  | No |  | No |  | No | A trip will be scheduled with RMW and TUS consultant for completion of repairs to Milroy chemical feed pump and calibration. | RMW | [9 empty] | Attachments | Other Documents | 2016-09-22 14:24
RMWTR-1427 | YKHC | Kotlik | Billy Westlock | 2016-08-17 | 2016-08-17 | Routine | $270 |  |  |  | Grant aviation | No |  | Name: Wilber Tonuchuk Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Ryan Prince Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | [8 empty] | Site visit Assist eho allisa Gustafson with sanitary survey | I arrived into Kotlik and met with WPO prince and Tonuchuk where we started to look over the water plant, everything was running good and normal. After looking over the water plant I assisted the wpo's with a sanitary survey with eho Gustafson. With everything running good I departed Kotlik at 330 and arrived back in emo at 4. | 0 | None at this time |  |  |  |  | None at this time | No |  | No |  | No |  | No |  | No | None at this time | Unknown | [9 empty] | N/A | Other Documents | 2016-08-29 08:15
RMWTR-1428 | YKHC | Nunapitchuk | Shane McIntyre | 2016-08-25 | 2016-08-25 | Routine | $80 | $0 | $0 | 0 | YKHC Boat | No |  | Name: Bob White Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Molly Berlin Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [8 empty] | Tune up the boilers for both water plants. And give Molly Hands on training on the boilers | We took off from Bethel at 8 am by boat and got to Nunapitchuk at 930 am. We met Molly at the water plant. Bob started the tune up on one of the boilers and was showing Molly and I the components of the boiler and how to clean the parts so that Molly and I can do the other boiler on our own. We took the gun assembly out and changed the nozzle, cleaned the baffle, and adjusted the electrodes, than we took the fan off and cleaned it and the air dampers. Than we got a vacuum and cleaned out the inside of the boiler. We used the testo to fine tune the boilers. We adjusted the air on the second boiler to lean it out a little. We than went over to the other water plant on the west side and did a tune up on those 2 boilers. we took the gun assembly out and changed the nozzles and adjusted the electrodes. than we used a boiler brush and cleaned as best we could. We used the testo to fine tune each boiler. | 7 | The boiler that Molly and I worked on in the East side water plant had a bunch of crap on the bottom on the boiler. It looked like wire bristles and rusty scale. The west side water plant needs correct spare nozzles. |  |  |  |  | none | No |  | No |  | No |  | No |  | No | get correct nozzles for west side water plant | Community | [9 empty] | N/A | Other Documents | 2016-08-29 09:20
RMWTR-1431 | DEC | Unalakleet | John Johnson | 2016-08-29 | 2016-08-31 | Emergency | $328 | $165 | $0 |  | Raven Air | No |  | Name: Dwayne Johnson Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Ken Melton Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: Donald Johnson Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: Rodger Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: Shannon Rough Title/Position: City Manager Accompanied By? No Telephonic Contact? No | [5 empty] | Steve Evavold, DEC RMW out of Anchorage and I were called on to assist Bryant Koonooka Norton Sound Health Corporation (NSHC) RMW with the water quality and treatment issues that the city of Unalakleet was experiencing. A teleconference was held prior to our departure to bring all stakeholders together, gather the facts and develop a game plan prior to our arrival. We also received an email from Lee Johnson and Johnny Mendez DW Fairbanks regarding some of the issues they were seeing and wanted us to address. | Steve and I departed on Raven Air out of Anchorage at 2:00pm on Monday August 29th and arrived in Unalakleet at 3:45pm. We were met at the airport by Maggie Halleran the local hotel owner and then headed to the hotel to check in and drop our gear. We then went to the water treatment plant (WTP) to meet up with the Operator Dwayne Johnson and the rest of the crew. We gave the plant a once over and noticed rite away the Honeywell recorder was showing some error readings. We also noticed that the combined filter effluent (CFE) was showing a higher NTU reading on the SC200 then filter-1 and filter-2 readings. We quickly realized that the terbidimeter heads had somehow been swopped between the basses and the SC200 were showing data from the wrong terbidimeters. We moved the heads to the corresponding SC200’s and were able to clear two of the alarms on the Honeywell recorder. The flow to the treated water storage tank was 52 GPM, we started the booster pump in the plant was able to increase the flow to the tank to 60 GPM. We then made a trip to the Power Creek well house to look over the issues with the control panel and the service panel and breakers. On our way out Dwayne pointed out the area they had repaired the transition line break and the underground power line is still severed in that vicinity due to approximately four feet of settlement in the tundra. A lineman will need to make the repairs in the power cable and that may not happen till October. Dwayne said the lineman mentioned that there were something like 20 line breaks in that section of power cable from the well house to a transformer approximately a quarter mile away. At the well house we took some photos and then looked in the well gallery where the 7HP pump was the only pump running because of the electrical capacity at the panel. Kolt Garvey from ANTHC is scheduled to arrive on Wednesday the 31st to install the new electrical panel, breakers and pump controls. Bryant Koonooka arrived on Bering air at 6:00pm and he met us back at the WTP. We discussed our findings with the turbidimeters and looked over the chemical injection and the stream and current detractor (SCD). Steve brought out a new probe for the SCD that was provided by ANTHC that we will install and then return the old one to them to check for any signs of corrosion and wear. We made a plan for the following day to meet at the plant and broke for dinner. Bryant joined Steve and me over at the hotel as we discussed the issues with the plant over dinner. The next morning at the plant we set up a calibration station for all the turbidimeters and Ken and Dwayne took turns cleaning and calibrating them as part of our onsite training. After the turbidimeters were cleaned and calibrated we had a 0.02 NTU on filter one, a 0.03 NTU on filter two and a CFE of 0.02 with 52 GPM flow to the WST. We had to back off on the booster pump in the plant because the flow was erratic, between 15 and 72GPM. Not sure why, possibly due to the electrical capacity at the pump. Bryant and Dwayne also changed out the probe in the SCD then Steve and Dwayne made adjustments in the chemical dosage and put the plant back in full auto mode. At about 8:30 Dwayne run a back wash on the filters. He said he has to back wash every day in a half to two days depending on water conditions at the creek. After lunch we set up the Correlator to do some leak detection in the Happy valley subdivision. We worked from fire hydrant to flushing port and came up with two very high spikes on the correlator which indicated a leak. We did a visual inspection of the area but could see no indication of a leak. The two leaks seem to be at the main and service line connection. In the past the connections at the service line and pit orifice on the water main have completely detreated. We’re assuming that’s the case in these areas as well. The equipment will need to be repaired and they will have to excavate the area for further investigation. An additional leak was noted a couple days earlier near the fish plant and isolated. That repair will take place in the next few days. The following day we went through the plant again and looked at the flow to the WST on our portable flow meter we installed the day before. We wanted to check the flow over a 24 hour period against the flow meter in the plant. The flows were fairly close, the plants flow meter picks up incoming flow from the Powers Creek raw water line (total flow into the plant). Our flow meter was placed on an uninterrupted section of 4” SCH 80 PVC that picks up flow to the WST after treatment. The minor discrepancy in the overall total flow was from the treatment stream to waste from the SCD and the four tabidameters. We met with Shannon at the city office to give her an update of our findings while I was onsite. And that we expected Kolt in to town on the Raven flight that was scheduled to depart on at 3:45pm. We had gained about a half a foot of water in the WST and we were optimistic that the electrical upgrades would allow the 10HP and possibly the 7HP pumps to run simultaneously to increase flow to the plant. We also discussed the best practices score and the need to get the backup operator in for testing for the provisional certification and to implement the preventative maintenance plan we left with them. Shannon was already in contact with RUBA regarding the bookkeeping and had just been through an audit. They also registered Ken Melton for his training in November. | 16 | All four turbidimeters were not sending the correct data to the SC-200"s. We were able to rectify the issue while onsite by getting the correct head on each of the bases and then cleaning and calibrating each unit. | The SCD needed to be cleaned and a new probe was installed as well as a new section of ploy vinyl hose was installed. | The chemical feed was adjusted and the plant was put back on full automatic. | The service panel and the pump control wiring was replaced and upgraded to NEC code. | We were able to locate two leaks in the distribution system using the correlator equipment. The leaks appeared to be on the water main at the service line connection. | The Honeywell data recorder was not fully functioning. we weren't able to clear all the faults that appeared on the screen. There wasn't a Honeywell operations manual onsite to aid in trouble shooting the issues. A follow up site visit with a little research should solve the issues. | No | Water leaks through out the distribution system. Some have been located, but we feel there are many more to locate yet and repair. | Yes |  | No |  | No |  | No | Leak detection and repairs. | Community | Honeywell data logger programing needs to be corrected and faults outside the recording parameters need to be removed. | Community | Send operator in for testing and certification. | Community | Continue to maintain and calibrate terbidimeters as needed to maintain and report water quality. | Operator |  |  |  | N/A | Other Documents | 2016-09-30 11:24
RMWTR-1432 | DEC | Chenega Bay | Floyd Murphy | 2016-08-25 | 2016-08-26 | Routine | $470 |  |  | Airplane |  | No | 10 miles | Name: Terri Michener Title/Position: Other Accompanied By? No Telephonic Contact? No | Name: George Eleshansky Title/Position: Wastewater Operator Accompanied By? No Telephonic Contact? No | [8 empty] | Work with the operator on the Enforcement Targeting Tool (ETT). Nitrate, Syntonic Organic Compound (SOC) water samples need to be taken. SNC (ETT) list issues to get Chenega Bay off the SNC (ETT) list. Work with the operator on Boiler Training on O & M of boilers. Any other operational problems the operator may be having. | Chenega Bay August 25-26, 2006 8/25/16: I was delayed one day by bad weather to get to Chenega Bay. I departed Anchorage for Chenega Bay on Alaska Air Transit around noon arriving in Chenega Bay around 12:45 PM. Terri Michener, Acting Tribal Clerk gave me a ride to the operators residence. We went to the Water Treatment Plant and went through the ADEC, Enforcement Targeting Tool (ETT). Nitrate, Syntonic Organic Compound (SOC) water samples need to be taken. Once these water samples are taken, along with completing the PMP emergency preparedness plan, they may get back into compliance. Nitrates are to taken annually. Syntonic Organic Compound (SOC) are to be taken quarterly. Note: After 4 quarterly samples are taken, an SOC waiver can be applied for. We than went through the Monitoring Summary for Chenega IRA Village. Current population is still around 50 people. Coliform (TCR): Monthly samples TTHM & HAA5 (DBP2): 1 DBP2 should be taken at the IRA office (Note: The IRA Office has been demolished to be replaced with a new building.) I have contacted Eric Burg, Environmental Program Specialist, at 262-5210 about this matter and left a message for him about a different site for taking a DBP2 water test. Eric was out of his office but will be returning on September 6th and we will make a different site for the DBP 2 test site. SOC: 1 sample quarterly for 4 consecutive quarters that SOC samples prior to reapplying for a SOC Waiver. NOTE: VOC sampling can be sent to a different laboratory at a cost saving for VOC sampling at: Eurofins Eaton Analytical Inc-South Bend, IN 110 South Hill Street South Bend, IN 46617 Phone: (574) 472-5523 Fax: (574)223-8207 They may be approved for other Alaska testing requirements at a savings to community water systems. Nitrate: Overdue: collect ASAP. Note: (Nitrate sample was taken but there were problems with the sample, resampling will occur once new samples bottles arrive.) VOC: Should be taken by the end of the year 2016, the operator ordered a sample kit for VOC sampling TOTAL GROSS ALPHA: Are also due before the end of 2016. TURBIDITY: 1 reading each day per month Test and record daily. Send reports to ADEC on the last day of the month. (Before the 10th of the following month). CHLORINE: Distribution System same time /place as routine TCR samples. Test and record daily. Send reports to ADEC on the last day of the month. (Before the 10th of the following month). CHLORINE: Entry Point: 1 reading each day per month Test and record daily. Send reports to ADEC on the last day of the month. (Before the 10th of the following month). ERP-PMP CERTIFICATION OVERDUE- CWS serving population of less than 1,000 required to complete PMP. CONTACT: Rachel Westbrook with DEC @ 269-8924 for assistance. (Note: I left George with a sample copy of a PMP. Sanitary Survey Corrective Actions: PMP Eric Burg, DEC Environmental Program Specialist contact information: (907) 262-5210 X420 1-888-956-7656 FAX: (907)262=-2294 Eric,berg@alasak.gov Information was given for additional assistance for water testing and sampling and sampling site plan assistance as needed was given. 8/26/16 George and I went to the water plant to assess any additional problems he may be having and have a Boiler Operation and Maintenance (O & M) training session. All covers were replaced on the operation controllers. Boiler operation was explained for combustion. About 4 hours were spent on the boiler O & M. George turned on the compressor for the air wash, nothing happened. The motor was inspected and appeared to be normal, the valves for the air scour were inspected and one was found to be open and another closed causing water to fill the air compressor with water. The valves were closed and opened per instructions for the back-wash procedure. The vacuum pump still did not operate so we got it turning by hand, tried it in the power on and it operated. George was instructed to follow the proper back-wash procedure and valve placement using a back-wash chart hanging on the pressure filters. George was instructed to turn the compressor on for a few seconds every day to make sure it operates. George demonstrated the turbidimeters calibration method to me on both the raw and finished water turbidimeters. The turbidimeters should be calibrated every 3 months and recorded in the Preventative Maintenance plan. The operator should order the sampling kits for SOC, VOC Total Gross Alpha and DBP 2, take these samples and send them in to the laboratory. Take Turbidity readings each day per month, chlorine distribution same time/place as routine TCR sample and Entry point Chlorine 1 reading each day per month. Test and record daily. Send reports to ADEC on the last day of the month (before the 10th day of the following month.) I departed Chenega Bay around 4:15 pm arriving in Anchorage around 5:00 pm. | 8 | The back wash air compressor was not operational. We were able to put the back-wash valving in the proper positions. Drain the water from the compressor and get it operational. The operator should follow the proper valving sequence when back-washing the filters to insure valves are in the normal operating positions. |  |  |  |  | None at this time | No |  | No |  | No |  | No |  | No | Operator to follow proper valving operation when back-washing filters. | Operator | [9 empty] | N/A | Other Documents | 2016-09-01 10:30
RMWTR-1436 | TCC | Circle | Fred Kameroff | 2016-08-30 | 2016-08-31 | Routine | [5 empty] | No |  | Name: Lawrence crow Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Jessica feilds Title/Position: Tribal Administrator Accompanied By? No Telephonic Contact? No | Name: Dennis carroll Title/Position: Other Accompanied By? No Telephonic Contact? No | Name: lee meckel Title/Position: RMW Accompanied By? No Telephonic Contact? No | Name: brian Bearden Title/Position: Environmental Health Officer Accompanied By? No Telephonic Contact? No | Name: racheal lee Title/Position: Environmental Health Officer Accompanied By? No Telephonic Contact? No |  |  |  |  | Repair washers, Repair Dryers Replace Hydronic leak on boiler, add water pressure to boilers Get Grundfos circulating pump going for building heat Run and test boilers | Mr. Lawrence Crow Jr contacted me stating he received the parts for the dryers and washers and asked me to assist him on making the repairs. I told him I can be at Circle on the last week of August. I arrived at Circle airport and was greeted by Mr. Crow and was escorted to the water plant. We than looked at the parts for the washer and dryers, the parts were all correct to make the repairs. Mr. Crow and I began working on the 20 lb Girbau washer, first we removed the front panel cover and installed the new door lock assembly, once we were done with that we put back the cover and tested the washer and to our finding the washer worked normally and we placed it back to service. Mr. Crow also mentioned the top load washer was not working, I asked what was wrong with it and he stated when people put in tokens the washer would not start. I removed the token slide and inspected it and found two things wrong, one the switch on the slider a small bolt was missing, I then made the correction on the switch and the other problem was the token slide was getting hung up on the top of the metal cover so I bent back the front end of the slide and tested it and the slider worked correctly and placed the washer back to service. Once we were done with the washers we turned our attention to 3 out of 4 gas operated dryers. Dryer # 1 will not run at all, so we checked the main breaker for the dryer and found the breaker was not tripped; we then removed the front bottom cover and inspected the parts, and found the motor maybe burned out. Mr. Crow did not have any parts to replace it. Dryer # 2 will not heat up, we replaced the two coils on the solenoid and tested the dryer with one customer who was washing laundry, and the dryer heated up and the clothes dried. Dryer # 3 the dryer drum rollers were worn out, we pulled out the front dryer panel and the dryer drum, then pulled out the old rollers and installed new ones and reinstalled the drum. Then we readjusted the dryer belt to the motor and put the front cover back on and tested the dryer and it operated normally. This resulted in us placing all dryers except dryer # 1 back to operation. The next thing we started to work on was the 1 ½ by 6 inch long black iron schedule 40 nipple on the boiler. The one on the boiler had rusted out this last spring and now is removed and replaced with a new one. On 08/31/16 Mr. Crow came by 9:00 am and we checked the circulating Grundfos pump, which he said will not run. I removed the air screw on the center of the pump and with a screw driver I rotated the impeller and it started to run. It felt like the impeller must have gotten build up on the inside, causing it not to run. Mr. Crow stated he was not feeling too great and asked if he can go home and rest and come back in two hours, I told him that would be OK. Mr. Crow then came by at 1 pm and we added pressure to the boilers by using the water. Once the pressure was set at 20 psi we started both boilers and turned on the circulating pump and heat started to transfer throughout the heating system in the building. Mrs. Jessica Fields asked me to check on the coin timer for the ladies side shower. I agreed and I removed the coin drop, cleaned it with rubbing alcohol, and once I was done I noticed the wires were not placed in the correct places. I than compared it with the men’s side and made the corrections and reinstalled the coin drop and tested it by dropping a quarter and to my finding the shower operated normally. Mr. Brian Bearden, and Mrs. Racheal Lee came up to Circle for the sanitary survey and ask Mr. Crow a few question on operations on the water plant on 08/31/ 16. Also I asked Mr. Bearden if Mr. Lee Meckel can come up and look at the Riello burner just to look at the wiring. Mr. Lee looked at the one burner and found the loose wire was a spare and he capped it with a wire nut. RECOMMENDATIONS/CONCLUSION Mr. Crow was a big help on the washers and dryers also with everything we had done at the water plant and the washsetria. Once the parts are ordered and received for the dryer I will make time to get up and make the correction. Distribution list electronic: | 8 | none |  |  |  |  | none | No |  | No |  | No |  | No |  | No | water operator | Operator | [9 empty] | N/A | Other Documents | 2016-09-02 15:54
RMWTR-1439 | DEC | Unalakleet | Steve Evavold | 2016-08-29 | 2016-09-01 | Routine | $480 | $210 |  |  |  | No |  | Name: Shannon Hough City Manager Title/Position: Accompanied By? No Telephonic Contact? No | Name: Dwayne Johnson Utility Manager Title/Position: Accompanied By? No Telephonic Contact? No | Name: Roger Nicholas WTP Operator Title/Position: Accompanied By? No Telephonic Contact? No | Name: Ken Melton WTP Operator/Maint Title/Position: Accompanied By? No Telephonic Contact? No | Name: Donald Johnson WTP Operator/Maint Title/Position: Accompanied By? No Telephonic Contact? No | Name: Bryant Koonooka NSHC RMW Title/Position: Accompanied By? No Telephonic Contact? No | Name: Kolt Garvey ANTHC Electrician Title/Position: Accompanied By? No Telephonic Contact? No | Name: John Johnson RMW Unit Supervisor Title/Position: Accompanied By? No Telephonic Contact? No |  |  | A series of issues were downgrading the water utility to where immediate assistance was asked for. The water level in the storage tank was losing ground, so the fish processor was shut down. The power line to the pump house had failed and the city was waiting on a lineman for repairs. The pump house for the water supply on Power's creek, now on generator, had electrical issues and the breakers kept tripping so a smaller Horse Power pump was only being used. The water plant instrumentation(SCD, Turbidimeters, data logger, etc.), and chemical feed pumps were not working or displaying/logging correctly. | Arrived in Unalakleet afternoon of the 29th with John Johnson and met with Dwayne and others in the water plant. Bryant, from NSHC, arrived shortly after. We looked at the process controls and saw that the 1720E HACH turbidimeter heads were moved onto wrong reservoirs. Filter #2 head unit was on the body for CFE(combined filter effluent), CFE was displaying filter #2, etc. I checked the Honeywell settings, pen locations, etc. and noted that values had been changed to where several alarms were in constant display. The SCD(Streaming current detector), process value was swinging to wide spread values. We drove out to Powers creek to give the pump house initial assessment. ANTHC, TUS, electrician Kolt Garvey was scheduled to arrive the next day to install new control panels. In the morning we met in the water plant and decided on a plan for the day. ANTHC, TUS, had sent out a new SCD probe assembly to replace the existing unit. Engineering wanted to check if the ferric chloride solution was corroding the contacts. I asked Bryant to work on that. I asked Roger to start a backwash for the filters. While Roger was in “drawdown” process, before the air-scour cycle, I took note of the layer of sludge on top of the media in the filters. There was about 4 inches of accumulation on top of the media. This was after just a 48 hour filter run. Differential pressure was at 7psi. I asked Ken to set up a table for us to start on calibrating the 1720E HACH turbidimeters. They hadn’t been calibrated in almost a year. I showed Ken the procedure for cleaning the bodies, bubble traps, checking the light bulbs for luminescence and moisture, Bryant assisted with that. The 1720E for raw water still outputs to a SC100 controller; Turbidimeters for Filters 1 and 2 output to a newer SC200 HACH controller, CFE turbidimeter outputs to an older SC200. We made several attempts, but could not get the 1720E for the raw water to calibrate to 20ntu’s. The display on the SC100 said “Bad Cal” each time. Ken changed the light bulb with same results. We moved over to the CFE and IFE (individual filter effluent), turbidimeters. Quite often, if the turbidimeters hadn’t been calibrated on a quarterly schedule, they don’t take a good calibration the first time. Both of these took three attempts before “’good Cal” was displayed. Ken said he was comfortable with the procedure and would stay with a quarterly schedule for calibration. Bryant will schedule another trip to assist. When Roger was finished with the backwash and ready for “Filter-to-Waste” I had Bryant turn on the SCD. Set point was at -10.0. When the CFE turbidity dropped enough to send water the tank, I noted 50-53gpm coming from Powers Creek off the 7HP pump. Flow meter on the tank supply pipe was working. Both flow meters, incoming raw, and effluent treated, are questionable for accuracy. The portable Siemens FP1010 flow meter I brought and had working was 20gpm less. The same result as a prior trip showed. The Ferric Chloride feed pump, a Grundfos DDA model, was set to manual for consistent feed of coagulant. I asked Dwayne to put the pump back on Automatic, and we waited for the SCD to recover. The PV(Process value), stabilized on the plus side of the set point so Dwayne increased the dosage on the Grundfos via the “Scaling” menu for the 4-20ma signal. Eventually the SCD PV settled down and ranged from -9.8 to -11.0. I checked the “Jet-wash” for the SCD; it operated as normal manually. I wasn’t sure how to check the automatic timing of the process. I looked into the observation ports on the filters and saw a “blizzard” of floc, which was the reaction of the Ferric Chloride with the raw water. I took a short video of the view and submitted that to ANTHC. The displays on the SC200 after calibration were not correct. The input for filter #1 was reading 0.001ntu’s and input for filter #2 was 0.002ntu’s. CFE displayed 0.000ntu's. John and I scrolled through each menu to note values entered. We made adjustments to the values entered and change decimal places, and arrived at what we considered accurate data. The Honeywell data logger was not displaying anything comparable to the SC200 outputs. The 3 pens designated Filter #1, Filter #2, and CFE for charting/recording were not aligned together in the 0.02-0.04 range as treated water has historically displayed. We researched each menu and submenu applications to decide if anything needed change. By the end of the trip I felt comfortable with the display and what was being recorded. I told Roger to use the data for daily turbidity on the operator reports. In the morning Dwayne, the operators, John, Bryant, and myself met with Shannon Slough; the city manager. We discussed current needs of the plant, Preventative Maintenance Plans, Operator Reports, Sampling requirements, Best Practices scoring, Leak Detection, and the operator certification requirements. Ken and Donald will need certification. Kolt Garvey, ANTHC, TUS electrician arrived. The wiring, breakers, and pump controls were in a dangerous array of loose wires in the Powers Creek pump house; breakers were worn and tripping with the loads. TUS, earlier in the year had inspected and inventoried the electrical needs for the building. Kolt was there to install new panels and controls, and hopefully be able to connect the 10HP pump and send 80gpm of raw water to the plant. Donald was asked to work with him as needed. John, Dwayne, Ken, and I looked at a map of the distribution system to decide on whether a leak detection effort could be done. The distribution system is 4-inch Sched 40 PVC in an arctic jacket. Most leaks in the past have been found on service connections, and located when the water surfaced. Arctic boxes on the houses are checked regularly in the fall for leakage. We decided to correlate between some usable hydrants on the “Happy Valley” loop. After a couple attempts, we could not find a strong response on any frequency that indicated a leak. We went down to the cannery service connections where a leak was discovered the week prior. Dwayne turned the water back on to give us a visual on the quantity of water flow. It was significant enough to impact the water shortage of the past several weeks. We discontinued the leak detection; more preparatory work needs done before another attempt. The storage tank had gained from 5 feet to 6 feet from Monday evening to Wednesday afternoon. Kolt and Donald had the 10HP pump running from the pump house and flow increased to 70gpm. Thursday, we monitored and rechecked settings, outputs, and water quality. The storage tank was still gaining. Compliments to Kolt for the pump house improvements! We left on the afternoon flight. | 16 | Daily monitoring of the plant is required. |  |  |  |  | Water supply from the pump house at Powers Creek is 4 miles out. The transmission line leaks and is in eminent failure mode at all times. The electrical transmission power line has been spliced at least 15 times due to breaks and separations. | No |  | No |  | No |  | No |  | No | A continuation of site visits by RMW program and ANTHC TUS unit consultants is recommended | RMW | [9 empty] | Attachments | Other Documents | 2016-09-16 14:48
RMWTR-1440 | TCC | Nulato | Lee Meckel | 2016-08-25 | 2016-08-26 | Training/Meeting | [5 empty] | No |  | Name: Wesley Shales Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Greg Patsy Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [8 empty] | Troubleshoot reoccurring electrical problems at the old town/uptown water plants. | Mr. Shales was able to determine that a component within a control panel in the lower town site that receives a signal from the WST located in the upper town site water plant was in need of a replacement resistor after failing during certain conditions. This liquid level control component converts line voltage to a low voltage sensing circuit and uses a relay to direct operation of a pump. It was found that the voltage was slightly higher on the low voltage sensing circuit at the component. Other components of the same nature all had a slightly lower sensing circuit voltage closer to the manufacturer recommendation. Also, they had a higher rated resistor. The Ohms value of the sensing circuit resistor is extremely important to correct operation of the component. In addition, other conditions that the manufacturer cautions about were considered, including possible faulty operation when running sensing circuit lead wires with other circuits, grounding issues, and degraded insulation on wires, and broke or loose wires and also including failure of internal parts of the component itself. Nulato has hard water that may be contributing to the failure of the probes themselves inside the water storage tank in the upper town site. Mr. Patsy requested that Mr. Shales investigate a “back feed” that had been looked at by an electrician from a private contractor working on the school that is attached to the lower town site water plant. The contractor looked at one of the panels he had tapped in to for temp power and had mentioned that the box, “was back feeding the neutral” at an electrical sub panel. Upon investigating the situation Mr. Shales determined the three phase panel did not have anything wrong with it. It was receiving power from a 120/240 volt 3phase-4W Delta main panel. He informed both Mr. Patsy and myself that with this unique voltage set up a wild leg (one of the three phases) is not intended to be used for anything but three phase rated motors or devices. `120V or 120/240V single pole/double pole breakers are not to use that position in the panel. The wild leg voltage to neutral is 208 volts. The contractor must not have been aware of the wild leg of power. Also there were a few of the wild leg or b phase of power that did have 120 volt breakers and Mr. Patsy is now aware of them and said he can take care of it. We also looked at the upper town site and noticed that there is a heating loop that services the washateria that has been plumbed with White Rogers’s five wire zone valves that are both on the return and supply of the heating loop (base board). The zone valves were bypassed by the previous RMW and Mr. Patsy has been having to heat the building by leaving the zone valves open in manual and using the circulator pump to get the building warm. We got the 24volt wire connected to the transformer and when we bypassed the thermostat we got power down at the zone valves and were able to determine that the power was not getting through the thermostat. I was also asked to assist with removal of a glycol heat trace that has been decommissioned by the plant operator. I will set up travel to head back and assist in removing equipment. The derelict plumbing is taking up valuable maintenance space and blocks many components that are still being used in the uptown site washateria. | 8 | Use the 3.3 kW resisters if the smaller ones continue to burn out, if this does not work then we might want to look into implementing an inline surge protector to the panel. |  |  |  |  | There is a heating loop that services the washateria that has been plumbed with White Rogers’s five wire zone valves that are both on the return and supply of the heating loop (base board). The zone valves were bypassed by the previous RMW and Mr. Patsy has been having to heat the building by leaving the zone valves open in manual and using the circulator pump to get the building warm. | No |  | No |  | No |  | No |  | No | Mr. Patsy had requested that I return to help finish the upper towns demo and get the heating loop back to being automated. I also was asked by Mr. Patsy to bring back a new thermostat for the zone vale and to locate more of the 3.3 kW resisters. | RMW | [9 empty] | N/A | Other Documents | 2016-09-13 13:34
RMWTR-1441 | TCC | Circle | Lee Meckel | 2016-08-31 | 2016-08-31 | Routine | [5 empty] | No |  | Name: Rachel Lee Title/Position: Environmental Health Officer Accompanied By? No Telephonic Contact? No | Name: Brian Bearden Title/Position: Environmental Health Officer Accompanied By? No Telephonic Contact? No | Name: Fred Kameroff Title/Position: RMW Accompanied By? No Telephonic Contact? No | Name: Lawrence Crow Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [6 empty] | Trouble shoot a boiler/burner that had been giving the operator some trouble. | I accompanied Brian Bearden and Racheal Lee on their sanitary survey to assist R.M.W. Fred Kameroff in trouble shooting and preparing the boilers and burners for winter use. There was a Riello burner that had been giving the operator issues so while Mr. Kameroff and Mr. Crow were working on the washers I was able to get the burner running. We then noticed that there was no pressure in the hydronic portion of the boiler. So we fillied it up and got the boiler to 12 psi and bled some of the air from the line using a ball valve until it was pressured up between 12 and 14 psi. | 2 | The Cl reading was a little higher than necessary to achieve disinfection. |  |  |  |  | I believe the high reading of cl was attributed to the fact that the pre mixed batch being injected was nearly depleted and there for was probably injecting a higher concentration than usual on account of settling. | No |  | No |  | No |  | No |  | No | Keep the water tank hatch closed at all times to ensure that nothing can contaminate your reserve. | Operator | [9 empty] | N/A | Other Documents | 2016-09-13 13:50
RMWTR-1442 | DEC | Tatitlek | Kevin Schoneman | 2016-09-07 | 2016-09-09 | Routine | [5 empty] | No |  | Name: Ricky Kompkoff Title/Position: Environmental Health Officer Accompanied By? No Telephonic Contact? No | Name: Dylan Geffe Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Jenny Vlasoff Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: David Totemoff Title/Position: Tribal President Accompanied By? No Telephonic Contact? No | [6 empty] | Routine Site Visit. Address Sanitary Survey Issues, site sampling plan and sample collection procedures | 9/7/16 I departed Anchorage@ 1400 and arrived in Tatitlekat about 1500. I was met at the airport by operators Jenny Vlasoff and Dylan Geffe. Dylan and I headed to the village office building to drop my bags off. Jenny joined us there at the office a short time later, we discussed what we would like to accomplish the rest of the day. We decide to begin at the water storage tank, the water storage tank is approximately one quarter of a mile from the water treatment plant. The tank holds 150,000 gallons and is in very good condition. I noticed only two very small wet spots, not really leaks. One of the deficiencies that was pointed out in the sanitary survey, was both the vent and the water tank overflow had no screen protection. The screen material used for the initial construction was completely deteriorated. We all climbed to the top of the tank and began removing the 22 9/16 bolts that hold the screen securely in place, Jenny made one trip back down to the water treatment plant to get a pair of vise grips for the badly rusted bolts. We removed the flange and replaced the screen. We also worked on the hatch on the top of the tank, the operators will look for a pin or lock for the cover. We then moved down to the tank overflow outlet replaced the screen over the end. After we were done we gathered our tools and ladder and hiked back down to the water plant. After a short stop at the water plant we headed back down to start looking over the distribution system. We went to look at one of the areas where there was a suspected leak near the village office building. The next day we all met back at the village office to start looking at the drawings of the distribution system and looking for isolation valves. We located one suspected leak near the village office the day before. The location of the leak was in an area that shouldn't have had any water service. We turned off a couple of service connections in the area to see if the water flow may slow down or quit. While we were waiting we decided to walk out to the "Mariculture Building" the building has water service but had been shut off quiet some time ago. When we got back the flow at the leak area had not slowed down. We tested the water for chlorine and got a .54 for residual. We stopped in the office and met with Ricky Kompkoff the IGAP coordinator and David Totemoff the IRA President to let them know what we had found. Ricky said he would try to get in touch with one of the equipment operators for the village to dig in the area of the suspected leak. Dylan, Jenny and I left the office and went to the water plant. Dylan gave me a tour of the water plant, we looked at the log books and started a back wash of the filters. We discussed the recent positive total coliform results, I asked Dylan to demonstrate his sampling method. We all discussed proper sampling procedures, I demonstrated the sampling procedure using a cap full of bleach to disinfect the end of the tap before collecting the sample. Both Dylan and Jenny said they would start using a small amount of bleach when collecting the samples in the future. After lunch we met back at the village office and started to work on the site sampling plan and hand digging in the area of the suspected leak. We dug down a couple of feet until we hit a large rock and could not remove it. The next day we spent several hours in the area of the old water storage tank for looking for isolation valves. We all agreed that the valves we looking for were either buried or removed during construction of the distribution system. After meeting with Ricky is agreed that there may need to be a scheduled distribution system shut down to make the repair. I left Tatitlek in the afternoon and arrived back in Anchorage at 5:00. | 8 | Water leak repairs. |  |  |  |  | Lighting in the water plant. | Yes |  | No |  | No |  | No |  | No | Locate additional isolation valves in the village. Repair problematic sewer service line. | Community | [9 empty] | Attachments | Other Documents | 2016-10-03 11:13
RMWTR-1443 | TCC | Arctic Village | Fred Kameroff | 2016-09-13 | 2016-09-14 | Training/Meeting | [5 empty] | No |  | Name: Robert Eric Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Racheal Lee Title/Position: Environmental Health Officer Accompanied By? Yes Telephonic Contact? No | Name: Johnny Mendez Title/Position: Other Accompanied By? Yes Telephonic Contact? No | Name: bernard Walker Title/Position: Other Accompanied By? Yes Telephonic Contact? No | [6 empty] | Mr. Johnny Mendez, ADEC inspection on the new water plant. | Mr. Johnny Mendez contacted me, Mrs.Racheal Lee, Mr. Brian Bearden if we would like to head up to Arctic Village for an inspection of the new Water Plant, we agreed to come along, but Mr. Bearden could not make the trip up. We arrived in Arctic Village on 09/13/16 and were greeted by Mr. Robert Eric, and escorted to the water plant by Mr. Limit Ross. Mr. Bernard Walker came to Arctic Village to help train Mr. Eric with treatment and operations on the new conventional water treatment plant. Mr. Walker asked Mr. Eric to get the river pump set up to start pumping and treating water. We then assisted with getting the river pump and hose set up with Mr. Eric at the Chandalar River. Once the river pump was set Mr. Eric turned on the pump and started to pump water into the Conventional treatment system. At 20 gallons per minute it took about 2.5 hours to pump water into the media. Raw water turbidity coming into the treatment was at 2.5 NTU and once it pumped through the filters it was 0.04. Once the turbidity reached below 0.2 NTU the valve opened and started to pump treated water into the water storage tank. As the conventional treatment was pumping Mr. Walker and Mr. Eric were having trouble setting the K factor for the Streaming Current Detector (SCD), once it was set the SCD would stay on as it was designed to. The other problem was the Clay Valve needed to be reset to allow the system to pump at 20 gallons per minute, Mr. Walker reset the setting on the Clay Valve and the system started running at 20 gallons per minute. During the night the pressure pump kicked on and once it reached the shut off it had a large water hammer. This is a problem with Schedule 80 PVC piping on the water pressure side, if it continues to hammer the PVC can break and cause the lower level of the plant to fill up with water. By next morning Mr. Eric started the back wash cycle, however the valves to drain the water from the filter media to a certain level would not drain out any water on both filter # 1 and filter #2. We then removed the outer side pipe by unscrewing the nut on the valve and found the screens were clogged with scum. Mr. Eric attempted to clean them out with a vacuum but was unsuccessful. Mr. Walker then asked Mr. Eric for a drain hose and hooked it up the bottom drain valve and drained out the filters. Filter 1 then started to backwash, filter 1 and filter 2 both backwashed once the water in the media dropped to a certain level. After the back wash was complete Mr. Eric then started up the river pump and began to treat water to waste until the turbidity reached down to 0.2 NTU and then sent the potable water into the water tank. Mr. Eric mentioned he turned off boiler # 2 due to the pressure relief valve (PRV) blowing out at 13 psi, and that the Hydronics on the dryer side was leaking. I told him this is a warranty issue and needs to be addressed by the contractor and/or Village Safe Water to have corrected. RECOMMENDATIONS/CONCLUSION I contacted Mr. Eric on 09/23/16 and asked if the leak on the Hydronics was fixed, he stated that the leak was getting worse and that he does not have a torch to reseal the joint on the copper tubing. I then told him I will contact Ms. Debra Addie on this issue to get it corrected. Mr. Johnny Mendez and Mr. Eric found a problem with the Chlorine mixing tank and the Chlorine solution tank. What they found was the mixing tank was not transferring into the solution tank: The drain on the mixing tank was about half way up which should be lower to drain most of the solution into the lower tank. The bottom of the lower tank may have a check valve not allowing the Chlorine solution to enter the tank. This was reportedly installed to keep the LMI pump from losing prime. | 8 | Chlorine tank needs to be corrected, media screens need to be replaced, pressure switch needs to be reset |  |  |  |  | none | No |  | No |  | No |  | No |  | No | CRW need to head back up and make the necessary corrections | Construction Project | [9 empty] | N/A | Other Documents | 2016-09-23 09:09
RMWTR-1444 | TCC | Birch Creek | Fred Kameroff | 2016-09-06 | 2016-09-07 | Routine | [5 empty] | No |  | Name: Vincent Williams Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Walter Williams Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: Brian Bearden Title/Position: Environmental Health Officer Accompanied By? Yes Telephonic Contact? No | [7 empty] | Check on the Radiant mixing block for the add heat for transmission line; prepare water system for winter. | I contacted Mr. Vincent Williams and told him I and Mr. Brian Bearden are planning to head into Birch Creek and check on the add heat pump to prepare for winter. He agreed for us to come in. We landed at Birch creek on 09/06/16 and were greeted by Mr. Vincent Williams and went to our lodging where we would stay for the night. Once we were settled in we met up with Mr. Williams at the water plant and started to look at the Taco brand Radiant Mixing Block RMB-1 for the add heat to the transmission line. After close inspection of the RMB-1, Mr. Bearden noticed that it needed a switch to turn on the pump. Once he had installed a switch the heat started to transfer throughout the transmission line. Mr. Vincent Williams stated two of the four filters were reading zero once the pump is running and asked me to look at it. I informed him to remove the case for the two filters and look at the cartridges, once he done that I noticed the inside of one filter was packed with silt. This is the reason the pressure filters would not pressure up to 30 psi when the pump runs. After replacing the filters with new ones the pressure went up to 30 psi and we placed to unit back to normal operation. The circulating pump for the raw water transmission line was running a little hot. I showed Mr. Vincent Williams and Mr. Walter Williams how to bleed out the air and check if the pump was running by unscrewing the screw on the pump. Once that was done the pump ran cooler and was circulating through the transmission line. RECOMMENDATIONS/CONCLUSION The transmission line now has heat running down to the well house and is heating it also. Mr. Williams asked me to look into ordering new water filters and have them shipped out to Birch Creek. | 8 | none |  |  |  |  | none | No |  | No |  | No |  | No |  | No | operator | Operator | [9 empty] | N/A | Other Documents | 2016-09-23 09:16
RMWTR-1445 | YKHC | Quinhagak | Bob White | 2016-09-06 | 2016-09-09 | Routine | $340 | $100 |  |  | Raven Air | No |  | Name: Bob Tsigonis Title/Position: Consulting Engineer Accompanied By? No Telephonic Contact? No | Name: Will Kemp Title/Position: Design Engineer Accompanied By? No Telephonic Contact? No | Name: Carl Kaplan Title/Position: Project Superintendant Accompanied By? No Telephonic Contact? No | Name: Frank Jones Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [6 empty] | Inspect construction of new life water sewer systems and water haul system. Locate leak in the forcemain glycol line. | 9-6-2016 When I arrived with Bob and Will we were met by Carl at the airstrip we then headed to the project office. We then made plans to look do the training at 1300hrs at Fannie Moores house. I met with frank at the utility building and we began air testing the glycol line. with about 10 PSI in the line we began to go and check connection with windex. unable to find any leaks in places we expected we ate lunch and headed to the lifewater training. We went over operation of the life water unit opening it up and looking at the internal parts. once we had gone over it completely we then repeated this with Fannie. Then we turned our attention to the water tank system and the interior plumbing. Once we completed the training we headed over to look at the neighboring units. Frank and I then turned our attention back to finding the Glycol leak. We started by re pressurizing the line with water keeping track of how much we were putting back in. with the line up to 30 PSI we noticed a steady drop but we were unable to locate a leak still so we added blue32 dye to the line and circulated it. After pumping in a strong dye dosage we were still unable to see any leak so at 2000 hrs we called it a night and left the line with 30 PSI of dyed glycol and water. 9-7-2016 We started back up at 0800 hrs by pressurizing the line to 30 PSI and walking the line to look for a leak. We found a slight green color about the size of a dinner plate next to a road crossing. We then started to check the pipe at the joint kits each side of the road crossing but they were dry. We then attended the homeowner training classroom portion held at the school. It was only attended by one homeowner representative Frank and myself. Once we got back to our leak site we borrowed a mini exscavater from the project and started to dig out the road. Once we were able to expose the buried pipe we saw a abandoned helical anchor pushed through the bottom of the pipe. We were able to cut back the insulation and clearly see the problem. with it getting late we shut down for the night at 1930 hrs. 9-8-2016 We started back up at 0800 hrs by preparing to raise the pipe to make repairs. The project assisted with this through bring blocking and providing the large excavator to lift the line. Once we had the line raised up Frank and I began cutting the jacketting back further to make the repairs. We got our patch all ready then the Project crew came by and used the electrofuser to fuse our repair in place. Frank and I then re pressurized the line and found no leaks. So we proceeded with re-insulating the line. then we lowered it back down onto new bedding that we installed and rebuilt the road to a shorter size that matched the culvert available. We finished up at 2000 hrs so I missed the flight out. 9-9-2016 0800 hrs. We checked the pressure and it had only dropped a couple pounds. We worked at bleeding more air from the system and refilled it to 30 PSI. I finally got on a plane 1100 hrs. | 32 | We have helical anchors heaving all over the community. | This leak was caused by a poor installation of the pipe over a abandoned helical. |  |  |  | The waste heat line to the Washeteria is not pressurized so it is not delivering any heat to the washeteria. | Yes |  | No |  | No |  | No |  | No | Work with City to get washeteria line pressurized. | RMW | Grinder pump stations need to be leveled before winter or we will lose a lot of customers to frozen lines. | [8 empty] | Attachments | Other Documents | 2016-09-26 13:45
RMWTR-1446 | TCC | Tetlin | Lee Meckel | 2016-09-14 | 2016-09-16 | Routine | [5 empty] | No |  | Name: Wesley Shales Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Mike Sam Title/Position: Water Operator Accompanied By? Yes Telephonic Contact? No | Name: Ricky Nyswer Title/Position: Water Operator Backup Accompanied By? Yes Telephonic Contact? No | Name: Johnny Lillie Title/Position: Water Operator Accompanied By? Yes Telephonic Contact? No | Name: Dan Drake Title/Position: Water Operator Accompanied By? Yes Telephonic Contact? No | [5 empty] | Assist with repair/improvements to Tetlin well pump casing in response to Level 1 RTCR investigation findings.. Also perform high pressure pump test at Tanacross with Operator and “pass thru visit/conversation” with Dot Lake Operator. | In Tetlin we dug 6’down to the location of the old pitless adapter at the well casing and installed a cap fitting that I had previously purchased while in Tok. The old discharge line from the pitless adapter had previously been sheared off due to the terrain shifting. At some time in the past, the discharge line had been rerouted through the top of the well casing and in through the side of the washateria. The old discharge line below ground through the well casing was abandoned and the new discharge line was routed out the sanitary seal. When trying to determine the source of contaminants that may have contributed to the hot total coliform samples from last month we had a discussion with Public Health Service Officers Kyle Wright and R.M.W. Program Manager Brian Bearden. It was determined that the break in the old pitless adapter was a potential source of contamination and that it would be a good idea to address it before the ground around the well was built up. Wiring and heat trace to the well was cleaned up and a new sanitary seal was installed. The well casing and all of the distribution system was disinfected for a twelve hour period and flushed. Extensive follow up procedures/instructions were discussed with the Tetlin crew with respect to further testing as well as finishing the work around the well casing that needed to be completed. While in Tanacross we discussed with Mr. Lilly how the plant was performing and then proceeded to perform a pump test of the high pressure pump system. Johnny appreciated the follow up/refresher on the pump procedure. We continued on in to Dot Lake where we had a quick discussion with Dan as to plant performance and the heating system operations and went over some minor concerns he had with an aqua stat that had been controlling a circ pump. | 9 | I have also expressed the need to add grout/cement around the well casing and to build up the ground around it as ADEC has instructed. The Tetlin crew was addressing those needs as of our departure. |  |  |  |  | We have had extensive conversation/consultation with the Tetlin crew about the need to construct a new insulated housing around the well head and supply piping/wiring, as directed in the RTCR Level 1 follow-up letter from ADEC. | No |  | No |  | No |  | No |  | No | As of 09/26/2016 I have contacted the Tetlin Tribal Administrator to follow up with the progress and was the project is under way with the ground already being build up around the well. The insulated well house and water line piping are going to be constructed this week. Tanacross and Dot Lake are doing well and both operators will continue to keep in contact with Mr. Shales regarding any concerns they have. | Operator | [9 empty] | N/A | Other Documents | 2016-09-26 14:18
RMWTR-1448 | YKHC | Napaskiak | Bob White | 2016-09-15 | 2016-09-15 | Routine |  |  |  |  | YKHC Boat | No |  | Name: Nelson Egok Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Brian Lefferts Title/Position: Environmental Health Officer Accompanied By? No Telephonic Contact? No | Name: Tom Bobo Title/Position: Other Accompanied By? No Telephonic Contact? No | [7 empty] | Replace plumbing on water storage tank heat exchanger. Meet with the tribal council. | I arrived by boat and walked to the water plant were I met Nelson. i started to look over the parts while Nelson headed down to the boat to bring up my tools. We then sketched up a plan of how we would assemble the parts before cutting out the old piping. Once we had all the piping removed we started to clean and reassemble parts. We completed the re-plumbing an hour before the council meeting. Tom and I then got a ride to the tribal office and waited for the meeting to start. Brian arrived just as the meeting was starting. We were able to talk about what the RMW program does for the village and how our Utility Management program can help in a similar way. After answering questions from the council we departed back to Bethel by boat at approximately 1900 hrs. | 6 | The heat exchanger piping had a large amount of corrosion probably do to over pumping. |  |  |  |  | Vacuum relief valve on the watering point needs replaced. | Yes |  | No |  | No |  | No |  | No | Replace all plywood and insulation on the bottom of the building. | Operator | [9 empty] | N/A | Other Documents | 2016-09-26 16:28
RMWTR-1449 | DEC | Angoon | Floyd Murphy | 2016-09-14 | 2016-09-16 | Routine |  |  |  |  | Airplane | No |  | Name: Paul Thomas Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Daniel Fredrickson Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Albert Kookesh III Title/Position: Other Accompanied By? No Telephonic Contact? No | [7 empty] | Familiarization with Angoon water and wastewater systems, work with the opreators on Significant Non Compliance issues. | 9/14/16 I departed Juneau for Angoon around 8:00 am, arriving around 8:40 am. I was met by the operators Paul Thomas and Daniel Fredrickson. We went to the water treatment plant, along the way a chlorine sample was taken on the water distribution line near the water plant. The reading was 1.7 coming out of near the WTP. Paul reported that two days before I arrived the plant was shut down normally for a back-wash of the filters. Upon completion of the backwash the well pumps were turned on again but pump 1 did not turn on as it normally does. The operators gave me a tour of the plant and operations, we than went to the lake water source Pump 1 was not operating it appeared to be in the stand-by mode however the operators stated that it should operating. The control for the pump is a power Flex 70. Using the pamphlets that were on hand we attempted to get it going. Unfortunately we were unable to do so. We stopped at the community office building and met with the Grants Administrator, Albert Kookesh III. I informed him that I was the DEC RMW assigned to Angoon and would work with the operator on the Enforcement Targeting Tool (ETT) (Also known as the Significant Non Complier list (SNC list)). On the most current ETT list of July 2016, Angoon needs to submit monthly report with all EP chlorine readings at or above the required EP level and by working on operational changes/system upgrades to lower the DBP’s. Once DBP samples that are low enough to allow the LRAA to be below the MCL we can RTC the vios. (EP=Entry Point, DBP’s= Disinfection by Products, LRAA= Locational Running Annual Average (Stage 2), MCL= Maximum Contaminate Level (type of violation) RTC= Return to compliance. Needs to work on operational changes/system upgrades to lower the DBP’s is Known Hardware Problems. I also gave Albert a copy of the Monitoring Summary for Angoon Public Water dated: February 19, 2016. The following requirements need to be addressed: Sanitary Survey, every three years, by the end of the year 2016. Coliform (TCR) Monthly. 1 Sample Monthly, Last Sample 12/2/13 Total Trihomethane, 1 sample(s) quarterly, Last Sample 8/11/15 Stage 2 TTHM Samples from: Upper- Paul Thomas APT. 1 Sample February, May, August and November. 1 sample(s) quarterly, Stage 2 HAA5 Samples from: Lower- John Silva House -1 Sample February, May, August and November. SOC Waiver should be applied for by the end of the year 2016. Nitrate; 1 Sample by the end of the year, 2016. VOC, 1 Sample Annually, by the end of the year, 2016. Emergency Preparedness Regulation, ERP-PMP CWS less than 1,000 people, required to complete Priority Measures Plan. Due 08/20/2013 Paul and Dan picked me up around 9:00 am. We went to the water treatment plant and worked on the Power Flex 70 trying to get it operational. We called Kolt Garvey, ANTHC Electrician for things to look for and program to attempt to get it functioning. Kolt said he would call Allen Bradley manufacturer of the Power Flex 70 and get their assistance with troubleshooting. The differential on the filters was nearing the maximum differential so they backwashed the filters. We also went through the same material that I presented to the Grants Administrator. The operators should apply for upgrades and certification testing to get within the community System Type / Classifications for the Water Treatment, Water Distribution and Wastewater collections. It is unknown when the water storage tanks have been last cleaned according to the operators, a future date is needed to clean 1 tank at a time there are three tanks total. Recommendations for purchase from ANTHC, AUSC: Turbidimeter lamps 6 Each The 10 inch, swabs for pigging. 2 Each Formazin 4000 NTU 100 mL standard to calibrate the turbidimeters. 1 Each 5 mL disposable pipette 1 box Item 30278 Bluebook 1 Each I departed Angoon for Juneau around 8:50 am arriving around 9:50 am. I checked into Alaska Airlines, departing around 1:50 pm arriving in Anchorage around 3:34 p. | 12 | The Power Flex 70 for water well pump #1 was inoperative, ANTHC Electrician Kolt Garve was contaced for advice. |  |  |  |  | Not all wastewater pumps were online, appears to be having problems for quite some time | No | ANTHC is schedualed to work with the community on addressing some if not all of the problems with the wastewater system. | No |  | No |  | No |  | No | Work with ANTHC Electrician to correect Power Flex 70 problem. | Operator | [9 empty] | N/A | Other Documents | 2016-09-27 14:57
RMWTR-1450 | YKHC | Alakanuk | Billy Westlock | 2016-09-22 | 2016-09-22 | Other | $88 |  |  |  | Personal skiff | Yes | 21 miles | Name: Desi Ayunerak Title/Position: Project Superintendant Accompanied By? No Telephonic Contact? No | Name: Allen Hanson Title/Position: City Administrator Accompanied By? No Telephonic Contact? No | [8 empty] | Take a look ar the erosion problem in two areas concerning the water main and sewer main. | I got a call from a local who was doing a little project on removing a little part of water main and sewer main in two areas of the east loop. When I arrived they had already moved one area back about 100 feet in the loop right below the city office. In this area there was no service connections only where they relocated the loop right on John Aloysouis service box which is about 100 feet back. In the other area was at the end of the east loop around the residence of Allen Hanson, this end of the loop was about 4 feet before it falls into the river. The crew will cut this main about 80 feet back to Allens service box and reconnect the loop there, this will give them time to think about what they are going to do about relocating the homes around that area which is eroding pretty fast due to high winds and high waters. The city needed 3 electro fusion couplings 6 inch which I will try and locate for them. | 0 | I will keep in touch with locating electro fusion couplings and when they will cut the pipes. |  |  |  |  | None | No |  | No |  | No |  | No |  | No | I will call and find out when the relocate is completed | RMW | [9 empty] | N/A | Other Documents | 2016-09-29 09:23
RMWTR-1451 | YKHC | Nunapitchuk | Bob White | 2016-09-27 | 2016-09-27 | Routine |  |  |  |  | Raven Air | No |  | Name: Molly Berlin Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Raymond Alexie Title/Position: Other Accompanied By? No Telephonic Contact? No | [8 empty] | Fix combustion problem with boiler #2 | I arrived by boat and went to the Washeteria were I was met by Molly we shut down boiler #1 and started boiler #2 we observed a small odd shaped flame and noticed a bad odor. Raymond came and we discussed the work he had done on the boiler and then shut down boiler #2 and started to disassemble and clean the gun. Once we reassembled the gun we were still unable to get a good flame as we only had 60 PSI of fuel pressure after attempting unsuccessfully to adjust the pressure I contacted the Manufacture technical support and they walked me through low fire fuel adjustment. With 125 PSI we were able to get the flame to look better and burn more efficiently. We then adjusted both boiler #1&2 for draft and efficiency with the wind calm outside we were not able to use the same damper settings as had been previously used. Once we established the new settings we were able to get boiler #1 to run at 84% efficiency and Boiler #2 to run at 82% efficiency. With the boilers tuned I discussed the water operations with molly reviewing corrosion control and polymer injection. As well as noted some work that the maintenance need to do on the fuel line under the building. I then departed by plane to Bethel. | 5 | Some roofing material need to be fastened back down as it is a little loose and may be damaged in a winter storm. | The fuel line has water in it. | The boilers are horrible to keep tuned properly as they are just to oversized. |  |  | Water in the fuel line. | Yes | 2' of chimney needs to be added to Boiler #2 to raise above roof line. | No |  | No |  | No |  | No | Repair loose metal on roof. | Community | Drain water from fuel line and add mud leg. | Community | Add 2' section of chimney to Boiler #2 | Community | [5 empty] | N/A | Other Documents | 2016-09-29 10:00
RMWTR-1452 | YKHC | Emmonak | Billy Westlock | 2016-09-27 | 2016-09-27 | Other |  |  |  |  | Personal atv | Yes | 2 miles | Name: Arthur Redfox Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Jamie Agwiak Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: Emmanual Mike Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | [7 empty] | Assist wpo troubleshoot the chemical feed pump for the water treatment plant. | I received a call from wpo Redfox wanting assistance with troubleshooting the chemical feed pump for the water treatment plant. For a while the chemical feed pump would not pump or gain any pressure going to the water treatment plant, the operators cleaned everything from the hoses to the pump side of the chemical feed. The pump would not feed, so we disassembled the pump side of the chemical feed cleaned again and found that the check valve wasn't working properly, so we changed both the check valves on the pump, put back the pump side tried it again, now the pump back in normal operating mode. | 3 | None |  |  |  |  | None | No |  | No |  | No |  | No |  | No | None at this time | Unknown | [9 empty] | N/A | Other Documents | 2016-09-29 09:35
RMWTR-1453 | DEC | Old Harbor | Steve Evavold | 2016-09-27 | 2016-09-28 | Routine | $750 | $90 |  |  |  | No |  | Name: Rick Burns Mayor Title/Position: Accompanied By? No Telephonic Contact? No | Name: Russell Fox WTP Operator Title/Position: Accompanied By? No Telephonic Contact? No | Name: Pierre Costello ANTHC TUS Manager Title/Position: Accompanied By? No Telephonic Contact? No | [7 empty] | The trip was scheduled for Water Plant inspection and to locate leaks in the distribution system for water loss estimate. Attend council meeting to discuss resolutions. | Arrived in Old Harbor with Pierre Costello, ANTHC, TUS manager and met with Russell at the water plant. Russell had been having problems with the Streaming Current Detector and flow meters. If the flow meter detects a flow less than the minimum required, it shuts down the SCD and the VFD for the polymer pump. Russell had been running the plant on manual. With good raw water, 0.05-0.07ntu’s to start with, producing 0.03ntu treated wasn’t that hard to do. Pierre stated the flow meters “wander” after a while and need to be reset. He showed us the procedure for adjusting. When done, automatic functions for the plant returned. I removed the cover for the probe assembly on the SCD. The clevis pin was wearing and the metallic dust was covering the probe housing. The dust can work its way down onto the probe causing erratic function; I replaced the clevis pin and left a spare on top of the SCD. The SCD probe and housing need cleaning on a regular basis and hadn’t been done. I showed Russell the procedure, adjusted flows, and turned the unit back on. ANTHC, had completed the energy audit recommendations, Pierre inspected those upgrades. Russell said he knew of 3 on-going leaks at service connections. I asked him to show us those locations and take us through the distribution system. I brought the RMW correlator for leak detection along and planned to document the results for the three sections of the community; old town, mid-town, and the newer HUD development. A leak detect effort was completed 5 years earlier. That study documented possible leakage still in effect. Initial run through showed us 2 “surfacing” leaks in the HUD area, and 1 in mid-town. Pierre and I started up in the HUD area of town; also known as “Up Town”, or “Hollywood”. There are two hydrants on the street about 420’ from each other. The already surfacing leaks showed up as “peaks” on the correlator measured via measuring wheel at 150’ and 280’. One outstation “Blue”, had to be attached to the hydrant stem inside the barrel, as the valve box couldn’t be opened. The valve box for the other hydrant was accessible and the sensor for outstation “Red” was attached by magnet to the valve’s operating nut as prescribed by the manual. No other indication of additional leaks were seen via correlator, or heard with the “Subsurface LD-12” listening device. We drove around downtown to decide on a starting point for correlation. As on the previous leak study, there are very few “Hard” contacts for the magnets to attach to. Plans show the water mains on the east (mountain), and on the west (ocean), of the downtown district. There are 4 “lateral mains” that connect the east and west mains located under streets named Matthew, Mark, Luke, and John. The eastside main when originally installed, had isolation valves at the tees for the four streets. Those valves have long since been buried. Pierre and I made significant effort to locate the valve boxes, but only found the valves on the southwest corner of the distribution system. They are below the corner of a shed by the “Church house”. The correlator located a leak at a hydrant on the southeast corner of downtown. There had been noise documented there previously, the correlator confirmed it. Pierre, using the LD-12, where I couldn’t use the TriCorr Pro, heard obvious water type noise at a service connection on Luke Street; that may be an abandoned dwelling. This is the 1st service west of the only hydrant servicing the middle of downtown. The mayor, Rick Berns, had requested that Pierre and I attend a council meeting at 6pm. Pierre discussed ANTHC and TUS involvement, contacts for the new PM, and fielded a couple questions regarding grants and funding. The city needs a pumper truck and upgrades in the distribution system. Electrolysis on the services is breaking the connections throughout the system. I relayed my findings so far; the need for fixing leaks, lack of hydrants in the downtown area (for flushing, leak detection purposes, and fire protection). We discussed the annual cost of the leaks, and the need for accessible isolation valves. The current process for fixing leaks is to shut the whole system down for repairs. The council is discussing the need for shutting off delinquent water/sewer bills. In the morning we went to the water plant. I wanted to check the numbers and operational status of the plant. Everything was still running on automatic, no issues were noticed. I calibrated the turbidimeters with Russell; when done the effluent turbidity settled down to 0.03ntu’s for treated water. The plant was producing 60gpm. The midtown section of Old Harbor consists of Birch St. (from the plant and storage tank), a loop and a side street (Second St.), that tees off the main to Hill St. with dead ends. This section is closest to the water tank and plant. Russell had shown us a significant surfacing leak at a service connection on Simmons St. when we arrived. I correlated Hill Street, hydrant to hydrant. With Second St. teeing off in the middle, the correlator kept reading “Out of Bracket” but indicated a nearby leak. Pierre with the LD-12 confirmed a service connection on the 3rd house south of the Second Street intersection. The contour of the property may be directing that leakage down onto Birch located below; where the road bed is wet and glaciates in the winter months. Further study will be needed for that determination. We ended the study with six leaks documented, three surfacing. Another 2-3 locations with indication of leakage are marked for future observation. | 5 | The numerous leaks could total 30,000-40,000 gallons per day. The savings potential here is considerable. Historically when a leak is fixed in this distribution system, water pressure increases and creates another leak elsewhere. The city has been proactive in replacing service lines with plastic. |  |  |  |  | Electrolysis is rampant in this aging system. Service connections and corporation stops need replacing. | Yes | The flow meters installed in the water plant on construction are no longer being implemented elsewhere, and should be replaced. | Yes |  | No |  | No |  | No | Nothing noted at this time. | Other | [9 empty] | Attachments | Other Documents | 2016-10-07 14:49
RMWTR-1454 | DEC | Kake | Floyd Murphy | 2016-09-12 | 2016-09-13 | Routine |  |  |  |  | Airplane | No |  | Name: Clifton "Kip" Howard Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Christine Bitterman Title/Position: Mayor Accompanied By? No Telephonic Contact? No | Name: Rudy Bean Title/Position: City Manager Accompanied By? No Telephonic Contact? No | Name: Timothy Eby Title/Position: ANTHC Engineer Accompanied By? No Telephonic Contact? No | Name: Jim Norris Title/Position: Project Superintendant Accompanied By? No Telephonic Contact? No | Name: Brian Menghini Title/Position: ANTHC Engineer Accompanied By? No Telephonic Contact? No |  |  |  |  | Work with operator on water distribution leak detection and Boiler Operation and Maintenance. Familarize self to the community water and wastewater systems. Go over SNC issues with the operator and Water monotoring to get systm back into compliance. | Kake Trip Report 9/15/16 I departed Anchorage for Juneau around 11:30 am to continue on to Kake, arriving around 5:30 pm in Kake. I spent the night at the Keex Waan Lodge. 9/16/16 I met up with Timothy Eby ANTHC Engineer and Brian Menghini, ANTHC Utility Support Associate Engineer who also stayed at the lodge. Clifton “Kip” Howard, Kake Water Plant Operator arrived around 7:00 am at the lodge to assist with and receive training on water leak detection. We met briefly with Jim Norris, ANTHC Project Superintendent, he informed us that the main road through the community would be closed for the day for the distribution pipe replacement instillation. Jim informed us that there was an alternate road about 10 miles long around the back side of the community and would be used during the day to access the other side of the community. We went to the Canadian Side Subdivision that was reportedly having leak problems in the distribution system. The first fire hydrant we stopped at a Mueller 5 1/4 inch, we could here water leaking. I provided training on the leak Detection 12 usage for leak detection. Using sound or the meter and material from the manufacturer on subsurface leak detection was used. Using 3 leak detection devices and the knowledge of the operator and maps provided by ANTHC we started our leak detection. The community owns a LD 12.This area was suspected to have water leaks. The pipe used for this subdivision is a mixture of pipe that was available for the installers, according to the operator. We located several water leaks and Mr. Eby documented the locations. In three places the pipe day lighted, the first one we found was in a culvert that housed connections for the distribution. This leak should have the king nipples, unions and nipples replaced. The second leak on the surfacing pipe was a pinhole leak on a nipple after a valve, the valve was shut off completely and stopped the leak. The nipple should be replaced. The third surfacing piping should also be rebuilt with new parts. This was located in a grassy area and was a major leak. It is hoped that funding can be obtained to replace the piping in this area of the community. We had a meeting with the Mayor, Ms. Christine Bitterman and City Manager Rudy Bean, Kip Howard to keep them informed of the water leak findings that were located. We went back to leak detection of the water distribution system. After lunch, I spent about 4 hours with Kip at the water plant going over the furnace and Operations and Maintenance. We also went over the Water Monitoring Summary and the Significant Non Compliance (SNC), DEC, Enforcement Targeting Tool, (ETT) reports for the system. Kip has been sending samples to the laboratory to get back into compliance with the SNC, ADEC, ETT, testing requirements. Kip also requested the telephone number for AMLJIA for the monthly Safety Teleconference. The number is # 855-257-8693 code 3008003 and requested to put the telephone on mute by hitting *6, *6 can be unmuted to ask questions. The AMLJIA information can also be found on the web by entering AMLJIA and following the provided information. I departed Kake for Juneau to spend the night around 5:45 pm, arriving around 6:30 pm to travel TO Angoon on an 8:00 am flight. I spent the night at the Driftwood Hotel. | 6 | None at this time |  |  |  |  | Water leaks in the north Tribal Court Subdivision. 1 Major leak, needs new parts | No |  | No |  | No |  | No |  | No | Community should order parts to replace the leaking fittings in the North Tribal Trailor Court, Operator can call me for assistance as needed. | Community | [9 empty] | Attachments | Other Documents | 2016-10-05 11:44
RMWTR-1455 | NSHC | Golovin | Bryant Koonooka | 2016-10-04 | 2016-10-04 | Other |  | $87 |  |  | Bering Air/Ravn Air | No |  | Name: Mike MarcAurle Title/Position: ANTHC Engineer Accompanied By? Yes Telephonic Contact? No | Name: Mike Soltis Title/Position: ANTHC Engineer Accompanied By? Yes Telephonic Contact? No | Name: Vern Hyde Title/Position: Other Accompanied By? Yes Telephonic Contact? No | Name: Pat Easter Title/Position: Other Accompanied By? Yes Telephonic Contact? No | Name: Krista Pihlaja Title/Position: ANTHC Engineer Accompanied By? Yes Telephonic Contact? No | Name: Ron Yeager Title/Position: ANTHC Engineer Accompanied By? Yes Telephonic Contact? No | Name: David Reed Title/Position: ANTHC Engineer Accompanied By? Yes Telephonic Contact? No | Name: Kathy Punguk Title/Position: City Council Member Accompanied By? No Telephonic Contact? No | Name: Wayne Henry Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Robert Moses Jr Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Final inspection,Water treatment plant complete. | Water treatment plant: Mike MarcAurele went to the city and got the mayor Dora Davis and council member Kathy Punguk to go thru the punch list with them. Mike pointed out how the water plant works and what chemicals are used before filtration and after filtration. We Went out and looked at the backwash pond and the water storage tank, and the backup generator. Micheal Soltis showed us where chemicals were injected and where they were mixed in the system. Washeteria: Mike MarcAurele showed us what they all did in the washeteria how chlorine went into the water to be stored in the 1.2 million WST.The Wst tank is leaking in couple places and the base has moisture most of the way around it. After we came up from the washeteria Wayne Henry(WPO) and Robert Moses Jr.(alternate WPO) went to the well and start up the well house generator to start making water.Went and looked at the well ,The river looked clear and Wayne and Robert had started to send water to the WTP. Took about 35 minutes for the water to reach the WTP,but they had to wait till all the air was out of the transmission line to send it to the filters.And had to bleed out the air before the filters.And filter to waste till the turbidity to go down.Took awhile but they had started to fill the rest of the WST,which was half way full. | 6 | 1.2 million gallon tank was leaking from 2 different sides,Needs repair. |  |  |  |  | 1.2 million gallon tank was leaking from 2 different sides,Needs repair. | No |  | No |  | No |  | No |  | No | Fix the older WST by the waheteria. | Other | [9 empty] | Attachments | Other Documents | 2016-10-10 16:26
RMWTR-1456 | TCC | Ruby | Lee Meckel | 2016-09-20 | 2016-09-21 | Training/Meeting | [5 empty] | No |  | Name: Malcom Nickolai Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Cliford Cleaver Title/Position: Other Accompanied By? No Telephonic Contact? No | Name: Wesley Shales Title/Position: RMW Accompanied By? No Telephonic Contact? No | [7 empty] | Respond to Ruby/Operator need for site specific training on maintenance and operation of the water treatment systems at the Plant as well as other Washateria building systems, in addition to the community sewer system maintenance needs. | After arriving and meeting with Mr. Nickolai we took a walk through the plant to become better acquainted with the pant and its current condition/needs. After a brief tour of the water treatment plant/washateria we went over the system from the beginning of the process of producing safe, clean, astatically pleasing, potable water. We explained to Mr. Nickolai the complete step by step process and operation of his water filtration/treatment system and how optimize its routine functions. We extensively discussed the importance of potassium permanganate its functions and showed him how to properly mix/administer the potassium permanganate as well as the chlorine. We then observed Mr. Nickolai mix up a batch of permanganate. We discussed the greensand filters and the how they work and the importance of permanganate in the process. We went over the steps to take on verifying a proper dosage of the solution and how he should look for “Tea color or pink water” before filtration, but after filtration he should find none. Next, we performed a backwash on the system and detailed the importance to Mr. Nickolai on properly following all the steps involved as well as a time frame for performing the backwash based on various factors such as time between backwash’s, differential pressure gauge readings, iron/manganese levels in the filter effluent, etc. We moved on to detail the critical steps of following and verifying that the administration of a proper dosage of chlorine is detectable. We had Mr. Nickolai test a number of samples for chlorine content. We emphasized the need for a minimum .2 mg/l of residual chlorine entering his distribution system and how he should maintain a certain amount throughout his entire system. We explained to him about chlorine demand, combined chlorine and free chlorine, in addition to “contact time”, MCL, and chlorine residual. We highlighted the importance of his record keeping, more specifically his daily readings and the much useful maintenance/ trouble shooting information that can come as a reward from properly recorded info. We also talked about monthly reporting to DEC in addition to the various water sampling requirements. | 10 | We supplied Mr. Nickolai with the list of Primary Drinking Water Regulations, a flyer on Water testing and Interpreting your Results, and a student manual on Intro to Small Water Systems. He indicated he had some very limited training and we clued him in on studying the material and preparing for an upcoming training and testing course he could take this Fall. T.C.C. will be hosting one in November. At the end of our time in Ruby his Pocket Colorimeter for testing chlorine concentration quit working properly and we promised to follow up on that problem a.s.a.p. We indicated that possibly the ANTHC supply shop could help him to order a replacement. We told him how they were an extremely good source for obtaining supplies and materials for the Plant. He did already have sufficient quantities of chlorine and permanganate ordered through them by Mr. Cleaver. |  |  |  |  | We pointed out areas that could be improved upon as well as maintenance that could decrease potential health related risks such as the watering point hose being too long to the point it can touch the ground at the washateria. There were also several auto pressure relief valves that needed to be replaced. The un-coverable abandoned well is a potential water source contamination hazard and was discussed with Mr. Cleaver and Mr. Nickolai. Mr. Cleaver and I agree it would not be too difficult to cut down the raised casing and recap it with an existing sanitary seal, by doing this you would be able to replace the fabricated well box cap sitting next to it. There is also a ¾” to 1” plug missing on the discharge line that could be a contamination entry point to the water plant that should be addressed. There is also an automated glycol make up tank that is in the boiler room but does not work. Mr. Cleaver had let me know that in the past the system was 55 gallons low. I would recommend looking in to this a little more. We were able to deduce that power is getting to the pressure switch on the make glycol up tank but not beyond when there is a demand. We were able to manually make the contactor on the pressure switch close and the pump fired up so it works it just needs to be dialed in. I am available to help if necessary. The bathrooms are already being taken care of based of the information I received from Mr. Nickolai.(there is a few plumbing leaks that have damaged the insulation and wood both underneath the building as well as the interior) and We happened to notice heat trace control box had been damaged and there are some exposed wires that could be an issue. Mr. Shales is a licensed election and said that there are repair plates that can cover the hole in the bottom of the control box so that more liquid tight could be coupled to the where it’s now too short to reach the bottom of the box, this way your power supply won’t be exposed to the elements or any local wild life/ kids. We discussed many ways to resolve these issues with Mr. Nickolai who seemed excited to improve his plant. | No |  | No |  | No |  | No |  | No | Towards the very end of our time in Ruby we were told about an operational problem with one of the sewer lift station pumps so we spent some quick time troubleshooting the situation. The VFD controlling the pump didn’t indicate any faults. The control panel didn’t indicate any obvious conditions. The pump did operate in hand mode so it was theorized that a possible relay problem existed. Two such targets were the alternating relay and/or an “intrinsic relay” needing replacement. Replacement part numbers were obtained and given to both Mr. Nickolai and Mr. Cleaver. Mr. Cleaver had been the one to alert us to the symptoms of the v.f.d. earlier that day at the water plant. We went to the lift station to look at the manual for the v.f.d. Mr. Cleaver met us there and was apparently alerted to our presence after we triggered the high level alarm in the lift with a willow while attempting to simulate a demand for the pump we were trouble shooting. As for the sewer lagoon we spoke with Mr. Nickolai about future maintenance needs and how they would play out with respect to effluent and sludge handling when servicing the cells in the lagoon. | Operator | [9 empty] | N/A | Other Documents | 2016-10-17 08:25
RMWTR-1459 | TCC | Nulato | Wes Shales | 2016-08-25 | 2016-08-26 | Routine | [5 empty] | No |  | Name: Lee Meckel Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Greg Patsy Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [8 empty] | Troubleshoot reoccurring electrical problems at the old town/uptown water plants. | A component within a control panel was needing replacement of a resistor after failing during certain conditions. This liquid level control component converts line voltage to a low voltage sensing circuit and uses a relay to direct operation of a pump. It was found that the voltage was slightly higher on the low voltage sensing circuit at the component. Other components of the same nature all had a slightly lower sensing circuit voltage closer to the manufacturer recommendation. Also, they had a higher rated resistor. The value of the sensing circuit resistor is extremely important to correct operation of the component. In addition, other conditions that the manufacturer cautions about include possible faulty operation when running sensing circuit lead wires with other circuits, grounding issues, and degraded insulation on wires, and broke or loose wires and also including failure of internal parts of the component itself were considered. Another problem Greg wanted looked at is he was told by an electrician from a private contractor something to the extent that something “was backfeeding the neutral” at an electrical sub panel. Upon investigating the situation I determined the three phase panel did not have anything wrong with it. It was receiving power from a 120/240 volt 3phase-4W Delta main panel. I explained that with this unique voltage set up a wild leg (one of the three phases) is not intended to be used for anything but three phase rated motors or devices. `120V or 120/240V single pole/double pole breakers are not to use that position in the panel. The wild leg voltage to neutral is 208 volts. Also, we looked at an area of the uptown plant that contained piping, electrical conduit/circuits and motors that were no longer needed and Greg wanted removed not just because they were mothballed but because it would allow better access/maintenance of other areas/equipment that were still operational. We made tentative plans to return and demo all the electrical/plumbing at a later date. | 1 | None |  |  |  |  | None | No |  | No |  | No |  | No |  | No | We are sending Greg a service manual for the liquid level control component and assisting him with finding replacement parts which are available from local suppliers or the manufacturer. I also told Greg that it is common practice under some conditions to install a UPS/surge protection for control circuits or electronics that experience possible power fluctuations or (power) failure. As for the sub panel issue goes I recommend to Greg to label the outside of all the electrical panels with their voltage and to not let others utilize incorrectly the wild leg phase of that particular electrical panel. Nulato is Lee Meckel's RMW assignment and he is to have followed up on the communities needs. | RMW | [9 empty] | N/A | Other Documents | 2016-10-10 14:42
RMWTR-1460 | TCC | Beaver | Wes Shales | 2016-09-06 | 2016-09-07 | Routine | [5 empty] | No |  | Name: Paul Petruska Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Aaron Petruska Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: Wanda Pitka Title/Position: Tribal President Accompanied By? No Telephonic Contact? No | Name: Wilma Pitka Title/Position: Tribal Administrator Accompanied By? No Telephonic Contact? No | [6 empty] | Respond to the Operator concerns of a possible need to replace the media inside the filters at the Water Treatment Plant. | After a thorough onsite observation, performance check and evaluation, troubleshooting and speaking with Paul we agreed to not replace the filter media but to instead verify proper injection of potassium permanganate as well as increase the dosage, pre and post backwash of the filters after this beginning attempt, testing and continued use of the automatic operation of the water treatment plant with respect to water production, and increased attention to seasonal/environmental/ “idle time” factors that would require more proper backwashing procedures, etc. In addition, Paul agreed to an even more proactive approach to flushing the floc tank and grit separator and to consider reintroduction of the use of a polymer for an even more enhanced filtration process. Our initial efforts were found to be extremely successful with respect to turbidity as well as iron and manganese concentrations after filtration/treatment. For instance, during these initial efforts an after filtration level for Iron was .17mg/L | 6 | None |  |  |  |  | None | No |  | No |  | No |  | No |  | No | Paul will be keeping a close watch on the concentration needs of potassium permanganate as well as chlorine because of our recent adjustment etc. and correct them as necessary. In addition, Paul will closely watch the automatic mode characteristics of the water production after having kept it in manual mode most recently he wants to make sure he can consider it reliable as well as cost effective. Paul will keep me informed of any further concerns. All in all I found the Beaver Water Plant operations to be well provided for and maintained and the community of Beaver to be very welcoming. | Operator | [9 empty] | N/A | Other Documents | 2016-10-10 14:52
RMWTR-1461 | TCC | Tetlin | Wes Shales | 2016-09-14 | 2016-09-16 | Emergency | [5 empty] | No |  | Name: Lee Meckel Title/Position: RMW Accompanied By? No Telephonic Contact? No | Name: Michael Sam Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Ricky Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | [7 empty] | Assist with repair/improvements to Tetlin well pump casing, etc. | At Tetlin we dug down to the location of the old pitless adapter at the well casing and installed a pipe cap fitting that Lee had previously picked up in Tok. The old piping from the pitless adapter had previously become detached from the well casing and was abandoned and the new piping was routed out the sanitary seal. Wiring and heat trace to the well was cleaned up and a new sanitary seal was installed. The well casing and all of the distribution system was disinfected for a twelve hour period and flushed. Extensive follow up procedures/instructions were discussed with the Tetlin crew with respect to further testing as well as finish work around the well casing that needed to be completed. | 0 | None |  |  |  |  | None | No |  | No |  | No |  | No |  | No | Tetlin is one of Lee’s RMW communities and he has had extensive conversation/consultation with the Tetlin crew about the need to construct housing around the well head and supply piping/wiring. In addition he has communicated with them about the need to add grout/cement around the well casing and to build up the ground around it. The Tetlin crew was addressing those needs as of our departure. | Operator | [9 empty] | N/A | Other Documents | 2016-10-10 15:04
RMWTR-1462 | TCC | Tanacross | Wes Shales | 2016-09-16 | 2016-09-16 | Routine | [5 empty] | No |  | Name: Lee Meckel Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Wesley Hamilton Title/Position: Accompanied By? No Telephonic Contact? No | Name: Johnny Lillie Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [7 empty] | High Pressure pump test. | On our return drive back to Fairbanks we stopped in at Tanacross and reviewed the steps with Johnny for performing a high pressure pump test. We successfully completed the test. | 1 | None |  |  |  |  | None | No |  | No |  | No |  | No |  | No | Semi regular or scheduled pump tests. | Operator | [9 empty] | N/A | Other Documents | 2016-10-10 15:20
RMWTR-1463 | TCC | Dot Lake | Wes Shales | 2016-09-16 | 2016-09-16 | Routine | [5 empty] | No |  | Name: Lee Meckel Title/Position: RMW Accompanied By? No Telephonic Contact? No | Name: Dan Drake Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [8 empty] | Pass thru visit. | Dot Lake is only a few minutes off the highway and on our return trip from Tetlin we stopped by for a courtesy visit with the Operator. We reviewed recent work completed by myself and Dan on previous trips and spoke of the upcoming winter season and work he would perform on his systems. | 0 | None |  |  |  |  | None | No |  | No |  | No |  | No |  | No | I will continue to have regular contact with Dan. | RMW | [9 empty] | N/A | Other Documents | 2016-10-10 15:28
RMWTR-1465 | TCC | Circle | Fred Kameroff | 2016-10-03 | 2016-10-03 | Routine | [5 empty] | No |  | Name: Lawrence crow Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: dennis carroll Title/Position: Other Accompanied By? No Telephonic Contact? No | Name: Jessica feilds Title/Position: Tribal President Accompanied By? No Telephonic Contact? No | Name: brian bearden Title/Position: Environmental Health Officer Accompanied By? Yes Telephonic Contact? No | [6 empty] | Blow out air vent for well vault Repair leak on boiler Air release | The air vent was not working on the well vault, Mr. Brian Bearden and I brought our TCC/ RMW air compressor and hooked it up to a vent inside the water plant and to blow out whatever was clogging it up. Mr. Bearden observed and said that water had been plugging the vent line. After blowing out the water in the air vent we placed it back to service. Mr. Lawrence Crow Jr let me know that one of the boiler safety relief valves had a leak. I then removed the safety relief valve and pulled out the ¾ inches threaded nipple and replaced it with a new one and then reinstalled everything. I then added pressure to the boilers and tested the boiler and placed it back on standby. Mr. Crow also stated one of the washers was making noise when someone is doing a load of laundry, a circle resident came and did a load on the washer that Mr. Crow said was making noise, but after the clothes were done the washer operated normally. RECOMMENDATIONS/CONCLUSION We determined that the well vent had been plugged with water, and that it will occasionally need to be checked and cleared by blowing air through it again. Otherwise, if not cleared, the well draw a vacuum at the well head as we observed, which could suck in contamination | 4 | none |  |  |  |  | none | No |  | No |  | No |  | No |  | No | operator | Operator | [9 empty] | N/A | Other Documents | 2016-10-10 15:40
RMWTR-1466 | TCC | Ruby | Wes Shales | 2016-09-20 | 2016-10-21 | Routine | [5 empty] | No |  | Name: Lee Meckel Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Malcomb Nickolai Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Clifford Cleaver Title/Position: Other Accompanied By? No Telephonic Contact? No | [7 empty] | Respond to Ruby/Operator need for site specific training on maintenance and operation of the water treatment systems at the Plant as well as other Washeteria building systems, in addition to the community sewer system maintenance needs. | During our initial walkdown and touring of the water treatment plant/washeteria we described to Malcom the complete process and operation of his water filtration/treatment system and how it best operates. During the walkdown and throughout the training we pointed out a few areas in need of improvement or maintenance such as the watering point at the washeteria. We went over extensively the need to properly mix/administer the potassium permanganate as well as the chlorine. We observed him mix up a batch of permanganate. We discussed the greensand filters and the how they work and the importance of permanganate in the process. We went over the steps to take on verifying a proper dosage of the solution and how he should look for “pink water” before filtration, but after filtration he should find none. Next, we performed a backwash on the system and detailed the importance to him on properly following all the steps involved as well as a time frame for performing the backwash based on various factors such as time between backwash’s, differential pressure gauge readings, iron/manganese levels in the filter effluent, etc. Next, we detailed the critical steps to follow verifying the administration of a proper dosage of chlorine. We had Malcomb test a number of samples for chlorine content. We emphasized the need for a minimum .2 mg/l of residual chlorine entering his distribution system and how he should maintain a certain amount throughout his entire system. We explained to him about chlorine demand, combined chlorine and free chlorine, in addition to “contact time” and chlorine residual. We highlighted the importance of monthly reporting to DEC in addition to the various water sampling requirements. Towards the very end of our time in Ruby we were told about an operational problem with one of the sewer lift station pumps so we spent some quick time troubleshooting the situation. The VFD controlling the pump didn’t indicate any faults. The control panel didn’t indicate any obvious conditions. The pump did operate in hand mode so it was theorized that a possible relay problem existed. Two such targets were the alternating relay and/or an “intrinsic relay” needing replacement. Replacement part numbers were obtained and given to both Malcomb and Clifford. As for the sewer lagoon we spoke with Malcomb about future maintenance needs and how they would play out with respect to effluent and sludge handling when servicing the cells in the lagoon. | 8 | None |  |  |  |  | None | No |  | No |  | No |  | No |  | No | We supplied Malcomb with the list of Primary Drinking Water Regulations, a flyer on Water testing and Interpreting your Results, and a student manual on Intro to Small Water Systems. He indicated he had some very limited training and we clued him in on studying the material and preparing for an upcoming training and testing course he could take this Fall. At the end of our time in Ruby his Pocket Colorimeter for testing chlorine concentration quit working properly and we promised to follow up on that problem asap. We indicated that possibly the ANTHC supply shop could help him to order a replacement. We told him how they were an extremely good source for obtaining supplies and materials for the Plant. He did already have sufficient quantities of chlorine and permanganate ordered thru them by Clifford. All in all we found the Ruby Washeteria and Water treatment building to be well maintained and provided for. Residents of the Community were very friendly and quick for some good conversation or a hello. Clifford the Power Plant Operator proved to be a very busy individual but provides help and some training to Malcomb when possible. Malcomb looks forward to taking on other responsibilities soon such as water and sewer delivery/pickup, etc. | RMW | [9 empty] | N/A | Other Documents | 2016-10-10 15:48
RMWTR-1467 | TCC | Kaltag | Wes Shales | 2016-09-27 | 2016-09-29 | Routine | [5 empty] | No |  | Name: Jeremy Semeken Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Jackie Nicholas Title/Position: City Clerk Accompanied By? No Telephonic Contact? No | [8 empty] | Initial request was received to help out with sewer and water main line(s) flush and to assist with maintenance needs at the water treatment building, in addition to assisting with taking lead and copper samples. | Just before I arrived some available help from around the community assisted Jeremy with flushing the water and sewer mains. The lead and copper sampling was delayed. Jeremy thought a box from the testing lab contained the lead and copper sampling kit but actually upon opening it we found monthly coliform sampling bottles. A quick call to the testing lab confirmed they were behind schedule in sending it out and that it was sent out today as of the writing of this report. I supplied Jeremy with a collection of flyers and other info on water testing and drinking water regulations and then we went over subject matter with the Intro to Drinking Water Systems student manual. I emphasized the need to Jeremy that studying the book and a math formulas cut sheet would significantly improve his ability to be one step ahead of the crowd as well as successfully passing the exam for a upcoming level one training/exam in Fairbanks. Next, we focused our attention on some needed preventative maintenance. We prepped a number of pipe flange connections near pumps, including threading on the pipe or bolt fastening them. A lot of rust and corrosion had occurred and would complicate upcoming work scheduled. Pump parts on order would swap out a lot easier with clean connections to deal with. Plus, it looks better not to see such rust occurring within the water treatment facility. A leaking chemical injection (check) valve was replaced and I showed Jeremy how to find a replacement part number from a parts manual and then how he could easily call the ANTHC utility support supply warehouse in Anchorage and order the needed material(s). We did just that and they gladly assisted us with our request. In addition to being a resource for treatment chemicals they are able to assist with ordering many other parts and supplies/materials associated with water and sewer utility applications I told him. We spent some time checking the boilers and I showed Jeremy how using a boiler analyzer could assist in tuning up the boilers. I suggested a few different vendors from who Jeremy could order replacement nozzles from in Fairbanks. Last of all, Jeremy mentioned about a leaking water service valve at a long time vacant house. We went to the location and he spoke of how he had previously tightened the clamp portion of the valve and it didn’t leak so bad. He again attempted to fully correct the situation but it didn’t help. I told him the best and remaining solution would be to access the corp valve and totally shut off the service line. It was unlikely that the residence would be used again soon, if ever, he said and we both agreed at that point on the permanent solution. My plane was soon to arrive in Kaltag so I didn’t have time to assist him with that. | 6 | None |  |  |  |  | None | No |  | No |  | No |  | No |  | No | I will continue to follow up with Jeremy on his water sampling needs as well as his materials orders he is expecting to arrive soon. In addition I will continue to emphasize his need to prepare himself for the upcoming training and certification he will attend and to just keep in contact with him on a regular basis. | RMW | [9 empty] | N/A | Other Documents | 2016-10-10 15:57
RMWTR-1468 | TCC | Circle | Fred Kameroff | 2016-10-04 | 2016-10-05 | Emergency | [5 empty] | No |  | Name: lawrence crow Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: dennis carroll Title/Position: Other Accompanied By? No Telephonic Contact? No | Name: jessica fields Title/Position: Tribal President Accompanied By? No Telephonic Contact? No | Name: brian bearden Title/Position: Environmental Health Officer Accompanied By? Yes Telephonic Contact? No | Name: wes shales Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: dave masephol Title/Position: Other Accompanied By? No Telephonic Contact? No |  |  |  |  | Diagnose well pump problem | Mr. Lawrence Crow Jr contacted me on 10/04/16 stating that the well pump is not pumping water to the water storage tank. I asked if he checked on the main breaker and he stated that it was not tripped. I told Mr. Crow I and Mr. Wes Shales will be heading up the same day. Mr. Brian Bearden also agreed to come along. Prior to our departures we picked up a well pump from our supply. We arrived at Circle and met with Mr. Crow at the water plant. We then started to look at the well control panel and did a few tests but did not find anything wrong inside. By next day we looked inside the well vault and Mr. Wes Shales started to rewire all the hot leads for the motor but once he was done we energized the motor and it would still not run, so the main problem was the motor being burned out. Mr. Crow contacted Mr. Dave Masephol the power plant operator to hire him with his backhoe to pull out the drop pipe and the pump. Once we pulled out the pipe and the pump Mr. Shales made the splices on the 3 leads and one short section of the drop pipe had to be rethreaded and replaced, after all the necessary corrections were made we lowered the pump and drop pipe back down the well casing and closed up the well vault. We tested the pump by turning on the well control and to our finding water started pumping out to waste. We pumped out to waste for about an hour and a half before transferring fresh water into to holding tank. Then we pumped into the storage tank for about an hour, and we turned on the pressure pumps and they reached the set pressure and shut down. RECOMMENDATIONS/CONCLUSION The drop pipe needs to be replaced by the next year, preferably with HDPE pipe. Circle’s water system is over 20 years old and is in need to have an upgrade done. Most everything is old and we are now having to repeatedly go back to replace anything that goes down. | 8 | water system is in need of upgrades |  |  |  |  | having to repeatedly head back to circle for any kind of repairs. | No |  | No |  | No |  | No |  | No | water system needs a upgrade | Engineer | [9 empty] | N/A | Other Documents | 2016-10-11 08:38
RMWTR-1469 | YKHC | Kasigluk | Bob White | 2016-10-10 | 2016-10-10 | Routine |  |  |  |  | YKHC Boat | No |  | Name: David Brink Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Nickfer Nicholas Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [8 empty] | To cut well casing and address settling issues. | I arrived by boat in Old Kasigluk and went to the Washeteria. After looking over the plant inside I walked the around the exterior and could see visible settling around the old washeteria site as well as the whole perimeter of the Lift Station deck. We then removed the cover from the well box and I saw were they had to cut the insulation to close the lid. They did a great job re-leveling the well box adding gravel on the side that settled. We then decided to cut the casing down 2 " below the rim of the well box. We used the grinder to remove 10" from the top of the well casing. With the well cut down we reattached the sanitary seal and were able to put the lid back on the box. I instructed David to monitor the box for further movement. We then gathered information for parts needed to do a boiler cleaning at a future date. I then departed to New Kasigluk. In new Kasigluk I met with Nickfer Nicholas and we gathered information for a boiler cleaning as well. I then looked at the waste heat which is still not working since January of 2016 when it broke at the AVEC power plant. I discussed the setting issues they have had with the low pressure sewer lift stations. Currently they have 3 that need to be re-leveled as the helical anchors are jacking. | 6 | AVEC Waste heat exchanger is still leaking. | The ground is sinking around the old Washeteria sight causing ramp and deck supports to hang in the air. | There is signs of shifting in the Lift station and all edges of the surrounding deck have settled significantly. |  |  | AVEC waste heat | Yes |  | No |  | No |  | No |  | No | Repair or replace AVEC heat exchanger. | Other | Monitor the well box for further settlement. | Community | Order boiler nozzles and brushes for cleaning and tuning. | Community | Purchase lumber to re build post and pads on decks and ramps. | Community | Replace broken siding on the exterior of the water plant. | Operator |  | Attachments | Other Documents | 2016-10-11 16:10
RMWTR-1473 | MHC | Kiana | Jeff Luther | 2016-10-04 | 2016-10-06 | Training/Meeting | [5 empty] | No |  | Name: Richard Teel Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [9 empty] | Change Light fixtures in water plant | As I got there, a bunch of ballasts were out which lead the plant to have really poor lighting, the operator had a lot of new bulbs that required some adjustments with taking the ballasts out & rewiring the fixtures, I started in the office, wired the light like how the diagram showed, light's didn't turn on, studied the wiring diagram & saw that we have different fixtures hanging than what is on the paper, draw up a new diagram & added couple wires to make the new bulbs work, add 2-4 wires to every light fixture in the building. Showed & trained the operator how to properly wire the fixtures because there were 3 left to change by the time I left. | 25 | none |  |  |  |  | none | No |  | No |  | No |  | No |  | No | none | Other | [9 empty] | N/A | Other Documents | 2016-10-14 14:32
RMWTR-1477 | TCC | Allakaket | Lee Meckel | 2016-09-29 | 2016-09-30 | Routine | [5 empty] | No |  | Name: Elisa Bergman Title/Position: Tribal Administrator Accompanied By? No Telephonic Contact? No | Name: Delbert Bergman Title/Position: Local Laborer Accompanied By? No Telephonic Contact? No | Name: Floyed Saunders Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [7 empty] | Assist in prepping facilities for winter as requested by the water plant operator. | Mr. Saunders and I conducted an assessment of the water plant after my arrival. Mr. Saunders has had concerns regarding the settling of the WST and the additional stress that the ground has put on the water lines leaving the WST to the glycol waste heat exchanger loop used to regulate the temp of the WST. The water lines coming off the tank are flexible but have become stretched to the point that there are stress fractures in the water lines on the supply and return sides of the circulation system. The box that had been constructed to house the water lines at the base of the tank is also separating from the wall of the WST due to the stretching / settling of the ground. We started to deliver gravel to help build up the ground under the aluminum box that house the lines. I had to leave before we had completed the adjustments to the ground but will follow up the following week. | 8 | I had looked at the amount of broken down LMI chemical feed pumps around the facility and recommended trying the Stenner chemical pumps for future replacements. |  |  |  |  | We also noted that the water tank depth sensor is not programed properly. We will find the manual and investigate further as to the cause. I counted ten auto relief vents 3/4'” that look like they could be changed. There is also a toilet that has a broken water reservoir that needs to be replaced. We also noted that there were many leaks throughout the glycol waste heat system that need to be addressed. I have begun getting quotes on the materials needed to fix these issues and will forward them to Mrs. Bergman once they are ready to be picked up. Mrs. Bergman and I spoke about the purchasing of parts to maintain the plant and she’s fully on board to address the issues ASAP. | No |  | No |  | No |  | No |  | No | I would like to travel back and address the glycol leaks as they have been an issue for a while. I have begun on acquiring quotes and locating parts for the repairs necessary. The water hoses for the WST are already being built and should be ready for pick up. | RMW | [9 empty] | N/A | Other Documents | 2016-10-17 13:37
RMWTR-1479 | TCC | Allakaket | Lee Meckel | 2016-10-05 | 2016-10-07 | Routine | [5 empty] | No |  | Name: Elisa Bergman Title/Position: Tribal Administrator Accompanied By? No Telephonic Contact? No | Name: Delbert Bergman Title/Position: Local Laborer Accompanied By? No Telephonic Contact? No | Name: Floyed Saurnders Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [7 empty] | Assist in correcting facility waste heat leaks. Repair failing water lines that connect to the water storage tank (WST) and add missing valve to WST. | Mr. Saunders and I had conducted an assessment of the water plant during my previous visit. We were able to determine that there were multiple glycol leaks in the copper pipes due too poor soldering. I made a parts list and got quotes then forwarded the quotes on to Mrs. Bergman who authorized the payment I then picked up the form check here in Fairbanks at their bank of choice. I picked up the parts that were on hand. I was told that the rest would be in Fairbanks from Anchorage the day after, and they would be shipped to me in Allakaket. I flew to Allakaket the following day and was greeted by Mr. Saunders. We checked the level in the water storage tank (WST) that Mr. Saunders had been letting drain via its own head pressure. We announced over the radio that the watering point and the washateria would be closed for up to a day or two and gave people time to get what they would need from the facilities until the repairs were completed. The tribe also was delivering water to the Elders with small tanks and a flatbed truck. While waiting for the tank to drain we got our materials together to drain the glycol loop. We isolated it from the rest of the glycol loops and ensured they would be unaffected by our repairs and still be able to heat the rest of the heating systems through the boilers. We then let it start cooling off. The following day, to help speed the draining process, we used the back wash pump due to the amount of water left in the WST. We then drained the waste heat line that leads to the power plant and back. The plane had come in and I didn’t get my parts so I called the airline that had been tasked with delivering them and they assured me they would be in on the afternoon flight. I asked that Mr. Bergman go ahead and remove the broken toilet form the wall now that the new one was on the way. Meanwhile Mr. Saunders and I walked down to the well head by the river and Mr. Saunders showed me a brass tee that had burst from freezing. We had a new one and I was able to fit in the well box and make the repairs. We finished up right as the plane was due to arrive so we borrowed the truck from the tribe and went to collect our parts. Immediately after picking up the toilet bowl box you could hear the broken porcelain. We brought it back to the tribe and had them call the airline and vendor. We were able to utilize the rest of the parts, though not every fitting arrived so we were able to mix the Nibco press fittings with some soldering to complete the repairs to the leaking waste heat system. The following day we manually added the glycol back to the system. We had an airlock in the waste heat line that wouldn’t allow circulation so we had to go and change the auto vents that had failed; we used 7 of the 10 I had ordered. Once they were changed we were able to get the system charged although the boiler glycol low level alarm had tripped. We were able to manually pump the over flow glycol from the boiler glycol recharge vat to the system to shut off the alarm. The glycol recharge system is designed to catch the overflow when the pressure in the system is too great and to automatically recharge when it’s low from the same reservoir that catches the overflow. Mr. Saunders let me know that the glycol recharge station hadn’t worked unless he tapped it with a hammer and that it wouldn’t work at all anymore. We moved on to the WST hoses and removed the old ones and added the valve and new waterlines that had been fabricated. We were able to start making water. There was a group of plumbers that had been waiting to chlorinate the water lines to the new clinic being constructed and were relieved that the water was back on. | 16 | There are still several auto pressure relief vents that need to be replaced. The sewer Glycol loop was also under pressured and could be recharged from the glycol vat attached to it. |  |  |  |  | Mr. Saunders let me know that the glycol recharge station hadn’t worked unless he tapped it with a hammer and that it wouldn’t work at all anymore. | No |  | No |  | No |  | No |  | No | I would like to get the glycol vats /recharge stations back online. I would like to have the toilet installed if the vendors honor the shipping damages. Mr. Saunders still needs to spray foam the gap around the box to the water lines on the WST. There are still many auto vents that can be replaced inside the water treatment portion of the plant as well. It was a very productive visit and Mr. Saunders and Mr. Bergan were a pleasure to work with. I would also like to thank the Tribe for their hospitality | RMW | [9 empty] | N/A | Other Documents | 2016-10-17 13:54
RMWTR-1481 | MHC | Buckland | Jeff Luther | 2016-10-17 | 2016-10-18 | Routine | [5 empty] | No |  | Name: Erik Weber Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [9 empty] | Inspect WTP for errors from Contractor & discuss other issues | 1. KNMO4 -> Flow Switch They have the KNMO4 injection point installed right before a flow switch, causing the flow switch to gum up & fail every 4-5 days or so. Erik said that it started to happen after the 50 gallon contact tank that was sitting between the 2(injection point & flow switch) was taken out. He wants to move the flow switch BEFORE the injection point to hopefully keep the flow switch from plugging/corroding from the KNMO4. 2. Arctic Boxes He talked having trouble with arctic boxes in town where the sewer pipe was disconnecting from the homes shifting with seasonal changes(permafrost melting & freezing back up), I advised that he get order some flex line along with insulation & arctic pipe tape to address those issues instead of digging up the pipe to line it back up with the home(s). 3. Low Water Temp alarm He complained about how the heat add was piped in, the water from the river is 32degrees winter time & turns on his low water temp alarm, he set the low temp alarm to 28 which is below freezing & we both are not ok with that setting, he asked for suggestions to change it in the system, he wants to redo the heat add to where he is taking water out of the Water Storage Tank & discharging it back into the tank through the filtered influent or through another pipe so long he isn't short circuiting. | 3 | none |  |  |  |  | none | No |  | No |  | No |  | No |  | No | none | Other | [9 empty] | N/A | Other Documents | 2016-10-18 15:41
RMWTR-1482 | YKHC | Napakiak | Bob White | 2016-10-17 | 2016-10-17 | Routine | $175 |  |  |  | Yute Air | No |  | Name: Greg Aluskuk Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Leo Kusayak Title/Position: City Administrator Accompanied By? No Telephonic Contact? No | Name: Herald Illmar Title/Position: Other Accompanied By? No Telephonic Contact? No | [7 empty] | Install coin meter on the watering point. | I arrived at 0930 hrs by plane and waited till the Washeteria opened at 1000 hrs. When Leo arrived I talked over some heating improvements that I believe would save them money. Giving Leo a list of parts to order. Leo then asked what should be done with the washers that were bought years ago that were the wrong kind, I suggested shipping them back to Automated laundry for sale as consignment. Greg and I headed to the watering point with the coin meter and tools needed for the installation. When we arrived the building was cold. Greg went to get fuel and I plugged in the Toyo stove. After Greg got back with the fuel we were still unable to get fuel at the Toyo. We headed back to the Washeteria to warm up and have lunch. After lunch Herald came to help me while Greg went back to working on the Toyo. We finished the wiring and mounting of the coin meter then Greg joined us as we adjusted setting to get the appropriate amount of water dispensed. With everything working and the staff on short hours at the city I headed back to Bethel at 1600 hrs. | 6 | The heat should have been turned on before the outside temperature dropped below freezing. | The plant is clean and well organized. |  |  |  | The washeteria has some heat zones that are running wild. | Yes |  | No |  | No |  | No |  | No | Order boiler controllers for auto boiler reset. | Community | [9 empty] | N/A | Other Documents | 2016-10-19 09:11
RMWTR-1483 | YKHC | Quinhagak | Bob White | 2016-10-18 | 2016-10-18 | Routine |  |  |  |  | Raven Air | No |  | Name: Frank Jones Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Norman Title/Position: Other Accompanied By? No Telephonic Contact? No | [8 empty] | Replace heat exchanger. Charge glycol force main with glycol. | When I arrived Frank had all the parts we needed at the water plant so we started right in on removing the old heat exhanger and replacing it with the new one. This was simple as the heat exchanger was a direct replacement so it only took soldering four joints and then bolting it into place. We then headed to the Utility building to add glycol to the force main. We started by draining down the pressure on the force main so we could add in glycol. We then pumped in 200 gallons of 100% glycol which after circulating brought our glycol strength in the line down to a -10F freeze point. While we were pumping in the glycol I took time to get antiquated with the Washeteria waste heat system. It was shut off so I turned it on and then went to check on the operation at the Washeteria once it was all operating I reset the boiler temperature to 160F so that the waste heat would be the main source of heat with the boiler being the back up. I then discussed the operation with Bill McDonald from CRW to make sure I was understanding it correctly and he asked me to test that the valves went to bypass on power failure. I then cut power to the valves and they both went to bypass. Norman then told me about a problem he was having with one of the two lift station pumps. When we opened the panel I found that pump #1 was tripped I reset it then it started to work and cycled fine with out tripping. We then pumped more glycol into the boiler system but ran out before we got the system all the way up to pressure. i instructed them to order more glycol and pump the system up to 20 PSI. I then went to look at the Lifewater units that are newly operational. They had very little sign of discharge showing that the water is being absorbed by the ground. | 8 | The Washeteria has several glycol leaks on the hot water heating system that should be fixed. | The waste heat is operating as designed. |  |  |  | Glycol leaks in the Washeteria. | Yes |  | No |  | No |  | No |  | No | Order Glycol for the Washeteria. | Community | [9 empty] | N/A | Other Documents | 2016-10-19 10:27
RMWTR-1484 | TCC | Nulato | Lee Meckel | 2016-10-24 | 2016-10-25 | Routine | [5 empty] | No | [11 empty] | To look into keeping heating system running. | Once I arrived, John Frank and I looked at the boiler and we were able to determine that boiler two had a leak in the black iron 1-1/4” pipe that comes out to the low water cut off from the boiler. We repaired the leaks then looked at the black iron nipples that were removed from the boiler before being changed and they were literally over half full of sludge. If this is an indicator of the conditions of the inside of the boiler and its plumbing then I would like to have the system flushed. Boiler two did have a good burner that would fire when there was a demand for heat. The treated water from the WST is designed to be pumped through a heat exchanger that is plumbed into the boiler. The boiler portion of the heat exchanger had failed and been abandoned. The treated water does still circulate to stop from freezing. It would be a very good idea to replace the heat exchanger. The waste heat from the power plant generator is also not operating. I was told that there are multiple leaks on the line but A.N.T.H.C. will address this issue. If the waste heat can be brought back online it would take a lot of the burden from the boilers that are in poor operating condition thus hopefully allowing them to last until a better project is activated. | 8 | Mr. Frank also expressed some concern regarding the buried transmission line form the well head to the valve box. It had given the water plant operator issues in the past with freezing up after making water. Mr. Frank believed that the heat trace may have gone bad. I did not have time to confirm this as I was leaving just mins after we started discussing it. Mr. Frank and I discussed adding a compressor to help blow out the transmission line when done making water if the heat trace truly is offline |  |  |  |  | With the current state of the heating system it would be wise to replace the deaerator as soon as possible before any more leaks occur. | No |  | No |  | No |  | No |  | No | we could try a chemical cleaning and treatment followed with flushing of the boiler until we can remove the sludge. I would recommend Fernox DS40. We could also replace some of the piping that is seized like the valve that is on the supply side of boiler 2 that is stuck shut. Mr. Frank let me know that even though the valve is in the closed position water still makes it by the valve. | RMW | [9 empty] | N/A | Other Documents | 2016-11-14 11:43
RMWTR-1485 | DEC | Adak | Kevin Schoneman | 2016-10-16 | 2016-10-20 | Training/Meeting | [5 empty] | No |  | Name: Lynn Marino Title/Position: VSW Engineer Accompanied By? Yes Telephonic Contact? No | Name: Kyle Petersen Title/Position: Design Engineer Accompanied By? Yes Telephonic Contact? No | Name: Roy Pace Title/Position: Consulting Engineer Accompanied By? Yes Telephonic Contact? No | Name: Layton Lockett Title/Position: City Manager Accompanied By? No Telephonic Contact? No | Name: Debra Sharrah Title/Position: City Clerk Accompanied By? No Telephonic Contact? No | Name: Mike Maloney Title/Position: Consulting Engineer Accompanied By? No Telephonic Contact? No | Name: Louis Rocheleau Title/Position: Project Superintendant Accompanied By? No Telephonic Contact? No | Name: Peter (PJ) Dushkin Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Garden Finau Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No |  | Construction Project Substantial Completion Meeting and Inspection. On Site new equipment demonstrations and training. | On Sunday October 16, 2016. I traveled to Adak with a group including Lynn Marino, VSW Engineer, Kyle Peterson, Bristol Engineering and Roy Pace EDC. Also traveling along with the group on the trip was Mike Maloney representing Soar Technologies. We departed Anchorage at 3:00 P.M. and arrived in Adak at approximately 5:45P.M. That evening we toured several of the project construction sites in the downsizing areas. The next day October 17, we all met at the city office. In attendance was our group, in addition to Louis Rocheleau, (Brechan Construction), Norm Hubbard (Brechan Construction) and Layton Lockett Adak City Manager. After a brief introduction we discussed, the items at both PRV 1 and PRV 2 that still needed to be completed. We also were undated on the status of the B tanks filling by Norm Hubbard, he stated that the tanks were finally beginning to fill. Louis Rocheleau gave us all an update as to the electrical work being done at PRV 2. We were joined by Adak water operator Peter Dushkin (PJ). PJ asked about the sampling point in PRV-2 he had noticed that the piping was different and wanted to make sure that he was getting his samples from the correct spot. We also talked about a couple of leaks at PRV 1 that still were in need of repairs. We all agreed the group would tour the sites together and meet up again at PRV 1. Most of the group went to PRV 1 to look at the work that was done at this site. Brechen demonstrated the operation of the new sediment screen. It was discussed in the meeting that morning that all three of the clay valves in PRV 1 had several issues. Mike and Frank with Bering industrial started to look into some of the problems. One of the things we noticed was that some of the flow readings seemed a bit off. We also looked at the leaks that were discussed in the meeting. We all continued over to PRV 2 and A tanks, to look at the remaining work to be completed there. The contracted electrician was still in the process of installing the hydro generator and lights as well as the heating units. After lunch I met back with Mike and Frank at PRV 1 to see if we could resolve some of the issues with the pressure reducing valves. We cleaned the wye strainer screens on all three of the pressure reducing valves. We noticed that the flow through the 4” line was about 440 gallon per minute, with the flow through the 8” line at 280 gallons per minute earlier in the day. We decide to take the 8” valve apart and see what was going on internally. When we removed the bonnet off the valve we noticed the regulator inside was full of small rocks and organic debris. We were able to remove most of the rocks from inside of the valve, there was an internal basket that we tried to remove but did not succeed. Before we put the valve back together we flushed the valve several times with water from the incoming main. We checked the flow rate after we returned the valve to service with a result of 660 gallons per minute. Tuesday morning Lynn and I met with Kyle, Roy and city manager Layton Lockett at the city office. We discussed some of the progress from the day before as well as items still left on the project punch list. We also discussed some of the possible locations of a new water treatment plant. We then decided to walk across the street to the Anne Stevens Elementary building as a possible site. There appeared to be many issues associated with trying to meet some of the current codes, along with renovation costs. We decided because the weather was decent that we would make the trip to the dam at Lake Bonnie Rose, making the trip was Lynn Marino, Roy Pace, Kyle Petersen and myself. Along the route to the reservoir Kyle pointed out several of the isolation valves along the way and the proper sequence of operation. After we arrived at the dam we looked at the new intake screen installed during the downsizing project and talked about the process of cleaning the intake screen. After much discussion it was agreed that the operators could possibly brush clean the screen once per year. We also noticed the grouting of the dam had not been done yet, Kyle made note of this. Lynn and I started back down to the truck and Kyle and Roy made a trip around a portion of the reservoir. We all met back at the truck and went back to PRV 2 to check on the progress with the electrical for the hydro - generator and heat. Lynn and Kyle and I checked on the meter vaults installations for the project. Later in the day Lynn and I inventoried the shipment of facets that were sent to the City in October. The next day I met with the operators at the city office, we left the office and started the daily rounds for water checks. We first went to PRV 2 to collect a samples for both chlorine and pH. We tested the Chlorine at the site, the residual seemed a bit lower than normal. PJ thought maybe the batteries were low so we headed back down to the city lab. At the lab PJ added new batteries and we checked the pH level. We then decided to go up to PRV 1 to check on the chlorine injection, the day before the operators had installed a new cylinder and wanted to check to make sure it was feeding properly. When we arrived at PRV 1 the operator noticed that the weight on the chlorine cylinder had not changed from the day before. We started checking on the feed tubing and chlorine injection lines. We received a call from Kyle Peterson requesting we all meet at PRV 2 for a demonstration of the new Hydro Generator, we all met at PRV 2 with Mike Maloney, Kyle, Lynn and Roy Pace. Mike gave us all a demonstration on the operation and maintenance, the equipment is very easy to operate and requires a minimal amount of routine maintenance. We mentioned to Mike we were having trouble with the chemical feed system at PRV 1 and he said they had to increase the pressure at PRV- 1 for the proper operation of the Hydro Generator we all agreed to meet back at PRV 1 after lunch. After lunch we met back at PRV 1 and started looking at the pressure readings on the injection line, we adjusted the pressure regulators on the injection line and the chlorine began to flow properly. We also repaired the union on the injection line. The next day I met with the operators PJ and Garden at the city shop/ water office. We discussed the process of getting Garden certified and taking the certification test, Garden and I spent time going over some of the reading material he had been looking at. We left the shop and went up to collect water samples and check the chemical injection system. We also toured the wastewater lift stations that were still operational. Later in the afternoon Lynn and I met back with Layton at the city office and discussed some of the requirements and issues that may be upcoming as to the New Water Treatment Plant. Lynn, Kyle, Roy, Mike and myself all left Adak on the evening flight back to Anchorage and arrived back in Anchorage at 10:00 pm. | 8 | Spare parts for the chlorine injection system such as the pressure regulator. Also including tubing and compression fitting. | Personal protection equipment such as goggles or face shield, rubber gloves and apron. | Exercise as many of the water distribution valves as possible when time allows during the year. | Heat in the building at PRV 1 and redo electrical such as lights and exhaust fans. |  | Heat and Electricity in PRV 1 | Yes | Spare Parts and safety equipment. | Yes |  | No |  | No |  | No | Make a spare parts list for the disinfection system at PRV 1 | RMW | Exercise the water distribution valves as often as possible. | Engineer | Electrical work in PRV 1 | Engineer |  |  |  |  | Lynn Marino was looking into the possibility of switching from chlorine gas to a powder or liquid form now that the system was being downsized. | Attachments | Other Documents | 2016-11-14 15:00
RMWTR-1486 | NSHC | Elim | Bryant Koonooka | 2016-10-26 | 2016-10-27 | Emergency | $623 | $150 |  |  | Bering Air | No |  | Name: Roy Daniels Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: David Nakarak Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: Chistine Amaktoolik Title/Position: City Administrator Accompanied By? No Telephonic Contact? No | Name: Frank Kavairlook Title/Position: Local Laborer Accompanied By? No Telephonic Contact? No | Name: Donny Aucon Title/Position: Local Laborer Accompanied By? No Telephonic Contact? No | [5 empty] | Emergency WST repair. | WST repair:10/26/16 Roy Daniels had set up a bypass hose to continue to provide water community.He changed two bag filters to get the water GPM to 40 GPM to keep up with the demand of the distribution.He announced on local CB that to inform the community that we were going to isolate the WST but still going to provide water.That the water is still being injected with chlorine but does not have enough contact time for them to boil the water first before drinking it. Then we isolated the WST to start draining and pumping water out with a 2" sump pump,little giant sump pump.Frank Kavairlook dug little drainage ditches so the standing water around the tank can dry out.Set up tools to start with the cleaning of the WST.In little over a month, the WST has a lot of rust in it already. Took a lunch break to allow the pumps to draw the water down. David Nakarak set up a 3" Engine driven trash pump to help drain WST faster.Roy set up a bucket of chlorine to disinfect or boots before we enter the WST.I set up the fast blast M20 jetter to help remove the rust and aid in the cleaning of WST. WE went in and started cleaning the rust out of the WST again.WST got rusty in just over a month.The deep worn/rusted out parts we did not have enough EP-200 to cover had rusted thru in little over a month.Used the jetter and some squeegees to get most of the rust out of the WST.When the sump pumps could not pump any more Donny finished the cleaning with a shop vac. I showed the crew how to prep the holes to be patched up.Estimated the amount EP-200 epoxy needed to patch up the hole.Spread the mixture to repair the hole.I watch them do a few repairs.We worked pretty late the first evening used about half the tubes.Gathered all the tools and told them we will continue the next morning. 10/27/16 Gathered our tools and back to patching up the WST.I heated and cleaned the holes that needed to be patched and Roy and David Nakarak filled them in with epoxy.We ran out of epoxy.There was still three holes to patch up.Frank was patching the ones he found using a heat gun and wire brush. Went in the WTP to look for something to cover the last remaining holes.The bypass suction hose we were using to bypass the WST keeps bursting.As it expands when the pressure would go up and contracts when the water is being used.When it expands some other part of the hose would burst. We decided to try flux and soldier to cover the last few holes,it took awhile but the soldier worked.We gathered up the tools and put them away.I Had Roy make a 1% solution to disinfect to WST.After disinfecting Donny and Frank started closing up the WST. | 23 | Rust in WST and going to continue to rust in the future.Need to change WST. | Pin holes in the copper piping in the water treatment plant.Need to change out WTP piping. |  |  |  | Rust in WST and is going to continue to rust in the future. | Yes | Pin holes in the copper piping in the water treatment plant.Need to change out WTP piping. | Yes |  | No |  | No |  | No | Clean and repair and Put a liner in WST. They need a new WST,the WST will continue to rust and eventually make new holes. | Other | The piping in the WTP has a lot of pin holes.Which needs to be replaced. | [8 empty] | Attachments | Other Documents | 2016-11-01 13:40
RMWTR-1487 | YKHC | Akiak | Bob White | 2016-10-21 | 2016-10-22 | Routine | $400 |  |  |  | God's Country Aviation | No |  | Name: Nelson Owen Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Calvin charles Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: Michael vicente Title/Position: Environmental Health Officer Accompanied By? Yes Telephonic Contact? No | [7 empty] | To flush sewer mains and water mains. To clean and inspect the Water storage tank. | We arrived at 1300 hrs and were picked up at the Airport by Nelson. We the procedeed to the water plant were we had 4' of water remaining in the tank. We loaded the supplies that they had staged at the water plant and issolated the water loops for directional flushing. We then started to flush the sewer main in front of the community building with water from loop #1. We continued to move through the community flushing the water lines to manholes to clean both the sewer lines and the water lines. With the level in the tank low enough to open the manway we opened the manway and started to do the finaal pump down with a sump pump while we ventalated the tank. Once we were able to enter the tank we started to clean side walls with brushes and Chlorine. We then brushed interior piping and floor finishing by using a Shop Vac to clean the floor completely. With all cleaning and inspection done we did a final disinfection and exsited the tank. We closed the tank and started the filter up by 2200 hrs. and everyone headed home for the night at 2230 hrs with the filter running making good water. 0730 hrs I checked on the plant and we had sufficent water to turn the pressure pumps back on. once primed and pressure built up in the tanks we opened one loop at a time. Once the loops were presurrized we started the circulation pumps. We then spent the rest of the time ddiscussing other operations in the plant. | 14 | The bolts holding the water storage tank ladder are showing corrosion on the inside of the tank. | Only 5 gallons of fuel is on site in the day tank. |  |  |  | non-drained hydrants. | Yes |  | No |  | No |  | No |  | No | Thaw and drain hydrants that were not drained this summer. | Community | Fill day tank completely so Emergancy fuel is ready if waste heat is lost. | Community | Next time tank is cleaned epoxy ladder bolt heads to protect them. | Community | [5 empty] | N/A | Other Documents | 2016-11-01 10:05
RMWTR-1489 | DEC | Fairbanks | John Johnson | 2016-11-01 | 2016-11-01 | Training/Meeting | $175 | $45 |  | NA | Alaska Airlines | No | [11 empty] | 2016 Annual TCC Coordination Meeting Nov. 1st Fairbanks ADEC building (610 University Ave), conference rooms B&C To coordinate effective and consistent communication between the agencies ands the communities. To get all agency representatives up to date on community issues and agency work with the communities. To coordinate our efforts in providing service to the communities. | Attended TCC Coordination Meeting | 0 | Issues with permitting for DW,WW & SW. |  |  |  |  | Many communities have projects that have not been properly permitted or not properly closed out. | No |  | No |  | No |  | No |  | No | Recommend TCC meeting again next November. I found the coordination meeting very productive and a wealth of information was shared between all agencies present. | Other | [9 empty] | N/A | Other Documents | 2016-11-02 11:34
RMWTR-1490 | NSHC | Wales | Bryant Koonooka | 2016-11-02 | 2016-11-03 | Emergency | $432 | $150 |  |  | Bering Air | No |  | Name: Zachary Milligrock Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Kelly Anungazuk Title/Position: Accompanied By? No Telephonic Contact? No | Name: Kolt Garvey Title/Position: Accompanied By? No Telephonic Contact? Yes | Name: Debbie Title/Position: Vice-Mayor Accompanied By? No Telephonic Contact? No | [6 empty] | Emergency Pressure pump Repair. | WTP: Went to WTP and the water plant area was dark and cold.Looked thru pressure pump 1 would not run or run a little bit and get hot.Looked at PP2 and would not run so had Zachary go upstairs and get a new one.Changed that out and it ran and the lights went on boiler and Glycol circulating pumps started up. Switched the wires around in PP1 it started and after awhile the pressure pumps started to run erratically.After awhile no more power to the pressure pumps,boiler and glycol pumps.Went and checked the breaker panel and nothing had tripped. Called Kold Garvey(Senior Journeyman Electrician) ANTHC helped me diagnose the problem and told me what to look for.Checked the voltage on the PP1 123V on one side 8.5V.Opened up electrical box in front of PP's and the was a few loose wire nuts.Went outside and looked at AVEC connection From power pole to building,no visible damage. Asked if Zackary had an alternate source of heat,nothing he said.Told him to look for one to use in the morning. Clinic: Larry Sereadlook had come and asked Zackary and I can help him install a flow meter.Which would help the City/WTP keep track of the water clinic uses each month.We cut and fit the meter in place and soldered it up. Larry put up unistrut to secure the meter. 11/3/16 Called AVEC and reported the 1/2 power to the WTP. They said a lineman was heading to Wales on the evening flight. I found a HEAT STAR HD 50,000 BTU space heater and warmed the almost freezing WTP.Took awhile to heat up the whole place up. Found a long enough extension cord to power a pressure pump to charge the system.Took the pump we took off and changed the power setting to 115 to run the pump.Wired it up and it worked.Went and changed the setting on one installed and hooked it up. Could not get it to work on the starter,so had to wire straight to the pump.Had Zachary keep the water charged up to 40 PSI for couple hours.I went and checked the teacher housing(4-plex)water had good pressure.Went to the clinic and even with booster pump and circulating pump the pressure was really low.The line to the clinic was slushed up(starting to freeze) in the service line.Ran the faucets for awhile. Turned on heat tape after long time flow returned to normal.Help Larry diagnose the problem with the life water system.found that the UV light had burnt out,changed that out.Still not working properly and we think the blower was out.Looked up what parts needed to be ordered and showed him. Headed back to WTP and changed back the setting back to 230V ,wired back to the starter.AVEC lineman made it in worked on school service,after he was done there came to fix WTP service.WTP back to normal operation. | 20 | 40-year-old WTP showing its age. |  |  |  |  | 40-year-old WTP showing its age. | No |  | No |  | No |  | No |  | No | Order all the critical replacement parts needed to keep the place running. | Operator | [9 empty] | Attachments | Other Documents | 2016-11-07 09:28
RMWTR-1491 | YKHC | Scammon Bay | Billy Westlock | 2016-11-03 | 2016-11-03 | Other | $1,560 |  |  |  | Grant aviation | No |  | Name: Carlie George Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Noel Utteruiuk Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: Lizzy Buckingham Title/Position: Environmental Health Officer Accompanied By? No Telephonic Contact? No | [7 empty] | Assist water plant operators with lagoon samples Assist eho Lizzy Buckingham with sanitary survey. | I arrived into Scammon bay and met with WPO George at about 11 a.m. We met with eho Buckingham and proceeded over to the lagoon where we took a few grab samples that needed to be done. For the rest of the day eho Buckingham the wpo's and I conducted a sanitary survey and completed at about 4 p.m.. With the lagoon grab samples from the lagoon and survey completed I departed Scammon bay at 530 p.m. | 3 | None at this ti,e |  |  |  |  | None at this time | No |  | No |  | No |  | No |  | No | None | Unknown | [9 empty] | N/A | Other Documents | 2016-11-07 08:27
RMWTR-1492 | DEC | Nondalton | Steve Evavold | 2016-11-02 | 2016-11-04 | Routine | $500 | $150 |  |  |  | No |  | Name: Joanna Trefon Mayor Title/Position: Accompanied By? No Telephonic Contact? No | Name: Carrie Harried City Administrator Title/Position: Accompanied By? No Telephonic Contact? No | Name: Jesse Trefon WTP Operator/Maint Title/Position: Accompanied By? No Telephonic Contact? No | [7 empty] | Scope of work was to attempt to pull inoperable pump/motor in well #2. A rock dropped into the well, seen with a camera, had wedged the pump against the well casing and a previous attempt couldn't pull it out. If retrievable, I wanted to replace the motor with a spare, and return well to service. Utility looked to be unable to keep up indefinitely on one pump for the winter. Media in Adage Arsenic removal filters needed to be inspected. OJT with operator on backwashing filters, sampling, and daily operator reporting requirements. | Arrived in Nondalton and met with Jesse. The "lead" operator was gone from that position, and Jesse(listed as alternate), was keeping up with the water plant, city maintenance, garbage collection, and mail. Initial assessment in the water plant showed 0.2ntu treated water(read from the HACH SC200 controller), 28gpm pumping from the #1 well, and a trace chlorine residual from the plant sink. The pressures through the four sets of "Roughing and Polishing" filter vessels were up to 10psi(20psi requires replacing). I turned up the speed and stroke on the chlorine pump, by the end of the day I got a 0.46mg/l free chlorine residual from the water plant sink(entry point). There was a "dripping" flow to the turbidimeter. I turned up the flow, reseated the head on the 1720E and the turbidity dropped to a normal display of 0.02ntu. The transfer pump came on. The well(s), pump water through the plant processes and up to a small contact tank for disinfection outside the plant. When water level in the "CT" reaches 12.5', a transfer pump comes on and pumps water up to a larger 100,000 gallon storage community tank. the transfer pump shuts off when the CT level drops to 8.5'. With a possible leak in the distribution system, one well pump running, and residents running water overnight(for freeze protection), it's been difficult to keep any level of storage. Homes at the higher elevation have run out by morning. The "Adage" filter system, installed for Arsenic removal hadn't been backwashed. A reoccurring concern was made for media assessment and a visual inspection for depth. The instructions for Backwash, or "Rinsing/Fluffing" were vague for the flow requirements during the process. Early on, the operators just increased the backflow until media was seen in a sight glass for the discharged water. Flow was decreased until media was no longer seen. Jesse and I isolated the #2 filter, drained the water and removed the hatch on top. There was no build up of anything on the surface; the media looked fine; there was no additional sediment or debris mixed in. There was indication that about 2 inches of media was lost by the discoloration on the inside wall of the filter. I took samples of the media for analysis. Jesse secured the hatch and we backwashed both filters. ANTHC, TUS, had sent down some fuses for the pump controls, and a light bulb for one of the transfer pumps. The thought was maybe a fuse had blown in the controls for the inoperable pump. Jesse had already replaced the fuses. I turned the control for well #2 to manual and noted that the breaker had tripped. The problem was not in the panel. We went up to the city office to meet with the city administrator, Carrie Harried. We discussed the well problems and water plant needs. The plant was low on bag filters and HTH. On a previous trip, ANTHC electrician had looked into the need for a level control in the community storage tank. There is no transducer/signal generator available to give the operator indication of height of water in the tank. GCI has a satellite dish and a support shed up next to the WST. GCI has to be called for access to the shed. An electrical outlet will be needed for a power supply to generate the 4-20ma signal which would be sent to the water plant and display height of water on the Allen Bradley Panel View. GCI had not been called. I asked Jesse to start up the frontend loader and meet me down at the wells so we could make an attempt to pull the pump from well #2. The well pump motor had tripped the water plant breaker last spring and wouldn't reset. City maintenance had tried to pull the pump, but the drop pipe broke loose below the pitless adapter leaving the pump and 12' of pipe at the bottom of the well. On a previous trip I had sent a camera down the well and found a rock had been dropped in and had wedged in between the pump and well screen. One of the local maintenance guys had dropped a "Snare" down and caught the pipe still connected to the pump. The pump proved to be stuck with the rock when a lift was attempted. We tied the snare wire to a 4x4 across the forks of the loader and lifted. We thought the snare was going to snap at about a foot, but the pump/motor, and pipe assembly sprung loose and came up without too much effort. The rock when dropped in had settled on the wiring for the motor. The torque of the pump eventually severed the black wire and tripped the breaker in the plant. In the morning Jesse and I looked for the spare pump and motor supposedly on hand. When found I noted it was a 5HP pump and rated for a larger flow than the Nondalton Well could supply. The motor for that pump was in a box with a label that gave indication that the Pump/Motor had originally been destined for Kokhanok, not Nondalton. There was another motor in the water plant that looked new. When wired up it just hummed. We decided to resplice the wires to the motor we pulled and test operation. The motor worked fine and had good torque so we decided to send it back down the well. Both wells are pumping again. I inspected the lift station and wastewater collection system. ANTHC had installed new control panels and the unit was functioning. Several of the manholes along Hill Street and Main street have been moved off center by erosion, decaying concrete, etc., and are allowing sand, gravel, and ground water infiltration. | 10 | The water plant is out of bag filters for the Strain Rite filter vessels and is on the last bucket of HTH for chlorine disinfection. | GCI needs to be called and asked for access to an outlet. ANTHC, TUS will install a pressure transducer for the community storage tank when access is available. |  |  |  | There is still approximately 4000 feet of distribution system and 20 service connections along main street yet to be replaced. This section is a constant source of water leaks. | No | Due to road erosion and ground movement the sewer collection system is falling apart. Manhole sections are degrading and top sections and lids are off center, allowing sand/gravel and groundwater infiltration. Main street, and Hill street collection system need engineering inspection. | No | The water source is 2 shallow wells along the edge of 6-mile lake, that are a source of Arsenic. The treatment process for this made for a difficult treatment process. A new water source such a collection gallery into the lake should be considered for a (PER), Professional Engineering Report. | No |  | No |  | No | A request was made for well-head protection. There are no sanitary seals or electrical protection at the well site. | Community | [9 empty] | Attachments | Other Documents | 2016-11-22 10:30
RMWTR-1495 | TCC | Birch Creek | Fred Kameroff | 2016-10-31 | 2016-11-01 | Emergency | [5 empty] | No |  | Name: Vincent Williams Title/Position: Other Accompanied By? No Telephonic Contact? No | Name: Walter Williams Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: William James Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: Lawrence James Title/Position: Tribal Council Member Accompanied By? No Telephonic Contact? No | Name: Wes Shales Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | [5 empty] | Diagnose Well pump | Mrs. Mary James contacted me on 10/28/16 stating that there was no water getting to the water plant, and that they thought it may have frozen. I asked her when did this happened, she stated two days ago. I asked where Mr. Vincent Williams was, she said he was there at Birch Creek. I then told her I would contact him. I contacted Mr. Williams and asked what was going on with the well house; he stated the transmission line may have froze. I then told him that Mr. Wesley Shales and I would be heading out on 10/31/16. Mr. Wes Shales and I arrived at Birch Creek and were greeted by Mr. Williams and escorted to the water plant where we started to check on the controls for the well pump. Once Mr. Shales and I looked at the control panel and found everything was working okay, we made our way down to the well house. We checked the 3 motor leads and found they were all good with Diagnose Well pump Ground and the control box looked to be in good working order. We then asked Mr. Williams to go up to the water plant a kick on the power for the pump, and when he turned on the pump switch the drop pipe made a thud noise indicating the motor kicked on, but no water came out of the ¾ inch water spigot. We figured the drop pipe was frozen. A heat tape was in the well vault casing but was not hooked up to a power cord. Mr. Shales then spliced up the heat tape with a power cord and once he was done we plugged it into the outlet. Mr. Shales checked the amps with a volt meter and found the heat tape was working normally. By the next morning we made our way to the water plant and turned on the pump and to our finding the pump was pumping water into the raw water tank. We then filled up the first tank and waited for Mr. Walter Williams to show up to start treating water. Mr. Williams came by and we told him the well drop pipe was thawed out and we filled the raw water tank and he can now treat water, 60 gallons of water was treated in 1 hour and40 minutes. RECOMMENDATIONS/CONCLUSION Water has been restored at Birch creek and residents started to get water during the day, prior to our departure we tested the well pump to make sure it was still pumping water. | 8 | none |  |  |  |  | none | No |  | No |  | No |  | No |  | No | operator | Operator | [9 empty] | N/A | Other Documents | 2016-11-11 15:23
RMWTR-1496 | YKHC | Anchorage | Shane McIntyre | 2016-11-07 | 2016-11-11 | Training/Meeting | [5 empty] | No | [11 empty] | Training on lift stations and pumps. | I flew in to Anchorage Monday the 7th for lift station and pump training held at the RMW shop. I Reported to the RMW shop every day at 8 am and we were released by the instructor. | 0 | none |  |  |  |  | none | No |  | No |  | No |  | No |  | No | none | Unknown | [9 empty] | N/A | Other Documents | 2016-11-14 13:45
RMWTR-1497 | YKHC | Tuluksak | Bob White | 2016-11-09 | 2016-11-09 | Routine | $220 |  |  |  | Raven Air | No |  | Name: Jarah Peter Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Carl Peter Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Kristy Napoka Title/Position: Utility Clerk Accompanied By? No Telephonic Contact? No | Name: michael Vincente Title/Position: Environmental Health Officer Accompanied By? No Telephonic Contact? No | [6 empty] | Install Heat Exchange. Assist with Sanitary Survey. | When we arrived at the Washeteria we set out all the supplies on the work bench and found we needed a couple additional parts. We then contacted the school and looked arround the plant until we found the 4 additinal fittings. We then cut out the old heat exchanger and started to rebuild the new piping. We installed a bypass so not all flow has to go through the heat exchanger so we don't get velocity errosion in the heat exchanger any more. Once we had everything back together we were getting 15 degree drop on the glycol across the heat exchanger. Happy with the flows and heat we moved on to the Sanitary survey questions. We then discussed there maintenance logs they were doing making some adjustments to what they were recording. | 7 | The plant looked the cleanest I have ever seen it. |  |  |  |  | Holes in the floor. | Yes | leak on the school water line under Washeteria. | Yes |  | No |  | No |  | No | Patch the floor with the plywood that is onsite. | Community | Replace dielectric union on Boiler #1 | [8 empty] | N/A | Other Documents | 2016-11-16 10:31
RMWTR-1498 | NSHC | Teller | Bryant Koonooka | 2016-11-15 | 2016-11-15 | Routine | $200 | $75 |  |  | Ford truck | No |  | Name: Blanch Garnie Title/Position: Mayor Accompanied By? No Telephonic Contact? No | Name: Jerry Okbaok Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Jonathan Kakaruk Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Robert Dickson Title/Position: Other Accompanied By? No Telephonic Contact? No | Name: Debra Addie Title/Position: VSW Engineer Accompanied By? No Telephonic Contact? No | Name: Sean Lee Title/Position: VSW Engineer Accompanied By? No Telephonic Contact? No | Name: Kyle Peterson Title/Position: Design Engineer Accompanied By? No Telephonic Contact? No |  |  |  | Site visit ,BSSD meeting handing over WTP to City. | Jonathan Kakaruk gave me a tour of their WTP,Everything running fine Except for couple pin holes in the 3/4 copper piping.We try to go see the place they pump water,but ice prevented us from getting there. Robert Dickson showed us around ,their honey bucket/trash trailer.Told us how people put their honey buckets in a cardboard box a let it freeze in the winter.Makes for easier to transport to the disposal site.Showed us a metal honey bucket bin they haul around in the summer.They collect the waste and haul it few miles to dispose of it at their landfill and honey bucket lagoon. BSSD City meeting: Blanche Garnie(mayor),Gary Eckenweiler(BSSD),Jerry Okbaok(WPO),Lena Mathlaw(RUBA),Myself(RMW), Debra Addie,Shawn (VSW)and Kyle(Bristol). Lena started by introducing everyone.Meeting went very well. BSSD was willing to transfer the water plant over to the city.They discussed how the transfer would work out.Gary asked if they had a certified WPO.Jerry Kakaruk is certified level 1 water treatment and distribution.They discussed how the city would be doing the billing. The School would provide fuel for now, city will look for a way to get fuel and storage for the future.They decided to do the transfer at the end of the school year which is in may. We asked the school to provide numbers of how much fuel the WTP uses.How much water the school uses.And some more technical data they can provide. | 2 | Couple pin holes in the WTP. |  |  |  |  | A couple pin holes in the WTP. | No |  | No |  | No |  | No |  | No | Fix the pin holes. | Operator | [9 empty] | Attachments | Other Documents | 2016-11-17 14:46
RMWTR-1499 | TCC | Nulato | Lee Meckel | 2016-10-31 | 2016-10-31 | Routine | [5 empty] | No |  | Name: Greg Patsy Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Van Madros Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | [8 empty] | Fix a leak. | Upon arrival to Nulato I was taken to the washeteria in the lower town site. There I was shown a leak coming out of the well transmission line where the line entered the building and transitioned from HDPE to a steel flange. The steel flange connects directly to a 2” copper threaded male adapter that connects to a sight glass, then is reduced down in diameter to a 1-1/2” ball valve. The leak was in the copper reducer. After the ball valve, the copper pipe continues after the valve up to a 90 degree elbow. The vertical section of this piping is approximately 4’ in length and continues to the water storage tank array. Mr. Patsy had already purchased the parts that he needed to replace the leaking copper fittings in Fairbanks. I picked them up and brought them with me. Mr. Patsy wanted the piping replaced from the flanges past the 1-1/2” copper elbow. He explained to both Mr. Madros and myself that the reason he wanted to replace so much was due to the amount of pitting he was sure had occurred in the copper. He continued to explain to us that the old system never had any protection from galvanic corrosion, and so he had purchased a dielectric union to help act as a barrier between the two different metals, plus it allows access to the plumbing for repair. We cut the 4’ vertical portion of 2” reduced to the 1-1/2 copper as close to the soldered 90 as possible. Then we were able to break the corroded piping threads on the copper adapter and remove the old section of pipe that had been leaking. Due to the lack of couplings for the 1-1/2” copper pipe, we had to carefully heat up the existing solder on the 90 so it could be removed without damaging the existing pipe in order to allow the new Pro Press 90 to crimp the pipe and act as a coupler to the existing pipe. I removed the plastic insulators/ gaskets from the dielectric union and measured out the amount of 2” copper needed to reach the 2” pro press valve, then I soldered it in and replaced the gaskets/insulators and from there I threaded in the new union to the flange. I then used the Pro Press to secure in the valve and copper to the union and then used the same tool to reduce back to 1-1/2” diameter copper. I then measured the amount of pipe that needed to be removed from the horizontal portion that we had sweated off and then crimped to the existing plumbing. | 2 | Some pitting in the copper lines. |  |  |  |  | none | No |  | No |  | No |  | No |  | No | After the removal of the 1-1/2” copper elbow there were obvious signs of pitting and corrosion inside the line. Mr. Patsy has removed much of the old pluming and replaced with PVC to help with this issue but still adds orthophosphate to help inhibit corrosion in the metal portions of his system. This should be enough to address any further corrosion. | Operator | [9 empty] | N/A | Other Documents | 2016-11-18 08:33
RMWTR-1500 | TCC | Northway | Lee Meckel | 2016-11-09 | 2016-11-10 | Routine | [5 empty] | No |  | Name: Terry Albert Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Carl Carbon Title/Position: Accompanied By? No Telephonic Contact? No | Name: Wesley Shales Title/Position: Accompanied By? No Telephonic Contact? No | [7 empty] | Perform boiler combustion tests/tune ups and get an overview/consult on operator concerns with the water treatment and storage as well as address sanitary survey highlights. | I was contacted by Mr. Albert in Northway, he had expressed interest in having us look over his Weil Mclain Boilers and help prepare them for winter. Once we arrived Mr. Albert had already completed the cleaning of the boiler in the water treatment plant. I had brought along the Testo 320 flue gas analyzer to get a better idea of how the boiler is running. We tested the boiler and raised the Co2 from 4.2% to 9.48%. The eff. was 77% with a stack temp of 640F degrees after adjustment had been made. Typically oil fired boilers average 75%-85% efficiency. I did not have my fuel gauge to check the burner psi but will return and make sure that the fuel pumps are set at the correct pressure .We then went to the garage next door to the washeteria that houses the water truck. There we looked at two more boilers and made a few more adjustments to the air bands to get them up to the most efficient running operations possible. While we were at the garage we looked at the old RPZ that had frozen and broke and we will be getting quotes for a new one as well as new NSF-61 rated hose for the water truck so that we may look in to getting system wide approval to operate from A.D.E.C We also looked at the water storage tank (WST) in the washeteria and plan on making some repairs to some of the plumbing inside the tank as well as adding a grit separator to the transmission line. We will also plan on cleaning the tank out while completing repairs. There were also discussions involving the Cl dosage and what could be done to increase the residual in the larger WST. | 8 | The WST needs to be bolted back together on the top portion. Terry and I have already scheduled a time to repair this. |  |  |  |  | WST ladder is accessible needs a lock. | No |  | No |  | No |  | No |  | No | I have been working with Mr. Albert on getting quotes for the parts necessary to complete all repairs in the plant so that the plant may receive system wide approval to operate as well as handle any noted deficiencies from the recent sanitary survey. Once the parts are acquired Mr. Albert and I will be Scheduling some time to remedy these issues in December. | RMW | [9 empty] | N/A | Other Documents | 2016-11-18 08:45
RMWTR-1501 | YKHC | Napakiak | Bob White | 2016-11-08 | 2016-11-08 | Routine | $200 |  |  |  | God's Country Aviation | No |  | Name: Alysa Gustufson Title/Position: Environmental Health Officer Accompanied By? Yes Telephonic Contact? No | Name: Tom Bobo Title/Position: Other Accompanied By? Yes Telephonic Contact? No | Name: Leo Kusayha Title/Position: City Administrator Accompanied By? No Telephonic Contact? No | Name: Greg Aluskak Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [6 empty] | Give a tour of the Water Treatment Plant to the City council. Make a updated list of needed Repairs. | When we arrived at the city office we were met by Leo and we confirmmed the days schedual then we wentstarted doing a Hazard Vunrability Analysy. Once we completed the HVA we then started with gathering information on each of the system componets and condition. When the council met at 1 PM we took them to the water plant and gave them a tour explaining how the system worked. We then finished gatherring information on each of the system componets and there condition. | 7 | The council learned a lot durring the tour of the plant. |  |  |  |  | Report to be made soon. | No |  | No |  | No |  | No |  | No | Order the boiler parts I indicated so we can start saving on fuel imediatly. | Community | [9 empty] | N/A | Other Documents | 2016-11-21 09:03
RMWTR-1502 | YKHC | Emmonak | Billy Westlock | 2016-11-08 | 2016-11-09 | Training/Meeting |  |  |  |  | Personal atv | No |  | Name: Emmonak city council Title/Position: Other Accompanied By? No Telephonic Contact? No | Name: Debra Addie Title/Position: VSW Engineer Accompanied By? No Telephonic Contact? No | Name: Jamie Agwiak Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [7 empty] | Take a look at the vsw housing project with vsw engineer Addie, also attend a meeting with the city council concerning possible new upgrades for emmonaks future. | On Tuesday I assisted with inspection of a few houses that were completed by vsw plumbing crew which they did a very nice job. Later in that evening I attended a city council meeting concerning a perposal needed for water plant upgrade, and other possible tests to produce more water which is starting to be a major problem at certain times of the year. Hopefully vsw will come up with some solutions to take care of our water issues. Thru the next mornin I continued on inspecting homes that were completed until around noon. | 0 | None |  |  |  |  | None | No |  | No |  | No |  | No |  | No | None at this time | Unknown | [9 empty] | N/A | Other Documents | 2016-11-21 08:52
RMWTR-1503 | YKHC | Emmonak | Billy Westlock | 2016-11-14 | 2016-11-14 | Emergency | $57 |  |  |  | Personal truck | Yes | 7 miles | Name: Jamie Agwiak Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: Arthur Redfox Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Ridge contractors Title/Position: Construction Staff Accompanied By? No Telephonic Contact? No | [7 empty] | Assist with fire vacuum pumps catching fire number 1 vacuum pump. | At about 5 and 6 am vacuum pump number 1 caught fire, causing a lot of damage to the plumbing works, electrical, and structure to the building. This fire was the worst one ever to the water plant, reaching the ceiling. I took a look after the fire was out and I tried looking into getting the other vacuum pump going but everything above the vacuum pump and around the vacuum pump was to unstable. All the plumbing works and electrical for the pump were severely damaged and will not operate. After looking over everything there wasn't anything could do until the building was stable again and safe to work in. | 0 | need to watch over the pumps when number 2 vacuum is running again to make sure it doesn't get to hot |  |  |  |  | None | No |  | No |  | No |  | No |  | No | I will keep in touch with the water plant operators to see how pumps are doing | RMW | [9 empty] | N/A | Other Documents | 2016-11-21 09:15
RMWTR-1505 | MHC | Ambler | Jeff Luther | 2016-11-17 | 2016-11-18 | Emergency | [5 empty] | No |  | Name: Tony Tickett Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Roy Ramoth Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [8 empty] | Frozen water in take line | Went out there, verified that the heat tape was on at the plant & the lower lift station. Changed the water heating coils on the hot box & verified that it was working properly with the pressure washer & reaching the temperature settings, went down to the lift station & check the amperage on the heat tape, there was no amps, saw that the breaker to the two heat tapes wasn't on, turned it on & verified that heat was going through. After jetting from the plant down the line & getting the heat tape on the line opened up & we had water flowing through. | 7 | water hammer in pressure tanks |  |  |  |  | water logged or lack of air in pressure tank bladders | No |  | No |  | No |  | No |  | No | remove water logged or add air to bladders in pressure tanks | Operator | [9 empty] | N/A | Other Documents | 2016-11-21 09:24
RMWTR-1508 | DEC | Scammon Bay | Kevin Schoneman | 2016-11-01 | 2016-11-02 | Other | [5 empty] | No |  | Name: Elizabeth Buckingham Title/Position: Environmental Health Officer Accompanied By? No Telephonic Contact? No | Name: Brian Lefferts Title/Position: Environmental Health Officer Accompanied By? No Telephonic Contact? No | Name: Billy Westlock Title/Position: RMW Accompanied By? No Telephonic Contact? No | [7 empty] | Assist with Waste Water Lagoon sampling. | I arrived at the airport @ 1700 to check in for the scheduled departure time of 1900, I arrived in Bethel at 2000. The next morning I arrived at Raven Air and was joined by Elizabeth Buckingham with YKHC at 0700 for the scheduled 0825 flight for Scammon Bay. At 0830 they announced that the flight was being delayed due to weather in Scammon Bay and there would be a update at 0930. At 0930 they announced that the flight was still on a weather hold and that there would be an additional announcement at 1030. At 1040 they announced that the flight to Scammon Bay was going to be cancelled for the day. After we both received our bags back we decided to go to the YKHC office and come up with a plan for the next day. We arrived at the office at 1100, when we arrived at the office we were able to meet with the Program Manager, Brian Lefferts. We informed Brian that the flight to Scammon Bay had been cancelled and we trying to come up with a game plan for the next day. Brian called RMW Billy Westlock for Scammon Bay who was planning on meeting us and was holding his travel from Emmonak. We as a group went over the sampling locations and talked about possible alternative sample sites if needed, we also discussed the possibility that the sampling may have to be rescheduled for a later date. Brian informed Billy that we would look at the weather and pick a different day for the sampling. Brian, Elizabeth and I continued our discussions about the sample collection and the chain of custody and report form, I informed them that I had picked up a extra sample kit before I left Anchorage in case there was any delay with the kits we had arranged to be delivered before our arrival. Brian brought out a satellite map of the lagoons and we identified each proposed sample collection point. It was decided that Elizabeth and I would go through the kit that I had brought with me and fill out as much of the paper work as we could. It was also decided that Elizabeth and Billy would attempt a trip the next day or week depending on weather and their schedules. That afternoon Elizabeth and I went through the paperwork and sample kit and discussed the sample collection procedures. Elizabeth dropped me off at the terminal for my flight back to Anchorage, I arrived back in Anc. @ 2200 | 0 | None Noted this trip. |  |  |  |  | None Noted | No |  | No |  | No |  | No |  | No | Annual Lagoon Sampling | Operator | [9 empty] | N/A | Other Documents | 2016-11-25 11:12
RMWTR-1509 | DEC | Ouzinkie | Steve Evavold | 2016-11-14 | 2016-11-16 | Routine | $500 | $150 |  |  |  | No |  | Name: Dan Clarion Mayor Title/Position: Accompanied By? No Telephonic Contact? No | Name: Cliff Panamarioff Water Plant Operator Title/Position: Accompanied By? No Telephonic Contact? No | [8 empty] | The pressure sand filters had lost 4 inches of Anthracite over time; the operator asked for assistance with adding new media. The raw water check valves were not opening as constructed. I wanted to dismantle and inspect, or remove the assembly. The 21" raw water penstock for the reservoir had cracked. ANTHC and the city were in discussion about the best way for repairs. I was asked to inspect and assist. | Arrived in Ouzinkie and met with Cliff. The 6' check valves on the raw water intakes for each filter were independently failing to open/close as installed. This caused the flow to each filter to be inconsistent, and the loading rate was uneven. Cliff isolated the valves and we took turns on the ladder, got the valves down, removed the inside mechanisms, and reinstalled them. There were 22 bags of Anthracite on hand to load into the filters, 11 each. Cliff and I removed the access hatches on top of the filters, and Dan had a couple of the city maintenance guys assist with the lifting and loading the media. When done Cliff partially filled the filters with treated water from the WST, enough to submerge the new anthracite. We agitated the media with air scour to "sink" the anthracite that was floating, and we left the filters soaking overnight. In the morning we "rinsed" the filters with a slow rate of backwash for an hour each to lift and float out the fines/dust left in the anthracite. Then we drained down the water levels and air scoured again for 30 minutes, then again initiated a slow backwash, and repeated the procedure a third time. When comfortable with water clarity through the viewing port we "Filtered to waste" for most of the day, until effluent turbidity dropped to <0.10. Cliff and I cleaned/calibrated the pH probes and housings, along with the Turbidimeters. The M Roy soda ash pump is still set on manual operation at a 30% stroke. The ECC(Electronic Capacity Controller) for automatic function needs replacing or calibration. I caught up with Dan Clarion later in the day. He was gearing up for an attempt to slide a coupling onto the 21" PVC penstock transmission line from the reservoir to secure a replacement section of the pipe. The schedule 80 PVC penstock is approximately 30 years old. The pipe supplies raw water to a hydroelectric plant and further down to the water plant. Areas where access to the pipe for inspection over the years has brought forth concern for the integrity and life span of the material. PVC becomes "brittle" after so many years. The underside of the pipe crushed inward in a place about 400 yards downstream of the reservoir. A local resident noticed the significant runoff separate from the existing stream and notified the city office. Once the stream was identified as coming from a break in the raw water transmission line, the isolation valve for the reservoir was closed. The Hydroelectric plant was shut down, and the city generators were started. The back up water supply, a wet well gallery run by pumps, was started. ANTHC engineering and the TUS unit had been to the site for a visual inspection and supplied the equipment needed. The damaged section was cut out and a replacement section of pipe was laid in the trench. The downstream coupling was in place, the upstream coupling was needing more assistance to help it slide up to secure the next section of pipe. Dan decided to make a metal "collar" with hooks ahead of the coupling, to use with a couple of 1/4 ton come-along cable hoists either side to work the 21" PVC coupling into place. That was going to require a trip into Kodiak for fabrication. I checked the water plant and effluent turbidity one more time and left on the next flight. Follow up: Dan had a bracket made for the penstock and had successfully slid the 21" PVC coupling into place, and centered over the two sections. The penstock supply of raw water was reinstated, the hydroelectric plant is back up(Partially), and the diesel generators were at a diminished setting. Cliff said the water plant is running with normal numbers for effluent treated water. The filters looked to be loading evenly now. | 8 | Nothing noted at this time of report. |  |  |  |  | The 21" PVC penstock supply from the reservoir can fracture/rupture at any time and drain the reservoir. Replacement process should be initiated. | Yes |  | No |  | No |  | No |  | No | Nothing noted at this time | RMW | [9 empty] | Attachments | Other Documents | 2016-12-14 14:18
RMWTR-1510 | DEC | Port Protection | Kevin Schoneman | 2016-11-16 | 2016-11-18 | Routine | [5 empty] | No |  | Name: David Kahn Title/Position: Other Accompanied By? Yes Telephonic Contact? No | Name: Leslie Fahey Title/Position: Public Works Director Accompanied By? Yes Telephonic Contact? No | Name: Christa Hambleton Title/Position: Water Operator Accompanied By? Yes Telephonic Contact? No | Name: Terry Metcalf Title/Position: Water Operator Accompanied By? Yes Telephonic Contact? No | [6 empty] | Meet with the operators and work with DEC Engineer David Kahn on the system Sanitary Survey. | I arrived at the airport at 0900 on Wednesday November 16, for the flight to Ketchikan which departed Anchorage at 1100 and arrived at 1715. The next morning I arrived at the Taquan Air for the flight to Port Protection. I was joined at the terminal by David Kahn, Drinking Water Engineer for The State of Alaska. The flight was slightly delayed, we departed Ketchikan at 1030 and arrived in Port Protection at 1200. We were greeted at the dock by utility manager Leslie Fahey, Water Operator Christa Hambleton and Water Operator Terri Metcalf. After we introduced ourselves we all went to the Wooden Wheel Trading Post to drop off our bags and discuss the itinerary for the visit. We decided that we would just hold an informal meeting there at the trading post to discuss the information required for the sanitary survey. The first topic we talked about was the roles and responsibilities, Leslie stated she had been asked to take on the role of Water Manager which she agreed to accept and she is responsible for the book keeping, reports and records keeping as well as payments for water samples and repair parts. Christa stated that she was Port Protections (winter operator) and is responsible for the operations and maintenance of the drinking water system during the winter months. Terri stated she was the (summer operator) and was responsible for the system during the summer months. They all agreed if they were present and able they all contributed on a daily basis if needed. We also discussed the required water system plans such as the Emergency Response Plan, Routine Site Sampling Plan as well as implementing and submitting the Preventative Maintenance Plan. David asked the operators if any major changes had been made to the water system since the last survey and both of the operators replied “no major changes other than routine maintenance have occurred since the 2013 survey”. David also asked about the current water quality monitoring requirements, and Christa responded that as far as she knew “everything was current” which was confirmed by the system monitoring summary. We also briefly discussed the pending source re classification and the process and possible consequences. We also covered Christa’s and Terri’s certification requirements which they both stated they were aware of and working on their renewals. We then decided to begin a tour of the distribution system and hike up to the water storage tank. Leslie, Christa, Terri, David and I hopped into a skiff for a short ride to the other side of the harbor since the tide was in at the time. Once on the other side we began the hike up the boardwalk checking out the main line, fire hydrants and service connections along the way. Most of the water distribution system in Port Protection is above grade in most portions. As we made our way up the boardwalk we stopped by the community building where most of the files and paperwork is kept. As we continued on we encountered a section of the boardwalk that was being repaired and Christa explained that the boardwalk had been damaged in a recent pattern of high wind storms. The section of boardwalk just before and after the water storage tank was pretty much demolished, in one area a very large tree was blown over and fell across the village main water line but did not damage or break the line, one tree also narrowly missed the water storage tank. We inspected the water storage tank, the tank has only a couple of very small leaks and is in reasonably good condition. The operators both commented that some of the bolts on the inside of the tank are deteriorating and show sign of corrosion. We continued up to the spring box, the spring box is a concrete and wood frame building and is covered, locked and secured. Christa and I crawled inside the spring box to look at the drain valve for the spring valve the valve handle and operation stem are missing. There is also a couple of very large trees that appear to pose a threat to the spring box. We also looked at the control valves outside of the spring box, by this time we decided we should begin the hike back down to the trading post. The next day we met with Christa at the trading post and made another hike back up to the tank and spring box to get a GPS shot of both places for the sanitary survey. After a quick trip up and back we finished up with more discussion about the source and the future priorities for Port Protection water system. Our plane arrived at the dock at 11:00 and we boarded for our return to Ketchikan. I arrived back in Anchorage at 2130. | 4 | The valve stem and handle for the spring box drain are missing and need replacement. | There are several very large trees in the area around the water storage tank and spring box that should possibly be removed. |  |  |  | Dry suit for cleaning the spring box. | No |  | No |  | No |  | No |  | No | Research the valve replacement in the spring box. | RMW | Look into the removal of some of the threats to the water storage tank and spring box. | [8 empty] | Attachments | Other Documents | 2016-12-08 09:38
RMWTR-1511 | DEC | Newhalen | Floyd Murphy | 2016-11-15 | 2016-11-17 | Routine | $460 | $150 |  |  | Airplane | No |  | Name: Brian Menghini Title/Position: ANTHC Engineer Accompanied By? No Telephonic Contact? No | Name: Nick Johnson Title/Position: Wastewater Operator Accompanied By? No Telephonic Contact? No | Name: Gladys Askoak Title/Position: City Clerk Accompanied By? No Telephonic Contact? No | Name: J C Crawford Title/Position: Project Superintendant Accompanied By? No Telephonic Contact? No | Name: James Lamont Title/Position: Other Accompanied By? No Telephonic Contact? No | [5 empty] | Travel with ANTHC Engineer to inspect the new list sewer lift station and work with the operator on O & M of the lift station. | Newhalen Report: 11/15 – 17/16 11-15- 17-2016 To inspect newly constructed Lift Station, provide training to the operator. 11/15/16. I departed Anchorage for Newhalen on Iliamna Air Taxi around 11:00 Am arriving around 12:20 PM. I was met by a member of the community of Newhalen who gave me a ride to the Community of Newhalen. I made arrangements to meet with the operator, ANTHC Engineer and ANTHC Construction Superintendent after lunch. We met at the newly constructed sewer lift station building. The Building has 2 rooms, a wet well room and a dry control room. We also inspected the force sewer main from the lift station to the lagoon. The Superintendent, JC Crawford was still finishing up work on the site. Brian Menghini, ANTHC Engineer explained the sewer process from the community through the septic tanks than through the lift station and force main to the sewer lagoon to Nick Johnson the operator for the community. The septic tanks remove the sludge from the system and the supernatant goes to the lift station. 11/16/16 Nick, Brian and I arrived at the new lift station at 8:30 am to go over the operation and explain to Nick the operation and maintenance of the lift station. We removed the catch basket and a pump as a demonstration and training for pump removal and replacement, we also adjusted the sewer flush valve for more action to mix the bottom of the sewer lift station prior to pumping effluent. We tested all floats for operation and audible and visual alarms. Nick was instructed on the alternating relay and pump sequencing. Nick was shown the electrical schematic which he was unable to understand better. After lunch we located the confined space equipment. All equipment was accounted for and the 4 gas analyzer was also located. Nick was instructed on use along with testing the gas detector in the lift station. The ball check valves on the effluent lines after the pumps were not operating properly. They are slated to be replaced by swing check valves. 11/17/16 Nick and I went through the Water Monitoring Summary for Newhalen. A couple of tests were needed to be taken to get the system back into compliance. Nick was to call the ARUC manager to get the sample kits to him to get the samples taken. We went over the training that was given over the past couple of days, Nick was comfortable with the instruction so far. I departed Newhalen for Anchorage around 3:45 pm arriving around 4:15 pm. | 12 | None at this time as construction and corrections are being made to the system. |  |  |  |  | None at this time | No |  | No |  | No |  | No |  | No | None at this time | Unknown | [9 empty] | Attachments | Other Documents | 2016-12-01 15:15
RMWTR-1512 | MHC | Selawik | Jeff Luther | 2016-11-29 | 2016-11-29 | Emergency | $180 |  |  |  |  | No |  | Name: Ralph Ramoth Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [9 empty] | Frozen discharge line | Went to heat tape connection points, measured amps, verified heat tape was working in each box, verified glycol line was working for the sewer discharge line also, checked WTP & found that all 3 of his pressure tanks are leaking air, isolated the middle tank & kept the left & right one on, also saw that the valve wasn't working at the Island vacuum building's heat exchanger, cleaned it & got it to open, he had a heater that he thought was broken, took out the solenoid & manually kept the valve open with a screw & some washer to hold it open. All this was because the heat tape connection points weren't on AND the heated glycol line that runs in the sewer discharge line wasn't charged & heated, they do have 70-90 ft left to thaw out & I expect them to have it done today or within 2 days of this day(Nov 30). | 3 | order new tanks, order new hot box & pressure washer |  |  |  |  | pressure tanks | No |  | No |  | No |  | No |  | No | drain pressure tanks & change air bladder | Operator | [9 empty] | N/A | Other Documents | 2016-11-30 09:19
RMWTR-1513 | MHC | Selawik | Jeff Luther | 2016-12-01 | 2016-12-02 | Emergency | [5 empty] | No |  | Name: Ralph Ramoth Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [9 empty] | Assist operator thaw out sewer discharge line | Heat tape at the vacuum building was faulting, had it hooked up to 120volts, heat tape was melting extension cords & outlets, re-wired 240volts in it with 8gauge wire on a 30 amp breaker, before it would max out at 215ft on the 120volts, after the 240volts was wired in heat then traveled at 342ft, checked out some heaters they had & advised them to order solenoids & switches for the solenoids. Talked to operators about jetting the line, the night crew declined to cut pipe & put a jetter down, we were going to jet with the day crew the day after, but the line thawed out from the heaters, heat tape & heated glycol lines in the carrier pipe. | 4 | Community needs an adequate back up operator for when main operator leaves town |  |  |  |  | as listed before, pressure tanks needs new air bladders | No |  | No |  | No |  | No |  | No | order new bladders for the pressure tanks | Operator | [9 empty] | N/A | Other Documents | 2016-12-05 08:15
RMWTR-1514 | YKHC | Mekoryuk | Shane McIntyre | 2016-11-29 | 2016-11-29 | Routine | $604 | $0 | $0 | 0 | RAVN AIR | No |  | Name: Marka Peterson Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [9 empty] | Help trouble shoot the fuel delivery system on the back up generator for the water plant | I arrived in Mekoryuk at 10:00 am and met with Marka at the water plant. I took a tour of the water plant because that was my first time being out there. After that Marka led me to the generator in the garage. I asked Marka what was going on with the generator and he said that it would not start and will not run and that he had the village mechanic look at it but that they couldnt get it started. The first thing I went and checked was the fuel level in the fuel tank. after determining that there was enough fuel, I started to look for fuel in the filters, both filters were dry of fuel, I advised Marka that this could be the problem, fuel was not getting to the filters. After priming the filters with fresh fuel from a jerry jug, we tried getting the generator to start but it would not. Then I opened the top of the primary fuel filter and watched the fuel level go down after using the manual fuel pump priming lever on the mechanical fuel pump, I determined that the mechanical fuel pump works because when the lever was moved up and down, the fuel level in the filter went down but would stop after a few pumps. Next, I removed the access plate to the pulley for the fuel injection pump to inspect and see if the pulley was rotating with the engine turning over and it was. So then I loosened the fuel supply line to the injection pump to determine if fuel was getting delivered, fuel sprayed out after I cracked the line open and fuel flowed out when operating the manual fuel pump priming lever . Mark said that was more fuel than he and the village mechanic got to come out. Next I started to crack the fuel lines on the tops of the injectors to see if fuel was getting delivered to them, all we were getting was air bubbles, thinking we were getting fuel to push the air out, we continued this method only getting bubbles. The last thing I checked was the 12 volt solenoid on top of the fuel injection pump. Using the fluke meter, we were getting <1 volt when it should have been 12 volts. I disconnected the wires from the solenoid and replaced it with a 12 volt constant source. When the I hooked up the + and - wires the solenoid clicked like it should. So we then tried to bleed the injectors again with the solenoid getting a full 12 volts but still only got air bubbles at the fitting on the injectors. Telling me that there is a problem with the control board not giving 12 volts to the fuel shut off solenoid and that the seals on the fuel injection pump are leaking allowing air to slip by and not letting the fuel get delivered. | 6 | Control side of the backup generator is not supplying 12 volts to the fuel shut off solenoid on the fuel injection pump. | Air is leaking by the seals on the fuel injection pump causing only air to get pushed to the injectors instead of fuel |  |  |  | none | No |  | No |  | No |  | No |  | No | Get someone with more experience on the control side of the generator to diagnose the electical | Unknown | Re-move the fuel injection pump and send into Anchorage to be re-built and re-calibrated | [8 empty] | N/A | Other Documents | 2016-12-07 09:34
RMWTR-1515 | DEC | Anderson | Kevin Schoneman | 2016-11-30 | 2016-12-01 | Routine | [5 empty] | No |  | Name: Scott Thompson Title/Position: Wastewater Operator Accompanied By? No Telephonic Contact? No | Name: Dorothy Leake Title/Position: City Clerk Accompanied By? No Telephonic Contact? No | Name: John Collura Title/Position: Wastewater Operator Backup Accompanied By? No Telephonic Contact? No | [7 empty] | Routine visit and inspection of dosing stations. | I arrived at the airport at 0730 for the flight to Fairbanks, the flight left Anchorage at 1030 after a short weather delay. I arrived in Fairbanks at 1130 and picked up the rental car and headed to Anderson. I arrived in Anderson at 1345 the outside temperature was about -18, I met up with the operator Scott Thompson at the city maintenance shop. We discussed the dosing stations and the recent cold weather, Scott reported that the dosing stations appear to be working very well with only a couple of minor bugs. The dosing stations were brought into service on the 22nd of November. At that time the temperature in the area had started getting down to 0 and below. The water temperature in the wet well of the waste water lift station was 38 degrees Fahrenheit, from the operators years of pas experience the collection system was starting show effects of the declining temps, so the dosing station were brought on line. On the 24th of November after only two days the temperature in the wet well had risen to 42 degrees, after looking at the daily log sheets the lift station appears to be holding at about 40 degrees even with the prolonged sub-zero temperatures. The operator gave me a tour of the shop facilities and a run down on all of the maintenance equipment, we looked at the water truck they have set -up to supply warm water to both of the Mytana and the O’ Brien jetters as well as using the warm water to flush the lines when the need arises. The water truck is filled each day after any use and stored in a heated stall in the shop when it is not in use. Both of the operators have set-up a good monitoring system and daily checks list of various sections of the collection system, when they observe any ice build-up or reduction in velocity they either jet the line or manhole. After we looked over all of the equipment in warm storage we decided to take a look at the dosing stations. We started at the “Clinic” dosing station which doses the C Street 8” gravity sewer line. The dosing station blends 70% cold water @ 35 degrees and mixes it with 30% hot water @120 degrees at a rate of about .5 gallons per minute to achieve a target water temperature of about 60 degrees per cycle, each cycle occurs about every 2 hours. Each cycle of dosing the 60 degree water is discharged into a four inch clean-out which is connected to the 8” gravity main at the upstream end. For the most part the system operates very well and requires very little adjustments. Each day the operators check the water temperatures, blend ratios, flow rate and record the results. The flow rate does have to be adjusted on a regular basis most likely due to drift in the flow meters. Each syphon cycle adds 60 gals of tempered water into the sewer line. We then continued to the next dosing station which the operators refer to as “building #1”. This dosing station doses both D Street and E street. There does seem to be a problem with the exhaust fan in the station, the operator reported the breaker trips when the fan is turned on, this maybe just a lose connection. We then continued to building #2 dosing station, this dosing station ads tempered water to both F and G Street. There does seem to be a problem in this station with excess air in the system, it seems to occur after each well pump cycle. We determined that the pressure control tank may just need to have air added to the bladder. We then continued to the sewer system lift station which collects all of the influent waste water from the city and pumps it to the waste water lagoons. The lift station is in very good condition and show signs of constant care and upkeep. Each day the operators check both pump operations and log run times from the day before. By this time it was nearing the end of the operators shift and we headed back to the city shop. The next day I met Scott back at the city maintenance shop we discussed the implementation of a written preventative maintenance program, most of this information is already being collected on a daily basis. We also talked about certification testing in the upcoming year and the availability of some future training courses. We then decide to go through the dosing stations again and tour the collection system, dosing station number two required a slight adjustment to the both flow roto meters. We then toured the collection system and the waste water lagoons, while we were out Scott received a call from John who was out checking the system manholes and reported low flow velocity on Spruce Street. Scott asked John to go to the shop and pick up the Mytana jetter and we would meet him there, we met John at the manhole and jetted the line with warm water. We decided to continue to the remainder of the collection system and the waste water lagoons. The waste water lagoons consist of 3 cells, the Primary, Secondary and Percolation Cells. Wastewater is pumped first to the Primary Cell and begins the microbial process by settling out most of the suspended solids and break down of wastes, it continues to the Secondary Cell and continues the natural process of treatment and finally the treated water enters the Percolation Cell where the water is allowed to percolate into the ground. Scott received another report from John that he had noticed some frost in the line on Birch Street, Scott asked John to pick up the warm water tanker truck and we would meet him there. We met up with John at the end of the line on Birch Street and dumped approximately 3000 gallons of water in the last manhole on the line, there was no restriction in flow. We decide to stop by the city office and speak with the City Clerk, Dorothy Leake about the Preventative Maintenance Plan that Scott and I had talked about the day before, she was very happy to help with the gathering and submittal of information. It was the time for me to head back to Fairbanks for the flight back to Anchorage, I arrived back in Anchorage at 1800 | 4 | Back-up heat source for the dosing stations. In a the event of a prolonged power outage the plumbing may be at risk of freezing and damage. |  |  |  |  | Gas meter for each operator. | No |  | No |  | No |  | No |  | No | The air pressure should be checked on the pressure tank in Dosing Building #2. | Construction Project | Portable back up heat source for the dosing stations. | [8 empty] | Attachments | Other Documents | 2016-12-30 10:08
RMWTR-1516 | YKHC | Mtn. Village | Billy Westlock | 2016-11-29 | 2016-11-29 | Routine | $335 |  |  |  |  | No |  | Name: Ron Lawrence Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Charlie Long Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | [8 empty] | Assist with sanitary survey and also look over the system. | I arrived into mountain village and met with wpos Lawrence also Long where we were waiting for eho Michael Vicente to help complete sanitary survey. After a couple hours the sanitary survey completed to where we checked the system we know of one water break but waiting for excavator to be repaired. Over all everything was running normal. | 3 | None at this time |  |  |  |  | None at this time | No |  | No |  | No |  | No |  | No | Will keep in touch with excavator repairs | RMW | [9 empty] | N/A | Other Documents | 2016-12-11 15:16
RMWTR-1517 | YKHC | Bethel | Billy Westlock | 2016-11-29 | 2016-12-01 | Training/Meeting | $300 |  |  |  | Grant aviation | No |  | Name: All ykhc rmw's Title/Position: RMW Accompanied By? No Telephonic Contact? No | [9 empty] | Attend a meeting concernin all ov our villages that are in need of band aid projects. Talked about our clinics needing assistance from us needing assistance some issues from major work to least work. | I arrived into bethel on the nite of the 29th departed on the 1st of December. This meeting was concerning band aid projects in all of our communities from most urgent to least. Another part to this meeting was that we talked about all of our clinics from minor stuff to topics needing attention in our communities. | 0 | None at this time |  |  |  |  | None at this time. | No |  | No |  | No |  | No |  | No | None at this time | Unknown | [9 empty] | N/A | Other Documents | 2016-12-11 15:39
RMWTR-1518 | YKHC | Emmonak | Bob White | 2016-11-17 | 2016-11-18 | Emergency |  |  |  |  | Grant Aviation | No |  | Name: Brian Lefferts Title/Position: Other Accompanied By? Yes Telephonic Contact? No | Name: Allan Paukan Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Paul Dennis Title/Position: Electrician Accompanied By? Yes Telephonic Contact? No | Name: Mark Blake Title/Position: Carpenter Accompanied By? Yes Telephonic Contact? No | Name: Vigan Djelili Title/Position: Carpenter Accompanied By? Yes Telephonic Contact? No | Name: Aurthor Redfox Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Jaime Agwaik Title/Position: Water Operator Accompanied By? No Telephonic Contact? No |  |  |  | Make Emergancy repairs to fire damaged Vacuum Pump and building. | We departed Bethel with personnel lumber and pipe fittings we thought we would need to make repairs. When we arrived the city picked us up with a truck and moved us and our supplies to the water plant. Once we arrived at the plant I lined out the carpenters on how to brace up the fire damaged trusses while Allan worked with the operators on re plumbing the pump. The electrician started assessing the wiring and the controls. Allan was able to locate all the plumbing parts needed and rebuild the piping with the operators fairly easily so he then turned his attention to other things in the plant. The electrician determined we may be able to use the existing soft start so we tried to start it up but we had a fault that we could not clear. So we then removed the soft start and installed the VFD. Once we had the VFD installed it took some time to get it reprogrammed with the right parameters for the vacuum pump. With the ceiling braced up and the vacuum pump plumbed back in and wired the operators began bringing one branch of the system at a time. Once the whole system was on they sent out announcements by VHF to ask for any vacuum leaks to be reported immediately. They started to get reports right away and respond to each. The system was able to build vacuum but was unable to build enough to shut off so we closely watched the tempeture on the pump. The city brought in a night watch crew to keep track of the tempeture and manually give the pump rest periods. The next morning we installed a Vacuum gauge on the pump inlet piping and Jamie set up fans to blow across the cooling fins on the Vacuum pump greatly cooling the pump down. Allan and I worked with the operators to fine tune the treatment a little as we waited for the plane to arrive. | 16 | The hole in the ceiling is 10' by 10' and causing a lot of heat loss. |  |  |  |  | None at this time | No |  | No |  | No |  | No |  | No | Continue to watch the pump and respond to any vacuum leaks imediatly. | Operator | [9 empty] | N/A | Other Documents | 2016-12-12 10:31
RMWTR-1519 | DEC | Saxman | Steve Evavold | 2016-11-28 | 2016-12-01 | Routine | $675 | $210 |  |  |  | No |  | Name: Leona Haffner City Clerk/Admin Title/Position: Accompanied By? No Telephonic Contact? No | Name: Matthew Calves Water Plant Operator Title/Position: Accompanied By? No Telephonic Contact? No | Name: Ryan Orr City Maintenance/Op Title/Position: Accompanied By? No Telephonic Contact? No | Name: Tim Krug USDA State Architect Title/Position: Accompanied By? No Telephonic Contact? No | [6 empty] | A trip was scheduled to assist with inspection and pressure testing of a backup water source, familiarization with the water treatment process, and inspection of the septic tanks and wastewater collection system. | Arrived in Saxman and met with Matthew at the water plant. We discussed scope of the trip, water plant issues, and decided on a process to isolate and pressurize a temporary transmission line for the back up/alternate source. The drainage basin for primary source has been observed to have less runoff and supply needed for Saxman demand during periods of lower than normal precipitation. The reservoir has dropped to concerning levels several times in recent years. A second source, a tributary to the Saxman Creek, is being studied for a move. The Creek has almost twice the flow and provides for a better raw water quality, with less turbidity and organic color. A 850' 4-inch HDPE line was laid on ground surface from the plant up and over a slight rise and down into the creek. A foot(check) valve was added to the suction-end before submersion. The elevation drop of approximately 15 feet from the creek allows for siphonage of 20gpm of additional raw water to the plant. When full of water and isolated from the reservoir at the higher elevation, static pressure in the line is only 6.25 psi. DEC drinking water program requires a pressure test performed on the pipe before giving approval for use. When funded, a new dam and reservoir project will include a larger transmission pipe and be located 300' further up the slope of the basin from where the temporary pipe is located. Finished elevation would be close to that of the existing source at 230 feet. The floor elevation in the plant is 173 feet. The ANTHC designed water plant includes piping and valves for using a second source. Each can be isolated from the other. Matthew opened the valve for the reservoir and filled the 850' of 4-inch HDPE pipe. With that valve open, static pressure in the plant stabilized at 21.5 psi., as there is about 50 feet of head in elevation change. We walked the 850' length of the pipe and saw no leakage. There are a couple saddle clamps and spigots located at higher places in the line for air relief. I added a pressure gauge at the highest one and noted 16 psi. At 10 am, we decided increase the pressure for the test. Matthew isolated the 4-inch HDPE and pressurized the line slowly to 45 psi. Pressure noted at the high point was 33psi. At noon the pressure gauge was displaying 43.5 psi, and held that display until 2:30pm. The 4-inch HDPE was still isolated from the reservoir, and when Matthew relieved the pressure, the pressure dropped to the normal static display of 6.5 psi. I closed the valve again and Matthew pressurized the line up to 15 psi., and we left for the evening. There was no change in the morning. Matthew, Ryan, and I met with Leona Haffner, city administrator for introduction, and to discuss water plant operations, needs, and the current projects funded and/or being applied for. Sewer main replacement will start this spring and design for the new water source hopefully soon after. Tim Krug, State Architect with USDA Rural Development, arrived to discuss timelines and requirements for continued support. ANTHC progress and communications were commended. Matthew and I inspected the area scheduled for the sewer replacement project. He had concerns about the septic tanks and the amount of sludge still left after being pumped. ANTHC Engineer had brought up the same concerns and hired another service to do the work before the project starts. | 4 | Nothing noted at this time. |  |  |  |  | The automatic valve that closes the plant down at a high turbidity event has failed. Bray Valve, the manufacturer, has discontinued that model. Replacement is costly. The operator is manually operating the valve. | Yes |  | No |  | No |  | No |  | No | A trip may be scheduled to assist in flushing and/or rodding the sewer mains. Leak detection assistance was requested. | RMW | [9 empty] | Attachments | Other Documents | 2016-12-27 10:43
RMWTR-1520 | YKHC | Napaskiak | Bob White | 2016-11-29 | 2016-11-29 | Routine |  |  |  |  | Snow Machine | Yes | 15 miles | Name: Jack Wassile Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [9 empty] | Trouble shoot controls at the East water plant. | When I arrived the well was frozen so I showed Jack how to thaw the well and showed him were to install a electric heater to keep it from freezing. I then started working on trouble shooting the Timer in the control pannel. After some time working with out a complete wireing diagram we found a complete copy and we were able to reset the timer. I believe that the timer is not starting because of a bad switch in the fill valve. With the tanks filling and the pannel reset we called it a day. Jack will contact me to let me know if the timer worked correctly. | 6 | Boiler #2 still is issolated because of a faulty pressure relief valve. | The well piping froze under the floor. |  |  |  | Power outages are frequent and no back up power generator is available. | Yes | Boiler #2 pressure relief valve is leaking. | Yes |  | No |  | No |  | No | Replace boiler #2 PRV imediatly. | Community | Install heater under floor in well pipe chase and set to 40 F. | [8 empty] | N/A | Other Documents | 2016-12-12 10:25
RMWTR-1527 | YKHC | Quinhagak | Bob White | 2016-12-12 | 2016-12-19 | Routine |  |  |  |  | Raven Air | No |  | Name: Frank Jones Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Fannie Moore Title/Position: Other Accompanied By? No Telephonic Contact? No | [8 empty] | Replace tranducer and repair broken water lines. | When I arrived the boiler was out of fuel at the Water Treatment Plant. Frank said fuel was ordered and we headed to the Utility building to replace the tranducer. Once at the utility building I looked over the damage from the freeze and we decided to install the new tranducer directly on the pipe moving it away from the door and the cause of the freeze up. So we removed the old tranducer and tubing and I installed the new tranducer into the shut off valve.we then re routed the wiring to a junction box on the wall where we could splice the large building wire to the small sensor wire. Once we had the tranducer installed we climbed the Water tank and measured the water level then set the tranducer to the appropriate level. We then repaired the frozen copper lines by the door. Once everything was leak tested we looked over the rest of the system at the Utility Building. I then went to the Tribal office and talked with Fannie about the haul systems and the problems that they have had. She was generally pleased with the system and the amount of water she can use. I then looked over some freeze ups that frank was working on at homes with grinder pump stations. I then headed to talk with the home owners of each of the haul systems. They each talked about problems with the circ pump and i spent some time troubleshooting one of the water system and found it was frozzen. It was then time to depart back to Bethel. | 8 | The wind blowing under the door caused several pipes to freeze. | The circulation pump in the haul systems are all installed high then low water level in tank. | Several lines froze between the house and the grinder pump station because of reverse grade on the pipe. | Poor instalation of the heat trace tempeture bulb causes it to short cycle in the water tanks. |  | Reverse grade on grinder pump station. | Yes |  | No |  | No |  | No |  | No | Relevel gringer pump stations. | Community | Move Circulation pumps on haul systems. | Construction Project | Relocate heat trace control bulbs. | Construction Project | Replace door weather stripping in utility building. | Operator |  |  |  | N/A | Other Documents | 2016-12-19 16:11
RMWTR-1529 | YKHC | Chefornak | Bob White | 2016-12-16 | 2016-12-16 | Emergency |  |  |  |  | Yute Air | No |  | Name: Brian Lefferts Title/Position: Other Accompanied By? Yes Telephonic Contact? No | Name: Allan Paukan Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Jeff Beaty Title/Position: Project Superintendant Accompanied By? No Telephonic Contact? No | Name: Jeff Harris Title/Position: School Representative Accompanied By? Yes Telephonic Contact? No | [6 empty] | Inspect fire damage and plan temporary repairs. | When we arrived in Chefornak we were picked up by the water plant operator and taken to the burned out plant. It was easy to see the cause of the fire as it spread right from a failed electrical outlet. The smoke damage was extensive and sever. The fire consumed all the building wiring in the chase right above the outlet. The light were not functional in the plant and the only working electric was pressure, circulation and boiler pumps because the project ran temporary wires to keep them operational. The rewiring kept the whole water loop from freezing. We found that the auto vent on the unit heater had it's solder melted and it came out. We valved it off then we were able to build pressure up in the hydronic system. Several leaks were noted and a parts list was prepared for the repairs. We then made a list of electrical parts that will be needed to replace the breaker panel and all wiring. Jeff then showed us the new water plant that is almost complete and the Washeteria building. We picked up Jeff Harris at the school and headed back to the airport. | 0 | The fire destroyed all critical wiring in the building. | The quick actions of Jeff and the crew in Chefornak kept the building from being completely destroyed and the quick temporary wiring kept the whole system from freezing. | The new Water plant is with in days of being completed. |  |  | This building has to many deficencies to note in this format and should have been replaced years ago it has outlived its servisable life by years. | Yes |  | No |  | No |  | No |  | No | Return with parts from list and make temporary repairs that will be able to get through the cold weather until the new water plant is on line. | RMW | Complete the new water plant and bring it on line as soon as possible. | [8 empty] | N/A | Other Documents | 2016-12-21 07:29
RMWTR-1532 | DEC | Anchor Point | Kevin Schoneman | 2016-12-12 | 2016-12-15 | Routine |  |  |  |  | State Truck | No |  | Name: Floyd Murphy Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Niel Sullivan Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Wayne Flint Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: Sean Lee Title/Position: VSW Engineer Accompanied By? Yes Telephonic Contact? No | Name: Dorothy Flint Title/Position: Utility Clerk Accompanied By? No Telephonic Contact? No | [5 empty] | Site Visit, and meet with with the new operator. Participate in PER discussions. | RMW Floyd Murphy and myself departed Anchorage @ 0730 on the morning of Monday Dec.12. We arrived in Anchor Point that afternoon, Floyd called the new operator Neil Sullivan to let him know that we had made it. Neil arrived at the Water Treatment Plant a short time later Floyd and I introduced ourselves, Neil gave Floyd and I a short tour of the plant and showed us some of the items he had been working on since starting as the water operator. We were the joined by the back up operator Wayne Flint, Floyd and I introduced ourselves to Wayne. Roy showed us a short 1 inch brass nipple that he had replaced on the circulating loop from the water storage tank and the plant. He replaced the nipple with a schedule 80 nipple that he was able to purchase in Soldotna, the nipple appeared to show some sort of deterioration. We were then joined by Dorothy Flint the utility clerk, Floyd introduce Dorothy and I. We talked about the schedule for Neil and some possible training and testing. We talked about some of the concerns and questions they would like to talk about the next day. We all agreed to meet back at the water treatment plant the next morning, Floyd and I left and headed for Homer for the night. The next morning Floyd and I went to the Homer airport at 0730 to picked up VSW Engineer Sean Lee who arrived on the early morning flight from Anchorage, we all then headed back to Anchor Point. We arrived in Anchor Point @ 8:45, shortly after we arrived we were joined by first Neil and shortly after Dorothy. Wayne was unable to join us due to a prior commitment. Sean explained to the group the purpose of his trip, Sean told the group that he had recently began working on the Preliminary Engineering Report for Anchor Point and wanted to hear some of the concerns from the community. Dorothy and Neil both expressed that one topic that had been discussed was a" additional small filling hose" at the watering point. They also expressed that some expansion of the distribution system was of interest to the community. Neil, Floyd and Sean all left to tour the distribution system and look at some of the areas for future expansion, shortly after the group returned Floyd, Sean and I left Anchor Point for Ninilchick. | 2 | Alarm warning light for the on site septic tank shows a " high level condition". |  |  |  |  | None noted this trip. | No |  | No |  | No |  | No |  | No | Check the 4 inch sewer line to the septic tank, possibly use the camera to check for line separation. | RMW | [9 empty] | Attachments | Other Documents | 2017-02-06 11:12
RMWTR-1535 | TCC | Allakaket | Lee Meckel | 2016-12-21 | 2016-12-22 | Routine | [5 empty] | No |  | Name: Floyed Saunders Title/Position: Accompanied By? No Telephonic Contact? No | [9 empty] | Assist in trouble shooting of the heat trace panels. | I was contacted by the operator in Allakaket about the sewer main being frozen. Allakaket has an independent glycol loop that strips heat from the boilers in the washeteria via a heat exchanger and circulates from the washateria to the lagoon and back. The distance to the lagoon from the water plant is so great that this loop was designed to run by positive displacement gear pumps. The closed loop is connected to a glycol recharge station that is supposed to recharge any volume lost from the system. There is an electric heat trace back up system as well. The loop in question has a history of leaking and the recharge station doesn’t work. This greatly increases the chances of the pumps being damaged, because gear pumps will burn out if allowed to operate dry, or if allowed to pump against a frozen line. While Mr. Saunders had been out of town the glycol system was shut down by the backup operator. The temperature dropped well below -32 degrees Fahrenheit. Mr. Saunders and I with the assistance of Mr. Bergman looked at the electrical heat trace panels and adjusted the timers allowing the heat trace to run as desired. They warmed up and began to thaw the sections of frozen sewer line from the lift station to the lagoon. The heat trace was warm and doing its job. I checked on it later that night to make sure they were running. I checked again in the morning before I got on the plane and they had been running. | 8 | Allakaket is still having issues as of 12/9/16 with freezing of the sewage at the beginning of the sewer line where the lift station discharges in to the sewer force main. I have been working with Mr. Saunders to diagnose the issue and now have a plan to get out and replace that section of heat trace and thaw the one troubled section so that the community will no longer have to haul they’re waste via holding tank. |  |  |  |  | Heat Trace is no longer drawing the correct amps. | No |  | No |  | No |  | No |  | No | order new heat trace | Community | [9 empty] | N/A | Other Documents | 2017-01-03 10:09
RMWTR-1536 | TCC | Tetlin | Lee Meckel | 2016-11-30 | 2016-12-04 | Emergency | [5 empty] | No |  | Name: Mike Sam Title/Position: Accompanied By? No Telephonic Contact? No | [9 empty] | I received a call regarding boiler and freezing issues from the T.A. I was told that the boiler keeps shutting off after it runs for a while. | Upon arriving in to Tetlin I met with Mr. Wallace at the washeteria. Mr. Sam had to be out of town for work. As we entered the building it was noticeably cold. The mop bucket I passed on the way to the boilers was frozen. I looked at the boilers and checked the temperature, neither was up to temp. I also noticed that the pressure was low. I added water to the system through a hard plumbed cold water make up line. Boiler one fired up and began heating the water. Once the water was close to 190 degrees the pressure relief valve (PRV) on the back of the boiler popped and discharged hot water in to a large trash bucket that was put directly under the PRV. The pressure on the boiler was well below 30 psi at time of the PRV being activated. This typically happens once the PRV has reached above 30 psi and once it pops it needs to be replaced or it will leak at lower than designed temperatures/pressures. Boiler two wouldn’t start when it had a call for heat so I looked at the controls and noticed that the high limit had been set higher than the high heat cut off causing it to trip. I hit the reset on the high heat aquastat and adjusted it to be slightly higher than the high heat limit. Then the boiler fired up with no problem. I let it cycle twice and it did so without shutting off. Mr. Wallace had set up electric heaters throughout the building to help warm it up. We left for the evening. 12/1/2016 I had to pick up a few parts for the boilers and heating system from the hardware store in Tok which doesn’t open till 9:00 am. I picked up four auto relief vents for the heating loops and then I had to also grab an expansion tank for the hydronic heat to help with the pressure fluxing between high and low temps. The building was still cold but somewhat warmer than the night before. Mr. Wallace went around and changed some of the auto vents on the ¾” heating lines that ran to the heating resisters. Once that was done we were able to turn a few valves that had been shut off due to leaky auto vents and by doing so added another heating loop to the building. This heating loop controlled the heat in the hallway and the unit heater for the treatment side of the building. We looked at one of the heaters that was underperforming and when we pulled the cover off of the wall-recessed radiator we noticed that the valves had been throttled to the point they were almost closed. Once that was fixed boiler 2 began to run a lot more. I looked closer at boiler one and ran a flue gas combustion test. The test results were low in CO and efficiency. I looked closer and noticed that the fuel pressure was 50 psi to high. This is typically done when an undersized nozzle is used. I pulled the burner and the drawer assembly was wet and covered in soot. I scraped it off and checked the nozzle and it was the wrong size. I replaced the entire drawer assembly with a new one I had found in our office in Fairbanks. I also added the correct nozzle and adjusted the assembly to the correct length of the blast tube and she fired up. The flame inside the boiler looked much better and was burning cleaner. Once the burner was adjusted I played with the high and low limits to adjust the temperatures to have the boiler run a full cycle without popping the PRV. 12/2/2016 the next day I was able to focus on the frozen sewer main to the lagoon. The sewer was set up to trickle hot water in to the sewer main from a length of PEX tubing connected to the plant hot water through a backflow preventer. It had been running in the absence of the main water operator as a backup measure to prevent freezing. The hot water is produced through an indirect hot water heater. It uses the heat provided by the boiler to heat the treated water to 180 degrees. I believe that once the hot water was depleted the constant demand for the hot water led to the boilers running nonstop. This may not have been a problem for the boilers if the excess pressure in the system could have been vented out via auto vent and partially absorbed by the expansion tank. Without any way to relieve the constant high pressure the boilers got to hot and tripped one safety feature in the form of the high heat cut off and the other being the PRV. The hot water heater had been only 70 degrees by the time I had the boilers up and running. I shut it off so it could heat up. We then looked into the heat trace because someone had let me know that the breaker was tripping. I looked at it and tried to switch the breaker and it would not reset. I shut off the power to the main breaker and opened up the panel. I noticed that there was a matching spare breaker so I reconnected the power to it and tried start the heat trace. It didn’t work. I looked closer at the junction box that the power was being supplied to and traced the power up the bus bar to the breaker and found that someone had already moved the power to a different breaker and hadn’t labeled it correctly. It still didn’t work even thought it was getting power. 12/3/2016 Mr. Sam made it back to town the night before and began helping with the well and sewer thawing project. He showed me a brand new jetter that he had purchased and never used. We got it all set up and began to add water. The high pressure pump is gas powered and the hot water coil is heated by diesel. Once the water passed the high pressure pump and ran through the coil there was water dumping all over. The coil had leaks and was therefore unusable. We went back to using PEX tubing with hot water, and once we started depleting our water we noticed that it wasn’t filling back up. I looked at the well pump controls it was set to auto but nothing was flowing. I checked the well heat trace and it was dead. I found some unused heat trace and ran a whole new line to the well head and down the drop pipe while Mr. Wallace and Mr. Sam opened the well box and hooked up a space heater. We thawed the well and got back to thawing the sewer using half inch PEX and many couplers I had purchased in Tok. We started with 180 degree water and made great progress but quickly depleted our warm water and had to allow it to heat up again. To help with this I throttled the valve supplying the hot water to the pex so we could allow the hot water generator to keep up with the demand. We began to average about 120 degree water this way. Mr. Wallace, Mr. Sam and I began feeding the PEX to the frozen sewer outfall. It was a slow, long process. 12/4/2016 Mr. Sam left at 12:30 am while Mr. Wallace and I stayed taking shifts feeding the PEX down the sewer outfall pipe. I fell asleep for a few hours and Mr. Wallace woke me up at about 3:30am and brought me a hot plate of food. I took over for him and continued feeding the PEX. Around 8:30 am it finally broke through in to the lagoon. Mr. Wallace agreed to clean and put away the gear we had used, while I returned to Fairbanks. | 48 | Heat trace doesn't work any where along sewer line. |  |  |  |  | Sewer leaks | No |  | No |  | No |  | No |  | No | Repair all breaks. | Community | [9 empty] | N/A | Other Documents | 2017-01-03 10:45
RMWTR-1537 | TCC | Chalkyitsik | Lee Meckel | 2017-01-05 | 2017-01-06 | Emergency | [5 empty] | No |  | Name: Davis Carroll Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Tamara Henry Title/Position: Tribal Administrator Accompanied By? No Telephonic Contact? No | Name: Catlin Eagleshoot Title/Position: Other Accompanied By? No Telephonic Contact? No | [7 empty] | Assist community with ongoing frozen sewer line problem. | We arrived and assessed the lift station and sewer force main. We found that the section of sewer force main closest to the lagoon that had clean outs were thawed: largely in part due to the effort put forth by the local labor force before our arrival. We decided to start our thawing efforts at the beginning of the sewer force main. We found a point of entry to the arctic pipe at the beginning of the lift station. We used ½”pex pipe and plumbed it to the hot water generator with an adequate backflow prevention device and began to pump hot water into the clogged forced main. We made some progress that was soon interrupted by an impassable clog. We had depleted the hot water source so it was decided that we stop and allow the hot water generator to recharge. While waiting Mr. Shales used his skills as an electrician to diagnoses the integrity of the heat trace and made every attempt to get it back on line. He was able to succeed with one run of the heat trace, to do so required discovering why the motor starter in the heat trace control panel had been tripping out immediately after being energized. Mr. Shales informed us that a downstream section of heat trace had to be isolated and de-energized at an above ground splice box in order to utilize the undamaged section closest to the lift station. The following day we started preparing to use the hot water to flush out our blockage in the sewer main when I noticed that the temperature on the hot water generator was the same 90 degrees as when we had left the day before. I then noticed that the supply temp from the boiler to the hot water generator was same as the return temp from the hot water generator. This was due to low boiler psi and air in the hydronic line not being released. It was air locked so we added make up water / glycol mixture back to the boiler and opened an auto vent at the highest point in the hydronic heating line allowing the air to be purged form the system. We also found and replaced with a new auto vent because the old one had been isolated by a valve due to leaks. The domestic hot water began to heat up after our repairs to the hydronic heating lines. We continued our efforts at thawing out the sewer main. We got the pex through two of the 90’s leaving the washateria and possibly to the third where we began to see clumps of cloth and or mop strands as well as paper towel and baby wipes flowing out of the clean out. | 8 | We also made attempts to utilize the jetter that is in the shop. In our many attempts to get it to operate we could not get the water to discharge out of the high pressure pump. It did build pressure but would not discharge. I feel that successful trouble shooting of this device is the key to blowing out or cutting through the clog in the sewer main. |  |  |  |  | NO clean outs. Add clean out at the end of every 90 in the sewer force main this summer and if possible reroute lines to eliminate the excessive amount of 90’s and then pull new heat trace at the same time. | No |  | No |  | No |  | No |  | No | Add cleanouts or reroute sewer pipe to existing hanging arctic pipe under Washateria. | Operator | [9 empty] | N/A | Other Documents | 2017-03-07 10:35
RMWTR-1538 | TCC | Rampart | Lee Meckel | 2016-12-12 | 2016-12-14 | Emergency | [5 empty] | No | [11 empty] | Assist with troubleshooting and repairing the well and the sewer force main. | Rampart called to inform us they were having issues pumping water from the well and thought that there may be a bad pump. We did some trouble shooting over the phone , had the operator check the voltage and resistance to ground and between windings and all checked out, leading us to believe the drop pipe had a hole in it and the water was escaping, or the well transmission line was frozen. Once there, I was able to find a union to access the well transmission line inside the washeteria building. From there we were able add treated water in from the tank. We let the water sit for a couple minute and the water did not drain down the well drop pipe. We made sure there was no check valve keeping the water in the transmission line and there wasn’t. From here we were able to deduce that it was frozen between the pitless adapter and building transmission line. We rigged some garden hose with back flow prevention to ½” pex pipe and fed the pex side down until we hit the blockage. We turned on the hot water and melted the ice in a few minutes. We had water pumping that night and filled up the tank. The following morning we tried to run the facility plumbing and found that the building sewer pipe had a blockage and was backing up into the bathtubs. We found a cleanout about four feet away from the inlet to the lift station. We opened it up and noticed that it was liquid to that point and so we checked the inlet to the wet well and it had frosted shut. We were able to break up the frost and let everything drain. Once the building sewer was unclogged we attempted to pump the effluent up to the lagoon only to find that the force main had frozen again. We took a separate coil of pex and space heaters and began snaking the pex down the force main from the lagoon end. I had suspected a few spots on the force main that were above ground and poorly insulated. The pex tubing we were using has the linear footage marked on it so it’s easy to determine where we are above ground. The blockage was in one of the suspected above ground areas so we set our generator up to power our space heater and began adding heat. We build a small bubble to trap as much heat as we could. We would push the pex as far as we could once it warmed up and we eventually made it through one blockage only to find another fifty feet further down the force main. We moved all our gear to the spot in question and set it up and waited. It was just begging to turn dark outside and we decided to test the lift station pumps and to our relief it began moving the effluent to the lagoon as it was designed to do. | 16 | The well box needs to have the gravel pulled off of the transmission line around the pit less adapter and the well casing and make sure that the heat trace is attached at the point of connection between the two. |  |  |  |  | . It may not be a bad idea to construct an actual well house and move the watering point out to the main road this way no one drives over the water transmission line while accessing the fill station as this may lead to larger issues in the future. The sewer force main should be straightened out and have a few clean outs added, and additional insulation in the problematic areas. This would be a good spring or summer project. We accomplished a lot in my short visit and I would like to thank Mr. Wiehl and Mr. Newman for the help. | No |  | No |  | No |  | No |  | No | . It may not be a bad idea to construct an actual well house and move the watering point out to the main road this way no one drives over the water transmission line while accessing the fill station as this may lead to larger issues in the future. The sewer force main should be straightened out and have a few clean outs added, and additional insulation in the problematic areas. This would be a good spring or summer project. We accomplished a lot in my short visit and I would like to thank Mr. Wiehl and Mr. Newman for the help. | RMW | [9 empty] | N/A | Other Documents | 2017-01-03 10:56
RMWTR-1539 | YKHC | Napakiak | Bob White | 2016-12-21 | 2016-12-21 | Routine |  |  |  |  | YKHC Truck | No |  | Name: Leo Kuskyuk Title/Position: City Administrator Accompanied By? No Telephonic Contact? No | Name: Greg Aluskuk Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Alysa Gustufson Title/Position: Environmental Health Officer Accompanied By? No Telephonic Contact? No | [7 empty] | Install boiler setbacks and tiger loops. | When i arrived I talked with Leo about how things were going at the Washeteria while i waited for Greg to come in. When Greg arrived we started right in on the boilers. He started on boiler #1 taking off the fuel line while I started on Boiler #2 wiring in the boiler set back. Once I had both Boiler controls wired in I started programing them. While they have the same model it has two different versions of software so it took longer than it should to program correctly. Meanwhile Greg had removed both boiler fuel line and installed the bypass plugs. So I then helped him finish up the installation of the tiger loops. Once we finished installing the tiger loops we test fired the boilers and they fired right up and ran automatically bleeding them selves. I then instructed Greg on how the boiler setback worked and what to do if he had problems with it. | 4 | The Intellidyne boiler economiser had two different software installed even though they were the same model |  |  |  |  | The dryer piping is two small on the double dryers and they do not get hot enough. | Yes |  | No |  | No |  | No |  | No | Order Piping and install new supply and return lines on the dryers. | Community | [9 empty] | N/A | Other Documents | 2017-01-03 14:10
RMWTR-1540 | TCC | Circle | Wes Shales | 2016-10-04 | 2017-01-05 | Emergency | [5 empty] | No |  | Name: Fred Kameroff Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Brian Bearden Title/Position: Environmental Health Officer Accompanied By? Yes Telephonic Contact? No | Name: Lawrence Crow Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Dennis Carroll Title/Position: Construction Staff Accompanied By? No Telephonic Contact? No | Name: Dave Masephol Title/Position: Electrician Accompanied By? No Telephonic Contact? No | Name: Jessica Fields Title/Position: Tribal President Accompanied By? No Telephonic Contact? No |  |  |  |  | Troubleshoot then fix reason for no flow from well pump to water plant. | As we narrowed down the root cause of the situation we ruled out control issues at the water plant. An excessive amp draw from the well pump indicated problems were most likely originating from the well pump itself. An extreme amount of corrosion and rust at the electrical connections at the well casing were discovered. Ultimately the well pump and a short section of drop pipe were replaced after pulling the old pump. Fortunately the spare well pump we brought with us was a compatible replacement. Waterproof electrical connections were made up for the new pump, I threaded a short section of drop pipe thanks to some local assistance in providing me with a pipe threader and vise. We replaced the safety cable to the pump thanks to more locally obtained material. After installation the new pump performed flawlessly while we remained on site. A problem with the delivery of chlorine into the system was corrected at the Plant then we departed for Fairbanks. | 10 | None |  |  |  |  | No comment. | No |  | No |  | No |  | No |  | No | Circle is Fred Kameroff’s RMW community and he will continue to work with them on their needs. The water collection and treatment/storage infrastructure at Circle is in need of some serious upgrade or replacement | RMW | [9 empty] | N/A | Other Documents | 2017-01-03 14:33
RMWTR-1541 | TCC | Circle | Wes Shales | 2016-10-07 | 2016-10-07 | Emergency | [5 empty] | No |  | Name: Brian Bearden Title/Position: Design Engineer Accompanied By? Yes Telephonic Contact? No | Name: Lawrence Crow Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [8 empty] | Troubleshoot and correct automatic well pump operation that had failed. | Responding to the situation we verified the tank floats were working properly then swapped out a series of float control relays which did not change the situation. Adjusting the time delay relay to zero corrected the automatic operation of the well pump within the well pump control. Brian said he recalled seeing it set to zero earlier in the week and it was unknown to me why it was different. Anyway, observation of the plant was maintained for an hour or so and it has continued to operate correctly since then, word is. | 0 | No comment. |  |  |  |  | No comment. | No |  | No |  | No |  | No |  | No | It’s always a good feeling to successfully end a trip with a positive outcome. | Operator | [9 empty] | N/A | Other Documents | 2017-01-03 14:39
RMWTR-1542 | TCC | Minto | Wes Shales | 2016-10-18 | 2017-01-19 | Routine | [5 empty] | No |  | Name: Jeremy Charlie Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Franklin Silas Title/Position: Tribal Council Member Accompanied By? No Telephonic Contact? No | [8 empty] | Determine if two used pressure pumps are in working condition and possibly install one, and replace a village loop circ pump. In addition, supply the community with information on possible options for treating their water hardness/water quality issues/concerns. | The used pressure pumps were tested and were found to be no good. We got the new village loop circ pump installed and it performed flawlessly. We observed it in operation and found no problems. I supplied Jeremy and Franklin with information on hard water treatment processes. Franklin approached Jeremy and requested info from me on the possible solutions to the community problem. I offered info on softening methods using lime and soda ash in the conventional treatment processes as well as Ion exchange processes for individual (residential/lite commercial) treatment. | 8 | None |  |  |  |  | None | No |  | No |  | No |  | No |  | No | I am going to assist Minto in getting a replacement pressure pump. As for the water softening concerns/needs of the community I presented Jeremy and Franklin with a community wide treatment option as well as an individual option. I indicated that the water treatment plant would need to be upgraded/have a good treatment/filtration system installed. I told them that this situation would best be addressed with the help of others at TCC, ANTHC, VSW, and or DEC. Presently Minto only adds chlorine to their ground water. The community has had an area wide long ongoing problem with pipe scale build up that has caused numerous mechanical issues with boilers, etc. and various plumbing fixtures/components. | Community | [9 empty] | N/A | Other Documents | 2017-01-03 14:57
RMWTR-1543 | TCC | Birch Creek | Wes Shales | 2016-10-31 | 2016-11-01 | Emergency | [5 empty] | No |  | Name: Fred Kameroff Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Walter Williams Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Vincent Williams Title/Position: Local Laborer Accompanied By? No Telephonic Contact? No | Name: William James Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: Lawrence James Title/Position: Other Accompanied By? No Telephonic Contact? No | Name: Jackie Baalam Title/Position: Tribal President Accompanied By? No Telephonic Contact? No |  |  |  |  | Diagnose and correct no water flow from well pump. | Upon arrival in Birch Creek we got an overview of the water distribution and filtration/treatment systems. Following our trip objective we proceeded to take voltage and amp readings at the plant. Those readings were all normal for voltage, amp draw, and well pump testing procedures for testing if the motor is grounded as well as the windings resistance. All valves at the plant were in there appropriate positions. Next we observed the situation at the well pump house during a call for water. A small but noticeable thud occurred from below ground level from within the well casing. The well house was heated and in addition a heat loop was active from within the arctic piping to the water treatment building. What stood out in the situation was an electric heat trace the was not terminated to a power source that originated from within the well casing and protruded to just outside of the sanitary seal. A water proof splice with a 120 volt power cord was terminated to provide power to the heat trace that was tested for electrical integrity first. An amp draw reading conducted on the live power at the heat trace was normal. Twelve hours later the next morning at 8 a.m. the water treatment plant was receiving water from the well pump again. A small excavation on the river side of the well pump house that allowed for some shoring up of the transition to the floor of the well house as well as further insulation of the area was covered up with dirt by William James. It was theorized that the opened up area had allowed colder air to penetrate around the piping that flows down to and underneath the river. That portion of the piping had never froze before. Fred provided assistance and advice the next day with Vincent and Walter on Thursday while they maintenanced the water treatment plant. We also observed the water treatment plant operations/ well pump performance. | 4 | None |  |  |  |  | None | No |  | No |  | No |  | No |  | No | The well house should continue to be checked every day and normal routines continued to be observed at the plant. Birch Creek does an excellent job of maintaining what they got and are making every effort they can including attending training to keep up with maintaining their plant. | Community | [9 empty] | N/A | Other Documents | 2017-01-03 15:05
RMWTR-1544 | TCC | Northway | Wes Shales | 2016-11-02 | 2016-11-03 | Routine | [5 empty] | No |  | Name: Lee Meckel Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Terry Albert Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Carl Carbon Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | [7 empty] | Perform boiler combustion tests/tune ups and get an overview/consult on operator concerns with the water treatment and storage as well as address sanitary survey highlights. | At Northway we spoke with Terry and Carl about the planning for and installation of a grit separator they had recently purchased to replace an in-line cleanout. We discussed the need for connectors they would need as well as the piping “method” they would use for installation. Next we worked with them on planning the parts order and installation of a flanged connector/penetration to the water storage tank located inside the plant. In addition we discussed the need for further securing a portion of the tank lid better and replacing the aged float valve inside of the tank. Efforts were made to locate necessary piping and parts from their inventory but were not completely successful. Next boiler combustion analysis was performed on the water treatment/washeteria boilers as well as the water tanker/pumper building boilers. We also planned out the replacement of a double check valve on the tanker fill piping that had been removed after freeze damage had occurred. We climbed the outside water storage tank and spoke about the need to install locks on the access to that. Another reason for climbing the tank was to view the top of the shop building and we verified that a china cap for the boiler exhaust was missing. Signs of excessive water entering into the boiler exhaust was evident during the boiler analysis. Also, Terry asked for advice on what to do about increasing the chlorine residual with the water stored in the tanks. His smaller sized/aged injection pump that he recently ordered a replacement for was maxed out on the speed and stroke settings. Cleaning and maintenance of the pump produced no benefits. We quickly offered the advice that he could increase the chlorine percentage solution. In addition, methods of preventing freeze up of a p-trap were discussed with Terry and Carl. Lee also spoke with them about preventative maintenance routines and the best practices score. | 2 | None |  |  |  |  | None | No |  | No |  | No |  | No |  | No | Northway is one of Lee’s RMW communities and he is going to assist them in ordering parts and material for the different areas we looked at. Lee will provide them with further assistance when installation of the replacement parts occurs. | RMW | [9 empty] | N/A | Other Documents | 2017-01-03 15:48
RMWTR-1545 | TCC | Tetlin | Wes Shales | 2016-11-03 | 2016-11-03 | Routine | [5 empty] | No |  | Name: Lee Meckel Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Michael Sam Title/Position: Tribal Council Member Accompanied By? No Telephonic Contact? No | Name: Kristie Charlie Title/Position: Tribal Administrator Accompanied By? No Telephonic Contact? No | [7 empty] | Follow up on recently performed work to address sanitary survey findings. This was a "pass thru" type trip since we were on the road system and within the community boundaries. | We spoke with Michael and Kristie at the Tetlin Tribal Office then went and saw the exceptional carpentry and insulation work that the Tetlin crew had built as a housing and transition for/from the well casing to washeteria. | 0 | None |  |  |  |  | None | No |  | No |  | No |  | No |  | No | Although this was a quick visit and more of a professional courtesy we verified that the work we and the Tetlin crew had completed earlier was doing fine. | RMW | [9 empty] | N/A | Other Documents | 2017-01-03 15:55
RMWTR-1546 | TCC | Beaver | Wes Shales | 2016-11-14 | 2016-11-15 | Emergency | [5 empty] | No |  | Name: Aaron Petruska Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: Paul Petruska Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Wilma Pitka Title/Position: Tribal Administrator Accompanied By? No Telephonic Contact? No | [7 empty] | Fully diagnose and repair inoperable water/sewer haul truck hydraulics. | A few days prior to my departure to Beaver I sent out a 5 gallon bucket of hydraulic/PTO fluid. Previously Aaron had phoned me stating that the vacuum pump system on the haul truck was failing. The truck uses separate interchangeable skids to either pump septic or deliver water. Upon arrival it was determined that the level guage was incorrectly read and that a not fully compatible fluid was being used for the situation. The truck has a holding tank and PTO driven system for operating the two separate motors on the different skids. A hydraulic driven vacuum pump motor on the sewer vac skid was not working correctly and tended to leak the “hydraulic” fluid out. The pump for that motor had its own separate reservoir for a hydraulic type fluid and that was full. A serviceable vacuum system breather filter was fully cleaned and sanitized and reinstalled on the sewer vac skid. We called up a vendor the next day and cancelled an expensive breather filter that Aaron had ordered but that was not needed. We did order some hydraulic filters tho. The reservoir holding tank on the truck was filled up with a full five gallons of PTO/Hydraulic fluid. In addition, the vac truck had two separate sections of hose replaced that were the cause for vacuum pressure leakage. The hoses jumpered between different components of the vacuum system. When the vac truck was finally checked for proper operation Aaron stated that the vacuum pump sounded “much more healthier”. Also no fluid leaks were occurring any longer at valves or other connection points. The viscosity and volume as well as other properties of the more compatible hydraulic fluid were allowing the system to work as designed. The next day tanks within the community were pumped and water was delivered. Also while I was in Beaver I terminated a circuit to a unit heater in the garage bay the haul truck was stored in. For whatever reason at some point the power to the unit heater had been disconnected at a junction box nearby it. Pre and post electrical checks were done on the circuit prior to calling the job done. In addition, info was taken down on pumps Paul and Aaron wanted to order backups for at the water plant. Also, we looked at what it would take to start using the heat exchanger again that pre heats water before treatment/filtration at the water plant. | 8 | None |  |  |  |  | None | No |  | No |  | No |  | No |  | No | Aaron will continue to use the more proper fluid for the situation with the haul truck and is looking toward the spring time to repair another haul truck that has had some mechanical issues in the past so has not been used for a couple of years or more. Also we will follow up on other areas we addressed while I was there at a later date. | RMW | [9 empty] | N/A | Other Documents | 2017-01-03 16:01
RMWTR-1547 | YKHC | Alakanuk | Billy Westlock | 2016-12-12 | 2017-01-03 | Emergency | $207 |  |  |  | Personal snogo | Yes | 200 miles | Name: Cyprian Augline Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Ijohn Augline Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: Kevin Joseph Title/Position: Other Accompanied By? No Telephonic Contact? No | [7 empty] | I received a call on the week of December 6th that some of the residence of Alakanuk weren't getting water, but I didn't think that the water mains were freezing. | Before I got to alakanuk the operators did some tests on the circulating water going down town, and noticed that even the flow indicator was moving constantly it was only circulating inside the plant, due to a bad check valve for the fire protection. The crew started to jet the water mains to where the last house was getting water, I calculated that there was 1.8 miles of frozen water main that needed to be thawed. When I arrived I noticed that there was no heat circulating in the building, so while the crew was thawing water main I started to figure out why there was no heat going through the building. In the days before the freeze up there has been multiple brown outs causing the panels to trip out, causing the contacts to trip, also causing them to give out or break until they get a new contact. Anyways I went thru every panel and started to get the heat going through the glycol, and also the water heat exchangers. Witherspoon the help of Kevin Joseph we got all heat going. The next few days we jetted in good weather and bad, we finally got the water mains going down town to circulate and is now back to normal. | 8 | Need to keep an eye on the number of brown outs and also watch the check valve to keep it closed until another check valve is there to replace the bad one. |  |  |  |  | Brown outs need attention check the plant every time a brown out occurs. | No |  | No |  | No |  | No |  | No | I will call to make sure the check valve is still shut off until the city of alakanuk could get another. | RMW | [9 empty] | N/A | Other Documents | 2017-01-05 09:30
RMWTR-1548 | YKHC | Holy Cross | Bruce Werba | 2016-07-05 | 2016-07-08 | Other | $0 | $0 |  |  | Personal Vehicle | Yes | 10 miles | Name: Steve Suitton Title/Position: ANTHC Engineer Accompanied By? Yes Telephonic Contact? No | Name: David Walker Title/Position: Water Operator Accompanied By? Yes Telephonic Contact? No | Name: Leo Peters Title/Position: Accompanied By? Yes Telephonic Contact? No | [7 empty] | To finish upgrade in water treatment plan t to the treatment train. | I assisted the WPO with completing an upgrade to the water treatment plumbing train that was began by ARUC. The project was placed on hold due to the fourth of July holiday and lack of material. After the 4th of July the materials arrived onsite, the WPO asked if we could complete the upgrade to the water plant. The parts that arrived were to finish off loops two and three. It took three days to complete the CPVC pipe, full port valves installation for loops two and three. Also a new buttertfly valve was installed for the water storage tank isolation. With a solid week of work in, all the necessary components for WDS operation was now complete without prolonged shut down of distribution loops. | 30 | Items were addressed with this plant upgrade. |  |  |  |  | A water meter was being waited on for installation to complete upgrades. The meter was installed not long after, a trip report will be submitted. | No |  | No |  | No |  | No |  | No | Wait on water meter for west loop upgrade. | Engineer | [9 empty] | N/A | Other Documents | 2017-01-05 12:01
RMWTR-1549 | YKHC | Holy Cross | Bruce Werba | 2016-07-14 | 2016-07-14 | Routine | $0 |  |  |  |  | Yes | 2 miles | Name: David Walker Title/Position: Water Operator Accompanied By? Yes Telephonic Contact? No | Name: Leo Peters Title/Position: Water Operator Backup Accompanied By? Yes Telephonic Contact? No | [8 empty] | Diagnose automated well pump controls that is malfunctioning. | With the weather continually raining a short developed in the wiring for the water storage tank (WST) control system. The line is 4500 feet long. This problem also occurred this spring. We went to the location where the previous problem occurred. Once the wire was exposed we ohmed the line between previous break to the water tank, that tested okay. We now knew it was from the exposed section to the water plant, which was about 2200 feet. After opening up the jackets and exposing the wire in a few places, we were still unable to locate the problem for the water storage tank float control system. With the problem lying in a bad location, further consultation with Village Engineer and ARUC Electrician is needed to help rectify the situation. After making arrangements with ANTHC Engineer we will repair bad well pump float control wiring to the water storage tank. | 6 | WPO will monitor the level of the water storage tank and operate well pump as needed. |  |  |  |  | After the rain quit, 5-7 days later the electrical short went away and operated as designed until we reapired the problem. | Yes |  | No |  | No |  | No |  | No | ARUC Engineer and RMW will talk on how to address the problem with the well pump control system. THe following day a few different options were spoke about. The ARUC Electricain will be flying out at a later date. | Engineer | [9 empty] | N/A | Other Documents | 2017-01-05 12:29
RMWTR-1550 | YKHC | Holy Cross | Bruce Werba | 2016-08-02 | 2016-08-05 | Other | $0 |  |  |  |  | Yes | 8 miles | Name: Steve Sutton Title/Position: ANTHC Engineer Accompanied By? Yes Telephonic Contact? No | Name: David Walker Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Leo Peters Title/Position: Water Operator Backup Accompanied By? Yes Telephonic Contact? No | [7 empty] | Install 3" water meter for west loop. | After finally receiving water meter that took 5 weeks to get onsite, we were able to complete all upgrades to loop two, loop three and west loop. The only thing left was to hook up the loop heat add for the west loop, of which the WPO will complete. With the installation of the meter this concluded all upgrades to the water plant plumbing train. | 30 | Only the heat exchangers to reconnect to ports already installed by the WPO. |  |  |  |  | None at this time. | No |  | No |  | No |  | No |  | No | Make sure WPO connects heat add for water distribution loops. | Operator | [9 empty] | N/A | Other Documents | 2017-01-05 12:45
RMWTR-1551 | YKHC | Holy Cross | Bruce Werba | 2016-08-22 | 2016-08-23 | Routine | $0 |  |  |  |  | Yes | 4 miles | Name: Steve Sutton Title/Position: ANTHC Engineer Accompanied By? Yes Telephonic Contact? No | Name: Kolt Garvey Title/Position: Accompanied By? Yes Telephonic Contact? No | Name: Andrea Moreno Title/Position: Other Accompanied By? Yes Telephonic Contact? No | Name: David Walker Title/Position: Water Operator Accompanied By? Yes Telephonic Contact? No | [6 empty] | Troubleshoot the well pump control wiring with ANTHC Engineer and Electrician. | The two days were spent with the ANTHC Engineers and Electrician troubleshooting the float control wiring. We tested from about halfway between previous line exposure and the wst, that tested okay. Our problem still lies between the last hole and the water plant, which is about 1100 feet away from the water plant. At the end, we found that it would be better to reevaluate the situation from a management aspect. The best option to get the problem resolved is to replace the entire wiring to the water tank or use radio communication. Of which a decision will be made during the upcoming year. | 10 | The well pump control wiring problem still has to be corrected. |  |  |  |  | none at this time. | Yes |  | No |  | No |  | No |  | No | Check with ANTHC Engineer for course of action required to fix problem with the float controls. | Engineer | [9 empty] | N/A | Other Documents | 2017-01-05 14:03
RMWTR-1552 | YKHC | Shageluk | Bruce Werba | 2016-08-24 | 2016-08-24 | Routine | $136 | $0 |  |  | Skiff | Yes | 134 miles | Name: John Hamilton Title/Position: Water Operator Accompanied By? Yes Telephonic Contact? No | [9 empty] | To complete a material take off list for upgrade to water distribution system (WDS) between the water plant, city building and clinic. | After years of freeze up problems on the WDS between the water plant, city building and the clinic we had enough funds and man power to change the current design of the wds. We went from past practice to a more current design to get rid of the freeze up problem that occurred when it got cold. We made an arctic box outside the city building and brought the piping from under the building to inside. It then went into the ceiling of city building and thru arctic pipe to the clinic. Once the route was found we made a materials list for future installation. I departed after all was done by my skiff to Holy Cross. | 4 | Make sure the materials are ordered before winter arrives, so the upgrade to the wds can be replaced. |  |  |  |  | None at this time. | No |  | No |  | No |  | No |  | No | Have the WPO call if any problems procuring parts and materials. | Operator | [9 empty] | N/A | Other Documents | 2017-01-05 14:27
RMWTR-1553 | YKHC | Grayling | Bruce Werba | 2016-08-31 | 2016-08-31 | Training/Meeting | $1,100 |  |  |  | Ak Scenic Air | No |  | Name: Will Kemp Title/Position: Consulting Engineer Accompanied By? Yes Telephonic Contact? No | Name: Brandan Sambei Title/Position: Water Operator Accompanied By? Yes Telephonic Contact? No | [8 empty] | To complete a Preliminary Engineering Report with consulting engineer and WPO. | After arriving into Grayling the WPO met us at the city office. We then went to the water plant where we started to inspect the water utility and then the wastewater utility. We inspected both utilities for any operational problems or infrastructure that needs upgrades to keep utility functioning as designed. With all completed we took a late evening charter that droppped me off in Holy Cross and continued on to Aniak with engineer. | 6 | North lift station is having problems with control panels, pump rails are nonfunctional any more, the wastewater is deteriorating the metal, as the building is 30 years old. | Manhole covers are not buried deep enough, the grader operator is knocking the lid or cement cover off the top and causing rocks and debris to enter the wastewater collection system. This is causing the sewer lines to clog, most of all, the lift station pumps are getting gravel and rocks and at worst case is frying the motor. |  |  |  | Manhole lids and covers need to be buried under roads to prevent the heavy equipment operator from being the water and wastewater utilities operators worst enemy. | Yes |  | No |  | No |  | No |  | No | After talking with Engineer Kemp we will wait for the recommendation from the PER. | Engineer | [9 empty] | N/A | Other Documents | 2017-01-05 15:04
RMWTR-1554 | YKHC | Shageluk | Bruce Werba | 2016-10-12 | 2016-10-12 | Routine | $193 |  |  |  | Skiff | No | 134 miles | Name: John Hamilton Title/Position: Water Operator Accompanied By? Yes Telephonic Contact? No | [9 empty] | Conduct well pump pressure tank maintenance. | At the request of the water plant operator i departed to Shageluk by my skiff. Once into Shageluk i met up with WPO at the water plant. We began by inspecting the six 302 well extrol tanks. All were at different levels of being air logged. The first task was to shut well off and then drain tanks. After tanks were drained we pumped the bladder with air till 20 psi was achieved. We then tested the well by turning pump on, the well pump shut off at 34 psi, before they were continually running. With all tasks performed I departed for home at five thirty. I arrived home at seven thirty P.M. | 6 | None at this time. |  |  |  |  | None at this time. | No |  | No |  | No |  | No |  | No | None at this time. | Unknown | [9 empty] | N/A | Other Documents | 2017-01-06 12:20
RMWTR-1555 | YKHC | Shageluk | Bruce Werba | 2016-10-24 | 2016-10-27 | Emergency | $500 |  |  |  | Ak Scenic Air | No |  | Name: John Hamilton Title/Position: Water Operator Accompanied By? Yes Telephonic Contact? No | [9 empty] | To complete Water Distribution System (WDS) upgraqde/ repair to city building line and the clinic line. Disinfect well because fecal coliform was found on last monthly bac-t test. | With the weather being bad a trip was finally made on 24th of Oct. Our first task was to super chlorinate the well. We made five gallon cantainer vat to mix chlorine and dump down the well casing. We let it sit for two hours and pumped it out in hopes of killing the fecal coliform and bacteria that was giving the well a positive sample. Before leaving we left high concentration of chlorine in all the treatment and distribution system piping. We called it an evening at 2030 hours. Oct 25 We started the day by flushing high concentration of chlorine in all the piping system. We then got four repeat samples from the system; raw water sample, and three from the distribution system, and then shipped it out on the next available plane. The next was to check on materials that arrived; knowing that most parts were onsite we began to replace the water distribution at the city building and clinic. After a hard day, the inside work for both buildings were complete, the following day the tie in will be completed. Oct 26 The tie in to both buildings were completed by 2030 hours. We called it a day shortly after. Oct 27 Today we completed the last of the water distribution by completing the arctic boxes for both buildings. With all tasks completed I departed home before dark. | 31 | Weather permitting; we will know the result of the bac-tee test by end of the week. Hopefully all the fecal coliform is gone. |  |  |  |  | None at this time. | No |  | No |  | No |  | No |  | No | Follow up on results of coliform repat testing that was conducted while i was onsite. | Other | [9 empty] | N/A | Other Documents | 2017-01-06 12:58
RMWTR-1556 | YKHC | Stony River | Bruce Werba | 2016-10-31 | 2016-11-02 | Emergency | [5 empty] | No | [11 empty] | To assist the city wastewater workers with desludging the septic system. | Oct 31 Today after arriving we examined the situation with the septic system. Our first task was to make a trench for the sludge to be disposed of at solid waste landfill. It took all day to make a trench 75 feet long by 6 feet deep. Nov 1 Today we began by doing the clinic septic field, next was Mary Willis, the old clinic septic tank and one load out Andrew Gusty, with every five hundred gallons of sludge pumped out we added a half a bag of lime. With the evening getting late we started to wash all equipment used to desludge septic tanks. We then started the winterization and securing process. With it being late we called it a day at 2230 hours. Nov 2 We began by securing equipment and vehicles into container vans. One last task was to be peformed and that was covering the solid waste site pit privy. Once all tasks were completed I departed for home with Ak. Scenic Air | 24 | Andrew Gusty and Mary Willis will need to be desludged next spring. |  |  |  |  | The community will need to look to purchase container vans to secure vehicles and prevent vandalization. | Yes |  | No |  | No |  | No |  | No | Nonbe at this time. | Other | [9 empty] | N/A | Other Documents | 2017-01-06 13:36
RMWTR-1557 | YKHC | Shageluk | Bruce Werba | 2016-11-03 | 2016-11-04 | Emergency | $840 |  |  |  | Ak Scenic Air | No |  | Name: John Hamilton Title/Position: Water Operator Accompanied By? Yes Telephonic Contact? No | [9 empty] | Complete the well disinfection process that was started Oct 24, 2016. | Nov 3 We started by making superchlorine vat, by dumping 2.5 gallons of chlorine to top, then powder chlorine was dumped to well casing. We then made a our pumping system with a transfer pump and hoses that stretched to the bottom of the well casing. This would allow circulation of the well for an hour and half. We let it sit overnight and called it a day. Nov 4 We began by flushing the well of high chlorine, the end reading was 2.5 ppm. We pumped some of the high chlorine residualed waster into the water plant plumbing. We flushed the system out again and are ready to send samples monday down to the Bethel OEHE Water Lab. With tasks completed I departed for Holy Cross on Ak Scenic Air. | 12 | Wait on more repeat samples that will be sent to Bethel water lab on Monday. |  |  |  |  | Repeat water saples will be sent the following monday. | No |  | No |  | No |  | No |  | No | Call OEHE bethel office to find out bact results. | Other | [9 empty] | N/A | Other Documents | 2017-01-06 13:55
RMWTR-1558 | YKHC | Kasigluk | Bob White | 2017-01-09 | 2017-01-09 | Routine | $390 |  |  |  | Raven Air | No |  | Name: Nickfer Nicholas Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [9 empty] | Install water meter at School. Troubleshoot Waste heat. | When I arrived we started to assemble the meter. Once we had it all prepped we went to the school and found it was not going to work as we prepared it so we gathered parts to reconfigure it for installation. Once installation was complete we tested it for leaks and flow with everything working as it should we departed back to the water plant. We then looked at the Waste heat at the AVEC connection and found our pressure gauge was not accurate enough to measure how low we were going to drop the pressure and with out any glycol to refill it we were unable to make any adjustments to the system. I then called for a pick up to return me to Bethel | 5 | AVEC has borrowed all of the villages Glycol and they need to get some shipped in so we can fix the Waste Heat. |  |  |  |  | The waste heat is only operational some of the time. | Yes |  | No |  | No |  | No |  | No | AVEC needs to order Glycol and return borrowed glycol. | Other | Utility Manager create new form that includes the School meter readings. | [8 empty] | N/A | Other Documents | 2017-01-09 16:41
RMWTR-1559 | NSHC | Gambell | Bryant Koonooka | 2017-01-06 | 2017-01-10 | Routine | $305 | $225 |  |  | Bering Air | No |  | Name: Curtis Silook Title/Position: Mayor Accompanied By? No Telephonic Contact? No | Name: Ramona Tungiyan Title/Position: Utility Clerk Accompanied By? No Telephonic Contact? No | Name: Rueben Tungiyan Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Gary Kaningok Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | [6 empty] | Inspection of wind damage to 1.3 million gallon WST and 500,000 gallon WST. Install replacement heater at the well house. | Water Storage Tank: 1/6/17 Reuben,Gary and I gathered metal cutting tools to cut loose metal from the top of the 1.3 million gallon WST. We also loaded up a bin with sand bags to secure the remaining insulation. We got the sand bags on the top of WST and began cutting loose material and securing down the rest with sand bags.Wind blew off 25% of the top insulation on the north west side of the WST. We got most of material off that day. 1/9/17 Finished cutting loose metal from the top 1.3 million WST and finished securing remaining insulation.Asked Reuben and Gary to put sand bags or some weight on the material that we removed that is on the ground.So that does not get tossed around when it gets windy again. Well house: Went up and helped Reuben and Gary remove the old burnt out heater and install a new electric heater.The new heater had a built in thermostat. | 16 | 1.3 million gallon WST insulation:Need a better way of securing the insulation so it stays on the WST. This is like the fifth time this has happened. 500,000 WST: The third band from the top snapped, Letting some of the outer metal shell start peeling off.Insulation under still intact. |  |  |  |  | 1.3 million gallon insulation on top of WST wind blew off.This is like the fifth time this happened. | Yes |  | No |  | No |  | No |  | No | If necessary put more sand bags to keep rest of insulation intact. Remove loose material on 500,000 gallon WST. | Operator | Find a better way to secure insulation on the WST/Or a different style of securing the top and sides of insulation. | Other | Change out Metal covering of the 500,000 insulation and re-band. | Other | [5 empty] | Attachments | Other Documents | 2017-01-11 13:20
RMWTR-1560 | NSHC | Savoonga | Bryant Koonooka | 2017-01-06 | 2017-01-06 | Routine | $305 | $75 |  |  | Bering Air | No |  | Name: Derek Seppilu Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [9 empty] | Site visit. | Water treatment plant: Nice and clean WTP every thing running smoothly.Looked the plant thru and nothing wrong. Only thing they can not get parts for the older valve assemblies for the toilets.When those go out got to change out to the newer valve assemblies. | 4 | Can not get parts for older valve assemblies.When they go out got to change out to the newer ones. |  |  |  |  | Can not get parts for older valve assemblies.When they go out got to change out to the newer ones. | No |  | No |  | No |  | No |  | No | Change out valve assemblies as the older ones break down. | Operator | [9 empty] | Attachments | Other Documents | 2017-01-13 12:07
RMWTR-1561 | TCC | Takotna | Wes Shales | 2016-11-17 | 2016-11-22 | Routine | [5 empty] | No |  | Name: Doug Heath Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Robert Perkins Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: Amanda Goods Title/Position: Tribal Council Member Accompanied By? No Telephonic Contact? No | Name: Amanda Paxson Title/Position: Tribal Administrator Accompanied By? No Telephonic Contact? No | [6 empty] | Assist with the installation of new appliances in the washeteria and the replacement of the storage tank outlet pipe flanges. Also assist with install of a RPZ and other piping replacement as time permitted. | Arriving at Takotna Doug, Robert and myself did together a complete job breakdown and discussed some preplanning and scheduling of the “project” stages. We began with the removal of old appliances; two large dryers and a commercial sized washer. Plumbing and electrical connections were removed and the units unfastened from mounts. The old units were removed from the building and the new units were moved into position. When I was not needed elsewhere I began the process of modifying or running emt/liquid-tite conduit and a drop cord for the new appliances. I assisted in other areas of the project such as the draining of the water storage tank, replacement of the new pipe flanges that connected to the tank, and the disinfection process of the water storage tank after the pipe flanges were replaced. Because the tank was entered and pipe connections to the tank were replaced, the tank and associated piping were disinfected with an appropriate concentration level of chlorine and left to sit overnight. As different areas of work progressed, Doug asked me to look at the installation of the RPZ backflow preventer. It was quickly noted that this RPZ would not be able to be installed at the desired location. This model must be installed in a horizontal and upright position. We discussed the need for significant support that needed to be built to install it at a location that the current piping configuration could accommodate. Unfortunately Doug did not currently have that material and our schedule wouldn’t allow for it anyway. At the end stage of the work I got to the point where I did a final termination of the electrical power supply to the dryers and the washer. I wired in a 24v power circuit from each dryer to a solenoid valve. I pointed out to Doug that these solenoids both at a minimum needed to possibly be cleaned of residue/calcium build up because each one showed obvious signs of not closing/opening all the way. Replacement solenoids were on hand and Doug agreed to replace them ASAP. Other work Doug had planned for after the Thanksgiving Holiday was more building piping replacement as well as some modification to the bathrooms at the Washeteria. | 8 | None |  |  |  |  | None | No |  | No |  | No |  | No |  | No | Doug is going to obtain some unistrut for support of the RPZ and continue on with the rest of the improvements he had planned out for the building. I lent him the TCC/RMW PEX press tool that I had brought with me to facilitate the install of more PEX tubing with the connectors he had. | Operator | [9 empty] | N/A | Other Documents | 2017-01-16 10:19
RMWTR-1562 | TCC | Koyukuk | Wes Shales | 2016-12-06 | 2016-12-08 | Routine | [5 empty] | No |  | Name: Joe Hess Title/Position: ANTHC Engineer Accompanied By? Yes Telephonic Contact? No | Name: Cody Uhlig Title/Position: ANTHC Engineer Accompanied By? Yes Telephonic Contact? No | Name: John Williams Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Alfred Title/Position: Wastewater Operator Backup Accompanied By? No Telephonic Contact? No | Name: Kay Harris Title/Position: City Administrator Accompanied By? No Telephonic Contact? No | [5 empty] | Assist ANTHC Engineers with their follow up work. Also familiarize myself with the water/wastewater collection/treatment building and washeteria as well as work with the operators on current and future maintenance needs at the Koyukuk facilities. | We worked together to install a flanged pipe bracket/support sleeve for the Biomass heating system piping that enters from underneath the water treatment building. The piping originates from the Biomass Boiler building located across the street. Next we began and completed an extremely well planned out process (by Joe and Cody) of applying a customized thick rubber membrane over the top of the water storage tank. After that we installed a new heavy duty raised hatch cover for the tank. That also included a new customized rubber gasket. The tank cover was secured to the “extended” portion of the tank that the raised hatch cover was bolted to with another thick rubber membrane (one sided) self adhesive very similar to roof ice and water shield like material. Next the ANTHC engineers and myself worked extensively-with John and Alfred involved-on the pre chlorination system/pump. Also, we emphasized extensively to the Operators the need to watch the chlorine residual at the storage tank. A need/more stringent effort to monitor the pre and post filtration levels of chlorine were also addressed. Joe and Cody also were able to find an easy fix on one of the greensand tanks that was inactive/turned off because of a leak that only originated from a hose connection. Joe and Cody also addressed other minor needs they were made previously aware of at the WTP such as replacing an indicator light on a control panel. They also brought with them a retractable heavy duty ladder for the water storage tank. As we were able to find the time John and myself went over some of the items that needed to be addressed at the washeteria/water treatment building. As he was able to Alfred was also involved with us. A heavy duty triple loader replacement washer recently received into the community requires a 208 or 240 volt two pole single phase circuit. In addition, at the point that the washer drains into on the building piping will have to be increased from 2 inch to 3 inch to accommodate the increased volume of water that the washer dispenses after its wash and rinse cycles. Some extra 3 and 4 inch abs drain pipe and a drain hose will need to be obtained before that project can be completed. At the end of our time in Koyukuk we were able to tour/review the operation at the Biomass boiler building. Joe and Cody’s knowledge and background with the operation of the system and there introduction to me about it was significant to my quick understanding about it. | 8 | None |  |  |  |  | None | No |  | No |  | No |  | No |  | No | John has asked me to return after the New Years holiday to help him replace the sections of drain pipe and do the electrical hookup for the new badly needed washer. Both John and Alfred requested more formal water treatment operator training to address the required testing/certification they need to take soon. I told them it wouldn’t be until spring time that training was offered at a couple different locations in the State. I said I would see what TCC can do for them to assist in them attending that training. | RMW | [9 empty] | N/A | Other Documents | 2017-01-16 10:30
RMWTR-1563 | TCC | Chalkyitsik | Wes Shales | 2016-12-15 | 2017-01-16 | Emergency | [5 empty] | No |  | Name: Larry Henry Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Woodie Salmon Title/Position: Tribal President Accompanied By? No Telephonic Contact? No | Name: Kayleen Carroll Title/Position: Utility Clerk Accompanied By? No Telephonic Contact? No | [7 empty] | Assist in addressing frozen washeteria sewer line, inoperable watering point, as well as other water plant operational methods. | Larry was out of town just prior to my arrival and during his absence as well as his recent return efforts to address immediate needs were taken that created other problems or concerns from others. A garden hose had been routed out the back door to a sewer line to try to prevent it from freezing and /or help thaw it out. It had been hooked up to a washer hot water supply tap. Cold air was entering the mechanical room from this setup. Larry said he would usually cover the door entrance with canvas or tarp when this was usually done. The hot water supply valve was turned off and the hose “cut” out of the picture. An end portion of the hose was removed from the point it entered the sewer line; thrown away and the entry point closed off. During normal operations water added to the sewer line from an appropriate location would help prevent residual water in the pipe from freezing but this effort was too late and the water added to the sewer line was only backing up and overflowing onto the ground. In addition the boilers had just recently failed /lost glycol and the hot water heat exchanger was not working because of lower operating pressure. Larry recharged the glycol in the heating system and closed off a couple different heating system auto air vents that had leaked glycol. I advised him to install new aerators/auto air vents when possible. Electric heat trace used on the sewer line when energized would cause the Village electric utility transformer that supplied the area of town that the water plant is located to blow a fuse. Just prior to my arrival two of what I soon found out to be the last fuses were used to re-energize the transformer. Control panel amp readings at the power plant showed that leg of the three phase electric utility supply was being close to overloaded under these conditions without using the heat trace. I very specifically inquired with Larry about using the water plant standby generator to operate the plant and the heat trace and he confidently responded that that too overloaded the generator at the water plant. We determined that the school going on its own generators would do no good because if the fuse decided to blow at the transformer even with the school load being dropped 1/3rd of the town would be without power until a special fuse would arrive to replace it. I helped Larry push a large Hotsy brand portable hot water maker into warm storage in the event he would possibly have to use it to thaw out the sewer line from a nearby cleanout. As I left Chalkyitsik for another emergency in a nearby community Larry felt confident he could get the sewer line thawed out with the Hotsy or using the sewer line heat trace and I did advise him I thought that the water plant standby generator should be able to handle the load. Another concern that was addressed was “carbonated like water” coming out of the temporary water point that was accessed from the same door the hose was routed out to the sewer line. It was quickly noted upon investigating the issue that the tap used to draw water out of was extremely close to the pressure pumps. The school filling up their water storage tanks and water being pumped to the holding tank from the supply source, power failures resulting in empty pipes at the washeteria were all contributing factors to this phenomena. New heat trace was installed at the community water draw access point and the piping was hooked back up. Also, in the event a hose was used to add hot water to anything in the future, I installed an inline check valve before a hot water tap that was also supplied with an anti-siphon attachment. This spigot is located within the water plant and not the washeteria side of the building that the initial hose going out the back door was tapped from. In addition I advised Larry that the greensand filters might need to be backwashed more effectivcly and that the GAC filter needed an appropriate backwash. He said it had never been backwashed because the Contractor told him it wasn’t necessary. (We couldn’t do any type of backwash at the plant at that time because of the frozen sewer line). Also, the plant contained no procedural operational maintenance manual. Last of all We verified that the water storage tank recirculation system was operating and that the chlorine pump was working and that an acceptable chlorine residual was present. | 8 | None |  |  |  |  | None | No |  | No |  | No |  | No |  | No | Upon my exit from Chalkyitsik Larry and I both were in agreement that an immediate bacti sample needed to be sent to Fairbanks. Without any doubt I found Larry to be an overall knowledgeable and capable water plant operator. I saw and understood that even though his work load at times might be “heavy” he still performed the work anyway with or without help. I found Chalkyitsic to be another TCC region community to be full of life and friendly in nature. People were quick with good conversation. | Operator | [9 empty] | N/A | Other Documents | 2017-01-16 10:43
RMWTR-1564 | TCC | Venetie | Wes Shales | 2016-12-16 | 2016-12-19 | Emergency | [5 empty] | No |  | Name: John Frank Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Ernest Erick Title/Position: Project Superintendant Accompanied By? No Telephonic Contact? No | [8 empty] | Assist in resolving failed heat trace. The water supply line from the well pump house to the water treatment building was froze up and the water storage tank was empty. | The well pump was operational and the small well house building was very adequately heated. Thru troubleshooting it was determined that one of the two separate sections of heat trace had failed that protects the water supply line from the well house to the water plant. The large capacity water storage tank is filled on an as needed basis approximately every three months. The design of the transmission line has been an extremely difficult situation for the community to maintain in the winter months. A low spot halfway thru the route of the line that has an accessible vault fills up with ground water in the spring/early summer. That situation causes the ground water to enter the below surface area and enter the arctic pipe. In addition, if the water inside the transmission line is not fully drained out (which is difficult to do) it is potentially able to freeze if the heat trace is not working or not energized. It was determined that the lower half of the lower section of the two separate heat trace had failed. At the vault I was able to isolate the good upper half of the lower section of heat trace. That section of transmission line was apparently frozen also. The upper section of the two separate heat trace was operational and registered normal amp draw. Because time, temperature and the overall situation with the heat trace was not on our side we decided that available water hose would be utilized to transfer water from the well house to the water plant. An exhaustive effort was accomplished of connecting approximately 1000 feet of the hose and covering it up with snow to help insulate it from the extreme cold. The effort paid off and the storage tank immediately began to fill up. Overnight monitoring of the situation at the water plant showed overall stable psi/flow. The hoses were connected at the plant at an appropriate location that would allow for chlorine treatment and filtration. Chlorine residual registered at .5 mgl. As of my departure from Venetie it was hoped that the upper half of the lower section of heat trace would thaw out the line and that the hose could be connected to the piping at the vault. That way the over-the-ground run of hose would only be about 250 feet. | 0 | None |  |  |  |  | None | No |  | No |  | No |  | No |  | No | As we progressed thru our effort many members of community came around to assist the original three of us. As of the writing of this report I lost the list of names. A loader operator, the school maintenance guy and a couple more individuals assisted us that I know of. I was impressed with the cool nature of folks that I worked with and met at the store. Thank you Venetie. | Operator | [9 empty] | N/A | Other Documents | 2017-01-16 10:54
RMWTR-1565 | TCC | Tetlin | Wes Shales | 2016-12-22 | 2016-12-23 | Emergency | [5 empty] | No |  | Name: Michael Sam Title/Position: Tribal President Accompanied By? No Telephonic Contact? No | [9 empty] | Respond to electrical hazard report of building main breaker tripping as a result of electrical malfunction/direct short of power feed at well box for well pump. Well pump remained out of service as a result. | Upon arrival I checked the building service at the panel and verified the breaker for the well pump was turned off/LOTO. Inspection of the well box contents revealed burnt wiring originating from power feed conduit that entered the box from underground. It was stated that an electric/diesel torpedo heater used to prevent freeze up at the box had accidently burnt up the wiring. It was also stated that the well casing itself had “turned red” from the heat. Shorted wiring under the sanitary seal was removed and the remaining wiring to the pump was used to test the pump motor and it didn’t reveal any continuity to ground, etc. A new temporary electrical feed to the well casing that was spliced in showed normal amp draw of the motor. Unfortunately piping to the building had frozen. Heat trace for the piping had not been completely installed around the pipe and was not producing any positive results. A new pump w/control box was previously bought by the community and not yet installed. Mike agreed to have us return after the holidays to install the new pump and control box. I informed him we would need new wire for the run to the pump from the control box as well as liquid tight conduit to run it thru. I also stated that it appeared the aged motor starter/thermal overload relay assembly showed signs of wear. It had a small amount of “blow” marks from repeated use. During testing of the temporary repair it had not shown to produce negative results tho. I did caution the crew about putting the pump on the hand position at the switch in the future or during testing of the effort to thaw out the frozen lines. In the mean time the frozen pipes prevented us from fully observing the repaired pump operations. I asked about simply replacing the short run of frozen water line but was told no available pipe existed locally. The crew working with me began the process of removing the lid to the artic box that goes between the building and the artic box that houses the well casing. I gave them some ideas and supplies on properly fastening the heat trace to the water pipe and the well casing and how to more safely supply supplemental heat to the artic box that surrounds the well casing. | 0 | None |  |  |  |  | None | No |  | No |  | No |  | No |  | No | As of the writing of this report we gathered up all the necessary wire/liquid tight conduit and splicing material to safely install the new pump and control box. Mike reported that the old pump started tripping out. Tetlin is one of Lee Meckel's RMW communitys. Lee went down to Tetlin yesterday to help install the items. I did clue him in on possibly adjusting the amp setting on the thermal overload relay at the motor starter and that resolved the problem. The new pump will be installed at a later date. | RMW | [9 empty] | N/A | Other Documents | 2017-01-16 11:04
RMWTR-1572 | DEC | Bethel | John Johnson | 2017-01-10 | 2017-01-12 | Training/Meeting | $380 | $105 | $0 |  | Ak Airlines | No |  | Name: Mike Roberts Title/Position: ANTHC Engineer Accompanied By? No Telephonic Contact? No | Name: Charissa Williar Title/Position: ANTHC Engineer Accompanied By? No Telephonic Contact? No | Name: Andrew Lean Title/Position: ANTHC Engineer Accompanied By? No Telephonic Contact? No | Name: Brian Lefferts Title/Position: Environmental Health Officer Accompanied By? No Telephonic Contact? No | Name: Bob White Title/Position: RMW Accompanied By? No Telephonic Contact? No | Name: Allan Paukan Title/Position: RMW Accompanied By? No Telephonic Contact? No | Name: Billy Westlock Title/Position: RMW Accompanied By? No Telephonic Contact? No | Name: Bruce Werba Title/Position: RMW Accompanied By? No Telephonic Contact? No | Name: Donna Lee Title/Position: VSW Engineer Accompanied By? No Telephonic Contact? No | Name: Sean Lee Title/Position: VSW Engineer Accompanied By? No Telephonic Contact? No | I traveled to Bethel to attend the YKHC Community Coordination meetings. I departed Anchorage on the early Alaska Airlines jet and arrived in Bethel at 7:30am. I caught a cab and headed to the conference location which was at the Prematernal Home this year. This meeting was to coordinate effective and consistent communication between the agencies and communities. And to get all agency representatives up to date on the community issues and efforts in providing service to the communities. | The coordination meeting started at 9:00am and there was a nice showing from all agencies. Solid waste phoned in to participate in the meetings. The first day we discussed issues and concerns with 25 of the 50 communities on the agenda. we adjourned the meetings at 5:00pm. The next day we started up at 9:00am again and were able to discuss the remaining 25 communities and we adjourned at about 4:00pm. I then met the YK RMW's at there shop to get a little one on one time and look over there facility. I found the extra one on one time to be very beneficial and I was able to learn a little bit more about the issues that meant most to the operators in that region. I departed the shop for the airport at about 6:00pm and we notified at about 7:30pm that our Ak Air flight was cancelled do to weather. I checked into the Long House Hotel for one additional night and then checked into Ak Air again in the morning at 7:00am. | 0 | The need for thorough design/review, construction as-built's and complete follow through as well as certificate to operate on all facilities is crucial. The need for all utilities to have a certified operator and a back up operator is an ongoing struggle in most communities. |  |  |  |  | Many issues were brought to the table that included local operation of the facilities, local government and the utilities, failing infrastructure and facilities, operator certifications, design issues, utility rates and preventive maintenance plans, taxes and workman's comp obligations, best practices scores and the need for funding for small projects that can increase facility operations and reduce costs. (projects under 50,000) | Yes |  | No |  | No |  | No |  | No | Continue to follow up on the issues that were brought to lite and work together to solve the issues in a way that's sustainable and cost affective. | RMW | [9 empty] | N/A | Other Documents | 2017-01-30 10:11
RMWTR-1573 | TCC | Chalkyitsik | Wes Shales | 2017-01-05 | 2017-01-07 | Emergency | [5 empty] | No |  | Name: Lee Meckel Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Davis Carroll Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Tamara Henry Title/Position: Tribal Administrator Accompanied By? No Telephonic Contact? No | Name: Kayleen Carroll Title/Position: Other Accompanied By? No Telephonic Contact? No | Name: Brian Joseph Title/Position: Other Accompanied By? No Telephonic Contact? No | [5 empty] | Assist community with ongoing frozen sewer line problem. | An attempt just prior to our arrival to thaw out the sewer line from the only two cleanouts a little over halfway down the length of the main was unfortunately unsuccessful. We made repeated efforts at thawing out the sewer main leaving the washeteria and were able to advance only approximately 30 feet or so. Clumps of cloth and or mop strands as well as paper towel did exit the area we were accessing the main at during our efforts. (Right next to the area it exited the building). During construction the route of the sewer line required placement of five 90’s within its path around the vicinity of the washeteria building. Both operators we have worked with recently as well as other community members have told us this. If cleanouts had been installed near some of the locations where the 90’s were installed underground this situation would have been a lot easier to correct. Apparently left over from construction of the sewer main are about six arctic pipe cleanout connections with other various pieces of material that are staged near the washeteria. Along with failed heat trace, installation issues, and operator turnover this has been an ongoing problem. Below surface utilities can be extremely hard to maintain or repair for obvious reasons including heat trace failure, ground freeze/thaw issues, or inadequate considerations during installation or even design. Add to that list the need for a better preventative maintenance program or even lack of maintenance during low or high use situations. It was our understanding that the heat trace was thought to be energized because the School was on their own standby power. When we arrived we found that the heat trace was actually turned off at the breaker panel still and so we began to troubleshoot why it would trip out at the motor starter. A downstream section of it had to be isolated and de-energized at an above ground splice box. No specific or as built drawing existed for what seems an unusual amount of heat trace splice boxes or power boxes for the route of the sewer line. A pipe with inadequate cleanouts and sitting water/sewer in it during 40 to 60 below weather that isn’t buried very deep and/or not insulated good enough and experiences heat trace issues etc. is asking for trouble. We found that the hotsy jetter we were going to use was missing some parts and had a blown high pressure gauge. It did have glycol in it. During my last 24 hours in Chalkyitsik time was also spent going over basic operation of the plant and procedures for testing for chlorine and maintaining a proper residual in the drinking water storage tank as well as how to safely mix the proper solution of chlorine. The mixing vat was dry at the discharge valve so we made up a new vat of it. Davis was fully involved with all work we performed as well as extremely quick to catch on. He and I went out to the well house before my departure and turned on the electric heat there and went over the procedures for pumping water up to the plant. It takes 2-3 days to fully heat up the place to a point the hose is thawed out. He said he thought Brian could help him pump water. | 16 | See trip details info. |  |  |  |  | See trip details info. | No |  | No |  | No |  | No |  | No | When a water or sewer system is designed and installed it should be done to reflect a standard of concern for future maintenance needs/maintenance accessibility. It is for good reason that plumbing and electrical codes exist that are intended not just for urban but rural safety and accessibility and also for intended long term operation. All too often lately it is observed that a treatment or collection facility is up to standard but that the distribution or collection/disposal system/site is not well planned out or constructed. It has been stated that during construction of the sewer system in Chalkyitsik the arctic piping had to be weighted down because it was floating with the high ground water level! In a community that doesn’t experience a lot of extreme weather conditions or massive permafrost a water or sewer system installation that experiences high ground water conditions during or after construction might not be so affected. Also: Everybody that designs or installs an electric heat trace system needs to be aware that heat trace goes bad/fails! I have installed heat trace in arctic piping that allows for future replacement as well as a backup heat trace in case one fails. Cleanout, cleanouts, cleanouts! It’s a lot easier to replace components of a system that aren’t buried underground also……. In addition, maybe a glycol heat loop if at all possible is a good idea not on just water lines but also certain sewer lines. Many communities have only one operator. Should a primary operator experience situations that result in departure from the community or not being able to adequately operate a facility it is critical that another reliable and trained individual is fully able to take over whether it is temporary/ long term/permanent or simply just day to day. I was an operator in a Village where 40-60 people lived and it was hard enough with two of us reliable Operators sometimes. | RMW | [9 empty] | N/A | Other Documents | 2017-01-19 09:58
RMWTR-1574 | NSHC | Koyuk | Bryant Koonooka | 2017-01-18 | 2017-01-18 | Routine |  | $75 |  |  | Bering Air | No |  | Name: Evette Henry Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Mathew Hoogendorn Title/Position: Utility Clerk Accompanied By? No Telephonic Contact? No | Name: Tracey Kimoktoak Title/Position: City Clerk Accompanied By? No Telephonic Contact? No | [7 empty] | Site visit. | Water Treatment plant: The WTP had been thru some ground shifting.The south side of the building Washeteria side sunk some.Creating cracks in the walls and cement floor,Doors hard to open and close.The floor is not level anymore. There we're beams,uni-strut and pipe that were braced up by 2" by 4"'s. Couple of the uni-strut were lagged into drywall with no backing.The pipe after the pressure pumps would shake when the pumps would turn on. They had just thawed out the supply line just before the new year,the return is still frozen.The main operators had got frustrated with equipment freezing and quit during the Jettering process to thaw out the line. Evette Henry stepped in after they left. Steve Hoogendorn has been helping Evette with the jetting and getting the WTP back up and running. They are running with just one well pump and they had ordered one from Alaska utility supply center(AUSC).As soon as they receive the pump they will install and get both pumps going.Water coming in at 19.4 GPM and tank level at 12 feet. | 4 | Ground shifting WTP not level anymore.Walls,cement cracking.Doors not level too. |  |  |  |  | Ground shifting WTP not level anymore.Walls,cement cracking.Doors not level too. | Yes |  | No |  | No |  | No |  | No | Change out or install new well pump when new one arrives. | Operator | [9 empty] | Attachments | Other Documents | 2017-01-19 15:29
RMWTR-1575 | NSHC | White Mountain | Bryant Koonooka | 2017-01-18 | 2017-01-18 | Routine | $324 | $75 |  |  | Bering Air | No |  | Name: Ed Titus Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Steven Titus Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: Yvonne Greg Title/Position: Utility Clerk Accompanied By? No Telephonic Contact? No | Name: Amos Brown SR Title/Position: City Council Member Accompanied By? No Telephonic Contact? No | Name: Kolt Garvey Title/Position: Electrician Accompanied By? No Telephonic Contact? Yes | [5 empty] | Site visit. | Water treatment plant: Ed and Steven were working on fixing a 3/4 inch plumbing to the unit heater in the water plant.The piping was leaking from the bottom of the 90* elbow o.Every thing else was running good. Ed had mentioned that the that the heat add to the distribution has not been opening or working.Worked the controller a bit and called Kolt Garvey,His phone went to voice mail.After looking thru the plant i noticed that the heat add system was with-in the temperature range and fine. Kolt called and talked me thru it and confirmed to that it was fine. Water storage tank: Still has a slight leak but hard to say from where as the base had about a foot deep of snow around the base of the WST. The tank level was about 20 feet of water in WST. | 4 | Water leak on the WST but not as bad as before. |  |  |  |  | Water leak on the WST but not as bad as before. | Yes |  | No |  | No |  | No |  | No | Change out leaking 3/4" pipe. | Operator | Keep a eye on the WST. | [8 empty] | Attachments | Other Documents | 2017-01-19 16:38
RMWTR-1576 | TCC | Chalkyitsik | Wes Shales | 2017-01-11 | 2017-01-14 | Emergency | [5 empty] | No |  | Name: Fred Kameroff Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Davis Carroll Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Tamara Henry Title/Position: Tribal Administrator Accompanied By? No Telephonic Contact? No | Name: Katelyn Englishoe Title/Position: Utility Clerk Accompanied By? No Telephonic Contact? No | Name: Brian Joseph Title/Position: Other Accompanied By? No Telephonic Contact? No | [5 empty] | Provide further assistance with frozen sewer line and pumping water from the river. | We brought along a 75 ft. long powered sewer snake to use in conjunction with either a jetter or pex and hot water to possibly help us clear the ice/blockage in the sewer line. Water delivery issues with attempting to clear the obstructions from the distant cleanouts prevented us in even attempting a serious effort from that direction. In addition, it was decided that should we have any amount of success doing that it would probably freeze back up with sub-zero temperatures and the lack of reliable working electric heat trace anyway. Initial efforts to check for frozen sewer line/blockages with our equipment resulted in the snake finding cleared line up to just past the possible third 90 in the sewer main at approximately 60-65 ft. down. A possible turn in direction is estimated to occur just after/at our reach limit with the snake. The heat trace appears to be working well in that first section and is warm to the touch leaving the building but cold at a splice box nearby the 60 foot reach point. At the clean-outs half way down the line the sewer is frozen. We refocused efforts at getting water flow from the pump house/river. In addition, we made the decision to begin pumping sewer into a pvc tank that was used previously in prior years to do the same. It would be hauled to the lagoon from the Plant. We would need a drain valve and a cap for the Tank. Fred agreed to return that day to Fairbanks and help out there in obtaining the parts and to standby for other possible calls because Lee was busy back in Fairbanks getting ready to take care of business elsewhere. Davis and I began the process of using an ice auger to drill a hole on the river ice. Our first hole at the usual spot found the ice too deep into the river. No water was found at 4 ft. down approximately. A second hole found water at just over 3ft. down and maybe 8-10 ft. farther out on the River. The pump was placed in the hole. A retractable 2” hose that cam locks to the pump was connected. The hose extends from the pump house down the river embankment and out onto the ice for a total of maybe 50-65 ft. Davis was completely unfamiliar with the electrical hookup to the pump that sits just at the surface level of water that has risen up to the top of the hole we drilled. I demonstrated the safe and proper method for hooking up the electrical feed to the pump. Previously we had redirected the flow of water to outside the water plant. All appropriate valves were opened or closed and water line would exhaust water away from the plant and independent of the filtration and storage/distribution system including the lift station/sewer system. Heat trace on the water transmission line from the pump house had been energized for weeks and indicated normal amp draw. Unfortunately we quickly discovered that the transmission line was frozen. The hose from the river was clear and the pump was working fine. We spent the rest of the day and into the evening turning on the glycol heat loop for the transmission line corridor. Initial temps from the heat loop indicated 25 degree temps on the return line just after I energized the circ pumps/opened the valves for that loop. The next morning on Friday supply temperature at the loop was about 80 degrees and 60 degrees on the return loop. We had rolled back up the hose to the river hole so we layed everything back out/hooked it up and turned it on to find 20 plus gpm flow at the water plant. We allowed about 500 gallons to bypass out the plant before we did a flush of the filtration/gac tanks. The flush of the tanks was exhausted out of the building also. We used valves and connections already in place and new or water specific hoses to perform the mentioned operations. Next we used a series of valve manipulation and connections to thoroughly backwash the tanks. That water also remained independent of the lift station/sewer system for obvious reasons. All these efforts at flushing and backwashing the tanks is a series of steps that will prevent an inrush of discolored looking water making it into the water storage tank especially if water hasn’t been pumped for a long time. Every time water is first pumped from the river these steps should be completed. After our initial steps were completed we opened or closed the appropriate valves and good, clean filtered/treated water began its push into the water storage tank. All during our efforts to get water flowing to the storage tank Brian Joseph was working on his frozen water line to the school. By Saturday the 14th he got the line thawed out. The school holding tank was empty. It is similar in size to the community holding tank. The Chalkyitsik holding tank had approximately only 7 feet of water. As of the writing of this report the school holding tank is full and the community holding tank is full with 19 feet of water. Late Friday afternoon we also received our parts for the sewer haul tank. Using the existing lift station pump and a bypass line we pumped straight into the tank. To empty the lift station of about its 300 gallons takes two quick trips with the setup we utilized. That haul tank is emptied by opening up the valve we installed and letting the mixture gravity feed into the lagoon. All this effort allows for a carefully maintained/monitored use of the washeteria facilities. Davis and I continued with a further review of the water plant operations as well as what he needed to do with respect to sending out water samples for analysis. We went over how to fill out forms and how and where in the plant to take the samples from. In addition, we went over how to mix the polymer and how it is used to help control turbidity. We also spoke of him (Davis) attending an upcoming water treatment operator course sponsored by TCC this early Spring. Also needing mentioning is what I found to be a faulty control of the lift station pumps. Someone or something (a faulty relay or other control device) has bypassed the HOA switch and on the next trip I will have the time to correct that. The pumps are still controlled by the correct action of the floats in the tank but are energized if called for by activating the disconnect switch to the on position. | 16 | See trip details. |  |  |  |  | See trip details. | No |  | No |  | No |  | No |  | No | Perhaps a larger lift station and a better haul system could be part of the answer to the ongoing sewer line problems. A new maintenance friendly sewer system is the ultimate answer but until then perhaps this summer TCC can help install cleanouts in the line. Better grinder-pumps for the lift station might also help including what is referred to as a inline “muffin monster” brand grinder that would make complete slurry out of anything traveling thru the line (after the pumps). It’s my understanding that there is already money put aside for something to do with the water plant. Eventually if anything else further testing of the electric heat trace is an option but by many accounts it’s easy to conclude it would be a major project just too properly replace the trace. | Construction Project | [9 empty] | N/A | Other Documents | 2017-01-19 15:45
RMWTR-1578 | NSHC | Diomede | Bryant Koonooka | 2017-01-20 | 2017-01-20 | Routine | $1,500 | $75 |  |  | Erickson Helicopter | No |  | Name: Robert Larson Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Betty Ann Koutchak Title/Position: Utility Clerk Accompanied By? No Telephonic Contact? No | [8 empty] | Site visit. | Water treatment plant: One of the boilers was working the other one needs a few parts to get it running.Every thing else was working just fine.The main W.P.O. Robert Umiak had gone out for certification training. The alternate Robert Larsen showed me around the W.T.P.He was using the back up generator,cause their power plant was having issues with some of their services and other stuff in the power plant. | 4 | Boiler #2 needs few parts to get it running. |  |  |  |  | Only one boiler running. | No |  | No |  | No |  | No |  | No | Get the other boiler #2 going. | Operator | [9 empty] | Attachments | Other Documents | 2017-01-23 14:38
RMWTR-1580 | DEC | Ninilchik | Kevin Schoneman | 2016-12-13 | 2016-12-13 | Routine | [5 empty] | No |  | Name: Floyd Murphy Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Sean Lee Title/Position: VSW Engineer Accompanied By? Yes Telephonic Contact? No | Name: Steve Vanek Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [7 empty] | Check on the water treatment plant and water storage tank. And meet with water operator. | RMW Floyd Murphy, VSW Engineer Sean Lee and myself left Anchor Point after the site visit there and headed to Ninilchik . I called the water operator Steve Vanek and asked if the group could meet with him at the Water Treatment Plant and Watering Point. After arriving in Ninilchik I talked to Steve again and he requested we meet at his residence and proceed from there to the plant. Once we all arrived at the plant we all went inside. Sean and Steve both gave me a tour of the plant and showed me the area that had been repaired on the Water Storage Tank. There was no evidence of any additional water leaks and the areas that were repaired earlier in the year were dry. Steve reported that there had been no problems with the boiler or any of the heating system. Steve stated he has been dipping the fuel storage tank at least once per week and figured that there was about 180 gallons of fuel remaining, there was some discussion as to who would be responsible for filling the tank when it was needed. Sean told Steve he would check with management as too who would be responsible for refilling the fuel tank. We all then went outside and checked the area on the tank that was repaired in early May and no visible sign of water seeping or leaks. The Water Treatment Plant appeared to be well maintained with no major issues. | 0 | None noted on this trip. |  |  |  |  | None noted. | No |  | No |  | No |  | No |  | No | Plan for fuel purchases for next winter. | Community | [9 empty] | Attachments | Other Documents | 2017-02-06 15:23
RMWTR-1581 | YKHC | Napakiak | Bob White | 2017-01-25 | 2017-01-25 | Routine |  |  |  |  | YKHC Truck | No |  | Name: Calvin Charles Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [9 empty] | To deliver heater and help troubleshoot electric heat trace. | I arrived in Akiak with the heater at the water plant were I was met by Calvin we talked about the problems they had through the last cold spell. I then put on my cold gear and we headed to the home they were having trouble with. I began by assessing the wiring at the site. we found the outlet was not powered and i decided we should check the heat trace for breaks by megering it. We proceeded to undo the connection and run a meger test. After that passed successfully we energized the controller and checked for proper operation to the heat trace connection with all that checking out good we deenergized the circuit and reinstalled the heat trace. with every thing back together the heat trace came on and heated up. The only problem we found was a questionable connection from the power supply to the heat trace. We then moved our equipment back to the water plant and I departed back to Bethel. | 4 | AVCP installation of the piping and heat trace was poorly done. |  |  |  |  | none at this time | No |  | No |  | No |  | No |  | No | Reset the heat trace controller to 30 F once line is thawed. | Operator | Remove needle in the MV80 jetter solenoid valve | [8 empty] | N/A | Other Documents | 2017-01-26 09:24
RMWTR-1587 | TCC | Chalkyitsik | Fred Kameroff | 2017-01-11 | 2017-01-12 | Routine | [5 empty] | No |  | Name: Wes Shales Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Harry Carroll Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Tamara Henry Title/Position: Tribal Administrator Accompanied By? No Telephonic Contact? No | Name: Kateyln Eagle Shoe Title/Position: Other Accompanied By? No Telephonic Contact? No | [6 empty] | Attempt to thaw out sewer line | Mr. Wes Shales and I departed for Chalkyitsik on 1/11/17 with a new motor powered 75 foot snake to try and free what maybe inside the sewer line. Mrs. Tamara Henry met with us at the airport and escorted us to the water plant where we met with Mr. Harry Davis Carroll and began to set up the new snake. Once we had put the snake together we attempted to snake out anything that might be inside the sewer line. After several tries with the snake we were unsuccessful pulling out anything, and could not push the snake past about 34 feet, which was the same as when Mr. Shales had tried with PEX tubing the previous trip The obstruction may be a freeze, a clog, but may also just be one of the several 90 degree elbows in the line, based on the distance. By next morning we walked to the clean outs and found them to be frozen, as for trying the snake we had come up with another plan. We told Mr. Carroll that he would need to pump and haul out the waste with using a 300 gallon container and dump it in the lagoon. After inspecting the container and seeing that it needed some parts, I made the decision to head back to Fairbanks and purchase the valve and the cover for the tank, and ship them up next day. Mr. Shales stayed behind and assisted Mr. Carroll on pumping and treating water and with the waste water, to help him get started on how to pump and haul it to the lagoon. RECOMMENDATIONS/CONCLUSION As for the sewer force main it will have to wait until this spring and dig it out and install a clean out and look to see if anything is clogging the sewer line. Also some parts of the heat will need to be pulled and replaced with new heat tape. Until then, pumping and hauling the wastewater keeps the laundry open for the residents of Chalkyitsik. | 8 | sewer force main frozen |  |  |  |  | none | No |  | No |  | No |  | No |  | No | sewer line will need to be dug up by this spring or sooner to clean out and add clean outs on line | RMW | [9 empty] | N/A | Other Documents | 2017-01-30 11:22
RMWTR-1588 | YKHC | Bethel | Billy Westlock | 2017-01-09 | 2017-01-12 | Training/Meeting | $600 |  |  |  | Grant aviation | No |  | Name: All ykhc rmw's Title/Position: RMW Accompanied By? No Telephonic Contact? No | Name: State rmw Title/Position: RMW Accompanied By? No Telephonic Contact? No | Name: Village safe water staff Title/Position: VSW Engineer Accompanied By? No Telephonic Contact? No | Name: Anthc staff Title/Position: ANTHC Engineer Accompanied By? No Telephonic Contact? No | Name: Bethel eho's Title/Position: Environmental Health Officer Accompanied By? No Telephonic Contact? No | [5 empty] | Conduct a meeting all about our water sewer communities thru out the ykhc region. | We started a meeting concerning all of the communities thru out all of ykhc region. This meeting was to see about on going problems, what's needed to make all our plants healthy again and in good running condition, up coming projects that are needed in each community. This was a very good informal meeting and to see if there is going to be future money's to get a community running water and sewer. On Thursday I departed for home after all our meetings were completed. | 0 | None at this time |  |  |  |  | None at this time | No |  | No |  | No |  | No |  | No | None at this time | Unknown | [9 empty] | N/A | Other Documents | 2017-01-30 12:28
RMWTR-1591 | TCC | Tanacross | Fred Kameroff | 2017-02-02 | 2017-02-03 | Routine | [5 empty] | No |  | Name: John lilly Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: chris deny Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: agnes deny Title/Position: Tribal Administrator Accompanied By? No Telephonic Contact? No | [7 empty] | Replace Circulating pump on Hydronic line. | Mr. Brian Bearden asked me to contact Mr. Chris Deny from Tanacross since Mr. Wes Shales, the assigned RMW for Tanacross, was traveling. I contacted Mr. Deny and he just needed info on where he could order anew Circulating pump. I told him he can call Mr. John Sims from ANTHC, and that Mr. Shales will be back in the office and I will forward him the info. Once Mr. Shales came to work the next day I passed the info to him and he contacted Mr. Deny. Mr. Shales then made a few calls on finding a pump for Tanacross; Mr. Shales contacted Mr. Sims and located the same make and model of Grundfos pump and had it shipped it up to our office to run it up to Tanacross. Mr. Shales and I arrived at Tanacross just after 5 pm and found Mr. John Lilly and Mr. Chris Deny getting ready to thaw out a house service line. We dropped off the pump and told them we will be back in the next morning. We arrived back at Tanacross on 02/03/17 at 8:30 am an met with Mr. Lilly and Mr. Deny. We then started to remove the old worn out Grundfos Circulating pump and installed the new one, after the new pump was installed and wired up we purged the air from the pump head and recharged the Hydronic system and started the pump. We verified the glycol was circulating, and let air out from the air vents. RECOMMENDATIONS/CONCLUSION Mr. John Lilly will need to order a new back up pump should the other pump go out. | 4 | none |  |  |  |  | none | No |  | No |  | No |  | No |  | No | water operator | Operator | [9 empty] | N/A | Other Documents | 2017-02-14 10:53
RMWTR-1592 | TCC | Arctic Village | Fred Kameroff | 2017-01-18 | 2017-01-20 | Emergency | [5 empty] | No |  | Name: George Yatlin Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: Tiffany Yatlin Title/Position: Tribal Administrator Accompanied By? No Telephonic Contact? No | Name: Limmet Ross Title/Position: School Representative Accompanied By? No Telephonic Contact? No | Name: Bernard Walker Title/Position: Consulting Engineer Accompanied By? Yes Telephonic Contact? No | Name: Nelda Walker Title/Position: Other Accompanied By? Yes Telephonic Contact? No | [5 empty] | Assist and train alternate water plant operator | Mr. Brian Bearden contacted me stating that Mr. Robert Eric had a medical issue and Mr. George Yatlin had been asked to fill in for Mr. Eric, He informed me that I may need to head up with Mr. Bernard Walker, but wasn’t sure when it would be. I contacted Mr. Walker on 01/17/17 and asked about Arctic Villages situation, he stated they had only 2 feet of water and the new operator had pumped in raw water (without treatment) as an emergency measure to keep the distribution system from freezing up. I asked when he was planning on heading up to Arctic Village; he said on 01/18/17. I told him I would head up with him. We arrived at Arctic Village and were greeted by Mr. Yatlin and Mr. Ross and escorted to the water plant. Once we were settled in the water plant we looked at the water intake and noticed a hose was connected from the raw water (river) intake line directly to the water line into the water storage tank. Mr. Walker removed the hose and reconnected the 2 inch ball valve to the river intake line. Mr. Yatlin then went to get heating fuel for the water plant boilers and said he would be back once he was done pumping fuel. Mr. Yatlin came to the water plant once he was done pumping fuel and we set up to start pumping and treating water. Mr. Walker explained to Mr. Yatlin the process of treating water, starting from the intake river line to the Streaming Current Detector, (SCD). The (SCD) detects the charge in the water and calculates the correct dosage of coagulant to be added into flocculation tank. From there the water flows to the clarifier and once it is filled up, it goes through the weirs and into the filtration chamber. Once the water passes through the filter it pumps out to waste until the turbidity level reaches 0.2 ntu, and then the automated valves open and begins discharging into the water storage tank. When that occurs, the chlorine pump turns on to disinfect the filtered water. Within one hour of pumping water the water pump and hose started to freeze and shut down the pump. By the next day we reset the river pump and the hose, insulated the raw water line the water pump from keeping it from freezing in the 50 below temp. At end of the day we had pumped and treated water for 7 hours and gained 1.6 feet of water and the chlorine residual was at 0.19 mg/l. On Friday 01/20/17 I was scheduled to fly back to Fairbanks and Mr. Walker said he was going to stay back and pump more water at least up to ten feet in the storage tank. I contacted Mr. Walker on Saturday 01/21/17 to see how the pumping was going and he stated he stayed up all night pumping water and now had over 8 feet of water, RECOMMENDATIONS/CONCLUSION Mr. Walker contacted Mr. Bearden stating he was trying to get hold of me to pick up the water samples he had taking from Arctic Village to take over to Analytica for sampling. The water samples were tested and came back negative and the water was good for consuming both at the school and the water plant water tank. Mr. Eric returned to Arctic Village sometime during the week of January 23. Mr. Yatlin and Mr. Eric pumped and treated water on 02/01/17 and Mr. Yatlin stated he had over 7 feet of water in the water storage tank. Mr. Eric is now back working at the Arctic Village water plant as the primary operator and Mr. Yatlin as alternate. Between these two operators they will make a good team to operate the water plant. | 16 | none |  |  |  |  | none | No |  | No |  | No |  | No |  | No | Alternate operator pumped and treated water | Operator | [9 empty] | N/A | Other Documents | 2017-02-02 10:04
RMWTR-1594 | DEC | Nikolaevsk | Kevin Schoneman | 2016-12-13 | 2016-12-13 | Routine | [5 empty] | No |  | Name: Floyd Murphy Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Sean Lee Title/Position: VSW Engineer Accompanied By? Yes Telephonic Contact? No | Name: Vasily Yakunin Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Chris Brahanam Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | [6 empty] | Site visit with community RMW Floyd Murphy and VSW Engineer Sean Lee. Discussion of Preliminary Engineering Report | I accompanied RMW Floyd Murphy and VSW Engineer Sean Lee to the village of Nikolaevsk on Wednesday Dec.13. We arrived in Nikolaevsk at approximately 1330 after our visit in Ninilchik. Floyd was able to call the operator Vasily Yakunin and ask him to meet us at the Water Treatment Plant. Vasily arrived at the water plant and Floyd introduced me to him after the introduction Vasily gave the group a tour of the Water Treatment Plant. We all then proceeded over to the office to discuss the Preliminary Engineering Report that VSW Engineer Sean Lee would be working on for the community. Floyd and I talked to Vasily about some of the training opportunities coming this year for both him and the new trainee he has been working to break in at the water plant. Floyd, Shawn and I headed back to Homer for the night. As we were preparing to depart Nikolaevsk we were able to meet briefly with the back up water operator Chris Brahanam. | 0 | None noted on this visit. |  |  |  |  | None noted. | No |  | No |  | No |  | No |  | No | Operator requesting energy audit. | Engineer | [9 empty] | Attachments | Other Documents | 2017-02-13 09:05
RMWTR-1595 | YKHC | Alakanuk | Billy Westlock | 2017-02-02 | 2017-02-03 | Other | $47 |  |  |  | Personal snogo | Yes | 40 miles | Name: Kolt Garvie Title/Position: Electrician Accompanied By? No Telephonic Contact? No | Name: Cyprian Augline Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [8 empty] | Assist troubleshoot electrical panels also remove old contacts and install variable frequency drives for all the pressure pumps. Also troubleshot the holding tank level indicator. | I arrived into alakanuk where I met up with Kolt Garvie and wpo Augline. We started to remove the contacts and old vfd for the pressure pumps and installed new vfd's on all the pressure pump panels, now all the pressure pumps are in good running order. We also tried to get the holding tank level indicator to work again but found that the transducer is burnt out most likely from ice formation damaging the internals. With all what we did until the next trip Kolt the anthc electrician will return again at a later date I departed for emo at about 3 p.m. | 8 | Need to work on a few more panels that need repairing from multiple brown outs that damaged the contacts. |  |  |  |  | None at this time | No |  | No |  | No |  | No |  | No | None at this time | Other | [9 empty] | N/A | Other Documents | 2017-02-06 17:19
RMWTR-1596 | DEC | Voznesenka | Kevin Schoneman | 2016-12-13 | 2016-12-13 | Routine | [5 empty] | No |  | Name: Sean Lee Title/Position: VSW Engineer Accompanied By? Yes Telephonic Contact? No | Name: Floyd Murphy Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Wlas Reutov Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Zack Reutov Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [6 empty] | Routine visit and accompany VSW engineer Sean Lee to discuss PER with the operators. | VSW Engineer Sean Lee, RMW Floyd Murphy and I departed Homer Wednesday December 14 for Voznesenka we arrived at the Water Treatment Plant and were met by the plant operator Wlas Reutov. Wlas explained that Zack Reutov was unable to meet with us at this time but would join up with us later in the morning. Sean started off by explaining the objective for his visit. Wlas stated that there had been some mention in the past of cleaning of the water storage tank in the past couple of years. Wlas stated that he was under the impression that the original project was to include a second water storage tank. Sean said he would follow up with the original project and look into that further. Wlas also brought up that the water storage tank had never been cleaned and he was concerned that the community would run out of water during the tank cleaning process. We all went inside the Water Treatment Plant to continue the discussion, Wlas stated he would also like to reply to the ADEC Drinking Water Department as to well #6-b this well has been out of commission due to a plugged well screen for quite some time. Wlas would like to clean all three well in the near future. We all discussed some of the corrosion and heat problems in the plant. Wlas told us that they had repaired the boiler several times in the past few years as well as repairs to the Toyo Stove in the shop and he believed that corrosion to the electrical components seemed to be the biggest problem. The operators feel that the Toyo is less expensive to operate with fuel consumption and annual maintenance cost. The operators also believe that the air scour compressor and the back wash pump are under sized and both of them should be bigger. Sean stated he would check with the filter manufacture as a follow up. We then decided to go on a tour of the community to look at some of the thoughts of the operators and community for distribution system expansion. When we arrived back at the plant we were joined by Zack Reutov, we filled him in about some of the things we had discussed in the morning. Zack said that he has some relatives in Katchemak Selo and that the opposition to chlorine in the drinking water may be easing some in the community, Zack also said there was some interest in hooking up to the Voznesenka water system. Both of the operators asked Sean what he thought it might take to insulate the water storage tank. Sean said he would look into it and get back to them with so cost estimates. There was also some discussion about the community watering point which Sean said he will follow up with. We decide it was time to head back to Homer for Sean to catch the evening flight back to Anchorage. Floyd and I overnighted in Homer and back to ANC the next morning. | 0 | Boiler in the WTP is not operational. |  |  |  |  | No back up heat source for the WTP | No |  | No |  | No |  | No |  | No | Back up heat source for the water treatment plant in the event the Toyo heater fails. | RMW | Alternate storage area for the salt for the Miox system. | [8 empty] | Attachments | Other Documents | 2017-02-13 13:45
RMWTR-1597 | DEC | Igiugig | Kevin Schoneman | 2017-01-10 | 2017-01-13 | Routine | [5 empty] | No |  | Name: Beth Layton Title/Position: City Administrator Accompanied By? No Telephonic Contact? No | Name: AlexAnna Salmon Title/Position: Tribal President Accompanied By? No Telephonic Contact? No | Name: Sandy Alvarez Title/Position: Utility Clerk Accompanied By? No Telephonic Contact? No | Name: Dave Hostetter Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Sheryl Wassillie Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: Karl Hill Title/Position: Tribal Council Member Accompanied By? No Telephonic Contact? No | Name: Halay Turning Heart Title/Position: Other Accompanied By? No Telephonic Contact? No |  |  |  | Routine Site Visit and meet with the operators. Faucet exchange program. | Igiugig Trip Report I arrived in Igiugig on Wednesday afternoon on Jan. 11, the trip was originally planned for my arrival on Monday but due to flight delays and cancellations. I was greeted at the airport by Beth Layton the Village Administrator and Sheryl Wassillie the back –up water operator. After dropping by bags off at my room we then went to meet briefly with AlexAnna Salmon at the Council Building. We briefly discussed some of the goals of my visit. Beth and I then drove over to the Water Treatment Plant to meet briefly with Dave Hostetler. Beth introduced Dave and I, Dave gave me a quick tour of the plant and the washateria which is directly next to the water treatment building. Beth had to get back to the village office to finish out her day. Dave and I made arrangements to meet back at the water plant the next morning. The next morning I met with Dave at the Water Treatment Plant with Dave, we started off by looking at a couple of issues that he was looking at in the plant. First of which was the waste heat exchanger for the heat loop to the Water Storage Tank, the circulating pump appears to be working and the water in and out of the unit does indicate a temperature rise of on average 4 degrees Fahrenheit. They have not experienced any freeze problems with the loop or the tank, but both Dave and I felt like it should be more of a temperature gain with the outside temperature being -10 that morning. I told Dave that I would check with the engineer as to what the temperature gain is expected to be. The next issue that they are experiencing is a small amount of Anthracite from the filters getting caught in the seat of a couple of the valves on the filters. Mainly valve number 6, both the operator and I believed this may have been mostly from startup and should not be a persistent problem hopefully. I will check to see if the valves can be repaired or rebuilt. Another area of concern for the operators is the tank level alarm, when the tank is filled and reaches the filled level the horn in the plant sounds. Apparently this problem for whatever reason is less prevalent than at the time of plant startup. For the remainder of the morning and early afternoon Dave went through the plant startup with me. We went through a back wash on both filters. Did the daily water analysis and readings logged the readings and filled the Water Storage Tank. Dave also gave me a tour of the power plant and showed me some the new monitoring equipment and backup generator they have on hand. After lunch I walked over to the Village Office and met with Beth who was getting ready for the Village Council Meeting which was scheduled for 2:00 pm. I asked if I could sit in on the meeting, Beth said that some of the council members had asked if I would be willing to attend. During the meeting I was asked “if after the one year time period of plant and source startup would the LT-2 requirement be lifted” I stated it should be and that I would check with the ADEC Regulatory Department. The rest of the meeting covered standard village business matters. In attendance @ the meeting were Sandy Alvarez- Accountant, Beth Layton- Tribal Administrator, Christina Salmon –Bringhurst Council Member, Karl Hill- Vice President Council, and Stacy Hill-IGAP Coordinator, AlexAnna Salmon- Council President, Halay Turning –Heart- Grants Administrator as well as several community members. After the Council meeting I met with Sheryl Wassillie Backup Water Plant Operator we talk about scheduling her to take the test for her certifications in the near future and we made arrangements to meet the next morning and go over the training and certification schedule. I also met with Tony with the village maintenance department. Tony and I inventoried the faucets and supplies and went over the replacement process. The next morning I met with backup operator Sheryl Wassillie at the village offices to review the process for testing for certifications and CEU requirements. I also met with Beth Layton to discuss the visit findings. Beth gave me a tour of the village which included a tour of the school. The WTP in general is in very good condition and very well maintained. | 6 | Operators Certifications |  |  |  |  | None noted this trip. | No |  | No |  | No |  | No |  | No | Both operators will be allowed to test for certification on-site. | Community | [9 empty] | Attachments | Other Documents | 2017-02-14 14:21
RMWTR-1599 | DEC | Nikolaevsk | Floyd Murphy | 2016-12-12 | 2016-12-15 | Routine |  |  |  |  | Company Truck | No |  | Name: Vasily Yakunin Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Christopher Brahanam Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: Sean Lee Title/Position: VSW Engineer Accompanied By? No Telephonic Contact? No | Name: Kevin Schoneman Title/Position: RMW Accompanied By? No Telephonic Contact? No | [6 empty] | Introduce the VSW Engineer to the Water Operator as an informational meeting for the upcoming project | Nikolaevsk, Sean Lee, VSW Engineer, Kevin Schoneman, DEC RMW and I were met by the operator Vasily Yakunin at the water plant and gave Sean Lee, Kevin Schoneman and myself a tour of the water plant. We than continued our tour at the office where Sean and Vasily discussed the upcoming project to replace the control panels for the water treatment system. Tank insulation and other projects were discussed for the CIP list. From the Community Water System Sanitary Survey completed by Sarah Ramey on December 16, 2014, it was noted that the water line feeding the MIOX system did not have a required back flow prevention device installed. Since the survey the back flow preventer device has been installed. See attached photo Vasily should fill out the registration form and take the level water treatment 2 certification test to meet the water treatment system level II and include the $150.00 per exam fee. As we were departing Nikolaevsk, we met the back-up operator, Christopher Brahanam. He has been working with the operator to become familiar to run the plant when Vasily is on leave. The next available Introduction to Small Water Systems class I could find in this Alaska Training Coalition Calendar (op cert – Training Calendar) was for April 17-21, 2017 in Anchorage being taught by Northern Testing Laboratory. The course fee is $675.00 plus $150.00 for the State Fees per exam fees. Northern Testing Laboratory can be contacted at (907) 452-6852 or register on line at www.ntlalaska.com. This does not include transportation or lodging and meals. This would be a good class for Christopher to attend to start his certification in the water works field. We departed Nikolaevsk for Homer to spend the night. | 3 | None at this time |  |  |  |  | None at this time | No |  | No |  | No |  | No |  | No | Have Sean lee, VSW Engineer continue working with the community with the control panel replacement project. | Engineer | [8 empty] | Since the 2014 Sanitary Survey the operator has corrected issues and installed backflow vacuum breaker on the MIOX water supply line and replaced two turbidimeters. | Attachments | Other Documents | 2017-02-09 14:36
RMWTR-1600 | DEC | Anchor Point | Floyd Murphy | 2016-12-13 | 2017-02-15 | Routine |  |  |  |  | Company Truck | No |  | Name: Neal Sullivan Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Dorothy Flint Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Wayne Flint Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: Sean Lee Title/Position: VSW Engineer Accompanied By? No Telephonic Contact? No | Name: Kevin Schoneman Title/Position: RMW Accompanied By? No Telephonic Contact? No | [5 empty] | Introduce Sean Lee, VSW Engineer to the community operators and assist operators as needed | Kevin Schoneman, DEC RMW, and I stopped at the Anchor Point Water Treatment Plant around 1:00 pm and met the new operator Neal Sullivan. Neal has worked for the Mat-Sue School District as the main maintenance person and had retired from that position. Neal is familiar with the Preventative Maintenance (PM) system and has been working on the Anchor Point PM Plan. He has tightened all the electrical connections in the control panels and added anthracite to filter # 2 to bring it to the same level as filter # 2. Water filtration has improved since adding the anthracite according to Neal has been working in the water plant since around July1st. Neal had some brass nipples leaking water he decided to replace the nipples, during the replacement he noticed that the nipples had corroded, the nipples were on the water flow metes. He replaced all the brass nipples on the meters, this problem is most likely caused by erosion corrosion, water slowing fast before and after the water meters. Wayne Flint, back up operator was also present during our visit. Neal has been working at the Anchor Point water plant since around June 1, 2016. After spending the afternoon with Neal we departed for Homer where we spent the night. Before departing we made arrangements to stop by Anchor point the following morning so we could introduce Sean Lee the DEC Engineer assigned to Anchor Point to meet the operators and for him to inspect the facilities and observe any problems or wishes for the community. Kevin and I headed to Homer to spend the night and to meet Sean Lee, DEC Engineer the following morning. The following morning Kevin, Sean and I went back to Anchor Point. Sean Lee was introduced to Neal Sullivan, Dorothy Flint and Wayne Flint operators of the water treatment plant. They shared their concerns to Sean from the engineering and operational stand points. One of the main concerns was that the water filters were having to be backwashed twice per day with the amount of water usage and causing the backwash lagoon to become filled. Neal also showed Sean, Keven and I where the community would like expansion of the water line to encompass more customers to the water system.We departed Anchor Point for Ninilchik | 3 | None at this time |  |  |  |  | None at this time | No |  | No |  | No |  | No |  | No | VSW engineer work with community on CIP issues | Engineer | [9 empty] | Attachments | Other Documents | 2017-02-09 14:57
RMWTR-1601 | DEC | Chenega Bay | Floyd Murphy | 2017-01-09 | 2017-01-14 | Routine |  |  |  | Airplane |  | No |  | Name: George Eleshansky Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [9 empty] | Assist operator replacing chlorine chemical pump | January 9 – 14, 2017 I departed Anchorage for Chenega Bay on Alaska Air Transit 9:30 am arriving around 10:10 am. I got a ride from the school personnel who delivered me to the operator’s George Eleshansky residence. I met with George and inquired about any problems he may be having at the water treatment plant and equipment, outside of needing the chlorine pump replaced. He explained the Air Scour Pump for the backwash had seized again. Water was infiltrating the compressor over time, the 4 inch Bray valves, series 21 with series 4 gear actuator from the filter should be replaced to correct this problem. The Bray control valves 4 inch with 8 bolt flange are not seating anymore and water is seeping back to the air scour. The hose bib valve should be opened after every use to keep water from seizing the blower. We went to the water plant, there was chirping noises coming from different areas of the water plant office area. I discovered that the smoke detectors were removed and the batteries were in need of replacement. The batteries were removed and solved the chirping noise. The operator should order new 9 volt batteries for the smoke detectors and reinstall them. These should be available from John Sims ANTHC, AUSC, at 729-3525 We than inspected the air scour blower for the backwash procedure. The blower had filled with water and was seized. The air blower is a Gardner Denver, Sutorbilt Model: GABMDRA, Serial: S318377. 3 inch right hand rotation, central timed with Lip Seals. The hose bib before the compressor was open to drain the compressor, the water in the compressor would not drain all the water from the compressor. I removed a hose on the discharge side of the blower. I removed a piece of hose and this allowed the water to drain from the blower. The blower was still ceased. After trying to get it to move, we scrapped the rust accumulation on the lobes of the blower with a rag, removing the rust allowed the blower to be able to rotate normally. We ran the pump to get rid of any remaining water in the blower and lines. The Blower is available from: Gardner Denver Sutortbilt, Inc. 1800 Gardner Expressway PO Box 4024 Quincy, Il 62305 1-217-222-5400 Also they can be found on the website: Gardner Denver at a cost of around $ 1505 plus any shipping fees. Because of inclement weather I was not able to depart Chenega Bay as planned on Wednesday the 11th of January as planned. I asked George if there were any additional problems with the water or wastewater systems that I could assist with him with. George said that he did not have any other additional problems. We spent time at the water plant making sure the air scour blower was operational and the chlorine pump would operate normally. I departed Chenega Bay on January 14th Alaska Air Transit around 4:20 pm arriving in Anchorage around 5:25 pm. | 18 | The Gardner Denver Sutorbuilt backwash air scour pump keeps filling with water. Spare pump replacement around $1500.00 |  |  |  |  | Other than air scour pump none. | No |  | No |  | No |  | No |  | No | Order spare air scour pump | Community | [9 empty] | Attachments | Other Documents | 2017-02-09 15:20
RMWTR-1602 | DEC | Gulkana | Floyd Murphy | 2016-12-19 | 2016-12-20 | Emergency |  |  |  |  | Company Truck | No |  | Name: Clint Maxim Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: John Dye Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [8 empty] | Assist community operators thaw water supply from WTP to WST | 11/19/16 I departed Anchorage for Gulkana around 1:30 pm arriving in Gulkana around 5:00 pm. I was met by Clint Maxim the past operator. Shortly after my arrival the operator John Dye showed up to assist with thawing the supply line to the water storage tank. . Clint had been working with the commercial water delivery service to add water to the water storage tank. Water added to the tank was keeping the distribution from being compromised. Before Clint left he stated he would be available if we needed assistance thawing the water line. I had been working with the operator John Dye over the weekend to resolve the frozen raw water line over the past several days telephonically. After several days the raw water line had thawed using the heat trace designed for that purpose. Upon the raw water line being thawed the operator started to make water, he thought. It was discovered that the make-up water / backwash water supply line had also frozen due to not being used for several days. This line does not have a thaw system provided to the line. Previous to my arrival John had tried to thaw the supply line with warm water and 3/8 inch Quest pipe and pump the pipe would not go around the 90 degree fittings in the water supply line. The water line is 170 feet total between the water treatment plant and the water storage tank. John was able to get the pipe in around 30 to 50 feet into the line. John informed me that he did have a hot box and jetter for thawing sewer lines but did not have a dedicated jetter line for thawing water lines only for the wastewater lines. Water to the water storage tank and distribution was being added through a water truck service at an added expense to the community. It was also discovered that the add heat to the water storage tank was not operational because the two Grundfos circulation pumps had failed. I called several vendors in Anchorage but a replacement pump was not in stock but could be ordered and made available in a couple of days. John had the Hot Box and jetter set up inside the water treatment plant near the exhaust fan to expel the exhaust from the equipment. Prior to energizing the equipment we also opened the doors for fresh air into the plant. John removed a valve as an access point to use as the thaw point for jetting the frozen water line. John was instructed on the use of the jetter and using the jetter process to thaw the line and add heat to the line as it was being thawed. Once we had everything connected we started thawing around 6:30 pm and had the line thawed by 9:30 pm. The add heat line was not thawed because it would most likely freeze up before the replacement pump arrived on site. The Quest pipe setup could be used to thaw the add heat line to the water storage tank. I assisted the community locate a add heat circulation pump. The price difference between two vendors was $303.69 for the same pump. The new pump was not in stock with either vendor and was ordered. Grundfos: New part number 98961763 the original pump was obsolete. 12/20/16 I inspected the Weil McLain Ultra Oil Boilers with Geckett Burners. The boilers are controlled by a Tekmar 268 controls. Boiler #1 was set on hand. Boiler #2 was in hand also but was not operating. I called ANTHC, DRUMS, Pierre Costello for assistance, however with the holidays and people on leave makes it difficult to contact tech support during this time of year. I also talked with my supervisor about the Tekmar system. There being 1 boiler on line meeting the demand of the water treatment plant, I departed Gulkana for Anchorage around 1:45 pm arriving around 6:00 pm. I delivered the equipment to the RMW shop and brought the truck back to the office. Recommendations: The water storage tank is a 100 thousand gallon tank, it is operated between 2 feet to 12 feet, according to the O & M manual. This is half the capacity of the tank. The tank is leaning and needs to be replaced or releveled so the entire tank can be used for fire flow protection and meet the needs of the community. In the current configuration the tank should be used in the 10 to 12 foot level. This will help the tank from getting to cold and keep a level that somewhat helps with fire protection. Because of the tilt, and it is suspected that if the tank is filled completely that it may fall over. The tank needs to be replaced or releveled for full use of the tank for fire flow and community demand. I spoke to Mr. Martin Suzuki, DEC certifications about the operator certifications. The Gulkana Village Water Treatment is a class 2 system and the operators should meet the certification of the water system classification. They should attend classes or conferences when they become available to get the 3 CEUs to maintain certification and take the level 2 test for Water Treatment to meet the System Type/Class. John Dye has certifications in Water Treatment Provisional and Water Distribution with an expiration date of 12/31/2017 for both certifications. John is eligible to upgrade his WT Provisional to level 1 and take the level 2 WT test after filling out the proper applications. He has 7.60 Core CEUs and meets the required CEUs to maintain certifications. Samson Frank has WT Provisional certification. Clinton Maxim has certifications in Water Distribution Provisional and Water Distribution Provisional. Clinton’s certification in Water Distribution Provisional expires 12/31/17 and needs 3 CEUs before the end of the year of 2017. This is accomplished by attending classes in the water treatment field or attending conferences that give CEUs after attending seminars. Clinton Maxim also has certification in Water Treatment 1 set to expire 12/31/16. The Alaska Training Coalition Calendar available on the web: https://dec.alaska.gog/water/opcert/TrainingCalendar.htm as the information on training classes. | 6 | The Circulation pump for add heat to the water storage tank had failed |  |  |  |  | Add heat system pumps failed replacement pumps are available from Hasco at 500.00 each | No |  | No |  | No |  | No |  | No | Community to work with ANTHC to correct WST add heat design | Engineer | [9 empty] | Attachments | Other Documents | 2017-02-09 15:46
RMWTR-1603 | YKHC | Anchorage | Bob White | 2017-02-08 | 2017-02-10 | Training/Meeting | $356 | $120 |  |  | Alaska Air | No |  | Name: Brian Lefferts Title/Position: Environmental Health Officer Accompanied By? Yes Telephonic Contact? No | Name: Tom Bobo Title/Position: Other Accompanied By? Yes Telephonic Contact? No | [8 empty] | To Present at the "Assessing and Improving Village-level Financial, Management and Technical Capacity" workshop. | 2-8-2017 I arrived in Anchorage at 2210 hrs and headed to the hotel. 2-9-2017 I arrived at the "Assessing and Improving Village-level Financial, Management and Technical Capacity" workshop. we spent the day listening to presenters as well as presenting. | 0 | The workshop lacked a lot of critical people who could make a difference in the policies and implementation. |  |  |  |  | None | No |  | No |  | No |  | No |  | No | None | Unknown | [9 empty] | N/A | Other Documents | 2017-02-13 07:44
RMWTR-1604 | YKHC | Tuluksak | Bob White | 2017-01-31 | 2017-02-02 | Routine |  |  |  |  | YKHC Truck | No |  | Name: Michael vincente Title/Position: Environmental Health Officer Accompanied By? Yes Telephonic Contact? No | Name: Kristy Napoka Title/Position: Utility Clerk Accompanied By? No Telephonic Contact? No | Name: Carl Peters Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Jarha Peters Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [6 empty] | To remove and replace the sand in the filter. | 1-31-2017 I drove up to Tuluksask on the river with Michael and the supplies we would need to remove and replace the media. When we arrived the filter had not drained down enough to start removing media so we started to sift the new media to remove polymer balls. After lunch we were able to start removing the media. it took a significant effort to remove media especially the further down we got. the last 18" of media above the under drain required a pick to bust up to remove. Once we removed all the media we had to bust out the damaged under drain. at 1800 hrs we decided to head back to Bethel to pick up under drain supplies and return in the morning. 2-1-2017 We drove back up the River to Tuluksak and started chipping concrete around the bulk head inside the filter so we could install the new under drain. once we were able to put on the new T we started assembling the under drain. Once we had the underdrain installed we started bedding it with gravel. We then built up the media installing all the green sand and Anthracite up to the appropriate level. We then added KMnO4 to regenerate the media and closed up the filter for the night. I drove back to Bethel. 2-2-2017 I returned to Tuluksak and we were ready to backwash the filter. We backwashed at 120 GPM for the first time in years. After completing the backwash we started the transfer and we were able to get about 17 GPM through the filter. With the system working I gathered up my supplies and headed back to Bethel. | 20 | The filter media was supper clogged with Iron to the point that the gravel had turned to one solid chunk of iron. | The transfer pumps will not build adequate pressure I think they may be damaged from cavitation. |  |  |  | Holes in the floor. | Yes |  | No |  | No |  | No |  | No | Check with pump supplier about Transfer pump rebuild kit. | RMW | Backwash at each filter run with at least 100 GPM of flow. | [8 empty] | N/A | Other Documents | 2017-02-13 08:51
RMWTR-1605 | DEC | Atka | Steve Evavold | 2017-01-29 | 2017-02-03 | Routine | $1,020 | $330 |  |  |  | No |  | Name: Dennis Golodin City Clerk Title/Position: Accompanied By? No Telephonic Contact? No | Name: Michael Swinney Water Plant Operator Title/Position: Accompanied By? No Telephonic Contact? No | [8 empty] | Training water plant operator on plant operations, maintenance, and daily data and reporting requirements, | 1/30/17. Arrived in Atka at 1400 and met with the water plant operator, Michael Swinney. Initial observations in the plant showed the plant to be clean and organized. The O&M manual, backwash instructions, and daily records were up to date, but missing data due to monitoring instrumentation failures. As Michael and I had discussed via email (only communication mode available), the turbidimeters, SCD (Streaming Current Detector), and polymer pump, were giving erratic numbers and having operational problems. The raw water turbidimeter was displaying 0.001 ntu, combined effluent turbidimeter was 0.200, and the SCD process value was steady at 78.0. We cleaned both 1720E HACH turbidimeters; the CFE turbidimeter calibrated to the 20ntu standard the second time through the menu. The 1720E for the raw water did not take calibration after 5 efforts. I had Michael disconnect the head and remove the protective cover assembly to expose the circuit board. There were no loose wire connections, but I saw the wiring harness on the underside going to the light bulb had a buildup of green corrosion on the contacts. I sprayed some cleaner on it and brushed it clean. Michael reassembled the head assembly, installed a new light bulb, attached it to the SC200 controller, and placed it back in the reservoir. The turbidimeter took the calibration and started displaying 0.700ntu’s for raw water influent. I asked Michael to remove the plunger assembly from the SCD. Milton Roy accepts the use of “Comet” no pumis/detergent for cleaning the staining and scum buildup on the probe/plunger. I had him use a small round brush to go down into the plunger housing to clean two contacts on the inside wall for better operation. The clevis pin was showing signs of wear and the lower bearing on the SCD rotating armature was seized. We replaced the bearing; should be done every 2years or as necessary. We reassembled the SCD and I explained the jet wash function for the plunger and suggested weekly use. I reprogrammed the set point to -2.00 to lower polymer dosage but saw no response from the polymer pump. I turned the SCD to “Manual” and adjusted the stroke to 100% and still didn’t see a response from the polymer pump. I looked at the LED display for the LMI chemical feed pump and saw that the setting was for “Internal” source(meaning manually controlled), and not set for “External” source, as is needed to accept a 4-20ma signal from the SCD controller. Michael had been operating the polymer feed “manually” since he started, which was partially the reason for erratic treated turbidity. The fluctuation in raw water turbidity gives manual operation of the polymer add system the capability to under or overdose the polymer. I set the polymer pump to external source and got a signal from the SCD, the pump slowed down and was operating around a 7ma signal. The turbidity numbers were acceptable when leveled out. I had Michael start sending water to the tank, it was down to 8 feet. Chlorine residual to the tank via a composite sample tested at 5.0 mg/l. In the morning treated turbidity had risen to 0.3ntu. I had Michael shut down the plant and start a drain down process for a back wash. While the filters were draining, we left the plant to identify 5 sites we needed for the overdue Lead and Copper sampling. Michael ran water for 5 minutes at each site and taped off the faucets reminding the residents not to use water until we returned 6 hours later. I had Michael extend the air scour and backwash cycles to breakup and expand the media in the filters. I suspected the filters may be somewhat cemented by the polymer. There was some mud ball accumulation also. When done with the backwash we “filtered to waste” until treated read 0.2ntu. By the end of the day, treated turbidity was down to 0.05ntu’s. In the morning CFE turbidity had dropped to 0.026ntu’s, and the water tank was up to 18 feet. Instrumentation, filters, and pumps were operating as designed. I brought blank operator reports, a template for a Preventive Maintenance Plan, and a city map to design a sample site plan. We discussed entry point and end of distribution sample sites, and where to take a raw water sample for the upcoming LT2 ESWTR requirement. We discussed the monthly coliform sample and where to take those samples. I said I’d get him the information for the Dutch Harbor testing Lab, if not we’d be sending the samples into Anchorage. Heavy rains and snow melt "funnel" grasses and other organics down into a small dam impoundment where a submerged Johnson screen collects water for the plant. Cleaning off the screen is a daily chore to keep the water flow to the plant. The impoundment itself is rotting. Most of the wood supports and planking are falling apart. When the structure fails, the stream will be flowing below the screen. Repairs up to now have been some plywood nailed to the outside of the supports. The dam is in eminent failure status. I looked at Michael’s log entries and calculated water flow from the WST. The first 3 weeks of January the plant produced about 19,500 GPD. The week before my arrival production averaged 26,800 GPD. This was during a cold snap and could be attributed to people running water for pipe protection, or possibly a leak. I asked Michael to document water usage on a daily basis as this is where he would see the first indication of a leak in the system. The rains and snow melt runoff while I was there showed a range of raw turbidity from 0.70 – 2.20 into the plant. We discussed the need for a full 130,000 gallon water tank for the ability to shut down the plant for a couple of days at times of high turbidity. We backwashed, cleaned and calibrated turbidimeters a couple more times, and again cleaned and discussed the SCD operation. Michael picked up on all the operations and maintenance needed for the plant very quick and will be in contact as needed. There is no phone contact available currently, only email. | 24 | The small undersized impoundment for water is in eminent failure status. As the only source of water for the community, attention to this critical component is needed. |  |  |  |  | A new reservoir is needed | Yes |  | No |  | No |  | No |  | No | Another trip should be scheduled to coincide with water source inspection and further OJT with operator. Possibly fall 17. | RMW | [9 empty] | Attachments | Other Documents | 2017-02-14 15:22
RMWTR-1606 | YKHC | Napaskiak | Bob White | 2017-02-13 | 2017-02-13 | Routine |  |  |  |  | YKHC Truck | No |  | Name: Michael vincente Title/Position: Environmental Health Officer Accompanied By? Yes Telephonic Contact? No | Name: Ken Larson Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Nelson Egoak Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [7 empty] | Teach WPO Egoak to rebuild LMI Pumps. Rewire electrical circuit that caught fire. Meet the new water plant operator for the City. | When we arrived at the tribal water plant the building felt cold and there was ice on the floor in spots. WPO Egoak was setting the jetter set up to clear the drain line. We helped him trouble shoot a problem he was having with the nozzle, once we had it operating correctly we pulled the LMI pumps and brought them to the bench to rebuild. I showed WPO Egoak how to verify the kits were correct before opening them. Once we had the correct kits with each pump we started the disassembly and cleaning. With all the pumps disassembled we started replacing seals and check valves. With all the parts replaced we reassembled the pumps and turned to replacing the foot valves and injectors. With the pumps installed we turned to the electrical fire and unit heater that needed trouble shooting. We tried the Unit heater motor but could not get it to work even though we had power to the motor. After troubleshooting we found that the neutral wire was tied to the outlet that had caught fire recently. We rewired the junction box that had caught fire and that restored the neutral to the unit heater. After we replaced the thermostat we had the heater working as we wanted. The building started heating up soon after. We then headed to the city Water plant and washeteria. WPO Larson and I started talking about the Washeteria and how things were working and what things weren't. We took a quick look at a couple items that needed fixing and I gave him some direction on what the problems probably were. We then headed to the water plant to see how things were. We discussed some things that changed since his last time working in the water plant. We found some area that needed work and discussed keeping the water level in the tank high enough to keep it working correctly. | 6 | The Tribal Water Plant has serious heating issues that are improved after we fixed the unit heater but the floor insulation has failed and must be replaced. | The City water plant water tank is dangerously low. | The building froze during the WPO change over little damage but a dangerous situation. | The city has failed to get parts and chemicals in a timely manner with some parts taking months to get. |  | The backwash drain freezes at the tribal water plant. | Yes | The insulation in the floor is water logged and completely ineffective. | Yes | the day tank at the Washeteria needs a new fuel pump. | Yes | The foundation under the tribal Water Plant is failing and needs reinforcements. | Yes |  | No | The city needs to order parts and chemicals so the plant can start producing water. | Community | The Tribe needs to repair the insulation and soffit under the water plant. | Community | This summer the heat trace on the back wash drain should be replaced at the Tribal water plant. | Community | [5 empty] | N/A | Other Documents | 2017-02-14 08:49
RMWTR-1607 | DEC | Seldovia | Kevin Schoneman | 2017-02-09 | 2017-02-09 | Other |  |  |  |  | State Truck | No |  | Name: Steve Evavold Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Jeff Beatty Title/Position: VSW Engineer Accompanied By? Yes Telephonic Contact? No | Name: Steven Hebnes Title/Position: Consulting Engineer Accompanied By? Yes Telephonic Contact? No | Name: Jeremiah Campbell Title/Position: Construction Staff Accompanied By? No Telephonic Contact? No | Name: Scott Alkire Title/Position: Plumber Accompanied By? No Telephonic Contact? No | Name: Tyler Tucker Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Randy Bond Title/Position: Water Operator Accompanied By? No Telephonic Contact? No |  |  |  | Construction inspection. | On the morning of February 9, 2017 I departed Anchorage at 6:00 AM to Homer and then on to Seldovia. Also making the trip was RMW, Steve Evavold and Construction Inspector, Jeff Beatty. We arrived in Homer at 1030 and went to Smokey Bay Air for our flight to Seldovia, when we arrived at the terminal we met up with Steve Hebnes, Construction Engineer for CRW. After a slight weather delay we departed for Seldovia at 11:45. We all were met in Seldovia by the Construction Superintendent, Jeremiah Campbell. We left the airport and drove to the location of the old (filter building). Jeremiah explained the work that had been taking place at this site. The new transformer and meter base had been installed with only the final connections needing to be made by the electrician after he arrived back at the job site. Jeremiah also pointed out where the area had been excavated for the Clarifier Effluent collection. In the future when the clarifier requires cleaning, it will be drained into a geo-tube in this area. We also discussed the absence of water seeping from the hillside since the 10” TWS transmission line had been decommissioned and repurposed to an electrical carrier conduit. We then then continued our visit by moving up to the construction site at the new Water Treatment Plant. Much progress has occurred on the project since my last visit in late August, at that time the work on the structural frame work was just getting started. At this time the Water Treatment Building is almost complete. The fuel tank and the concrete pad for the back- up generator are in place as well as the electrical disconnects. The work site is very well organized and clear of debris. Most of the group then continued on to inside the WTP, where several of the construction crew were in the process of adding the gravel layers under and over the filter laterals in the first of the three pressure filters. The filter laterals had been installed the day before we arrived and appeared to be in the correct configuration. Jeremiah mentioned that they were beginning to notice that as they were adding the different layers of gravel some of the measurements did not seem to coincide with the manufactures instructions. It was suggested that maybe adding water to the layers as they are installed may aid in settling the bed as it is installed. The group also discussed the installation of the anthracite layer, Steve Evavold suggested that there would be a substantial amount of dust and that it would be beneficial to have the filter face piping complete so that the media could be rinsed and back washed several times during the loading of the filters. We also looked at the office area/ lab and bathroom, this area appears to be 80% complete. We also looked at the mechanical room as well as the chemical room. The two Water Operators, Randy Bond and Tyler Tuckers arrived at the WTP we talked about the progress of the construction, we also talked briefly about possible dates to make a trip to Port Graham to meet with the operator there and look at the plant there. We also discussed the amount of chlorine that they are using on a daily basis. The operators explained that they are using one pail of chlorine per day, before the water storage tank reconfiguration and cleaning they used one half that amount. The operators did discuss this with the engineer Steve Hebnes and he explained that CRW is aware of this and is working on a solution. We also discussed the fact that there was possibly more than one contributing factor to this problem. By this time it was time for our flight back to Homer, and then on to ANC with brief stops in both Anchor Point and Ninilchik. Steve, Jeff and I arrived in Anchorage@ 9:00PM | 0 | I believe ballards should be placed around the road side of the electrical transformer and meter base at the (old filter bldg.) | Extensions on the valve risers at the Clarifier Solids Removal Area. Markers on these risers so that they would easily be found several years from commissioning. | Weather hoods over both the meter base and service disconnect at the filter bldg. and at the water treatment plant. | Stair access to the top of the chlorine mixing tank. | Back flow preventer on the hose bib at the south entrance of the WTP | Back up heat source for the WTP | No | Rain Hood over the day tank vent on the east side of the WTP. | No |  | No |  | No |  | No | Continue to meet on a biweekly basis. | Construction Project | Operator Orientation in Port Graham | Construction Project | Consider adding weather protection to outside electrical connections. | Construction Project | [5 empty] | Attachments | Other Documents | 2017-03-02 11:15
RMWTR-1619 | YKHC | Grayling | Bruce Werba | 2016-11-08 | 2016-11-09 | Emergency | $1,100 | $96 | $0 |  | Ak Scenic Air | No |  | Name: Mark Onalis Title/Position: Other Accompanied By? Yes Telephonic Contact? No | Name: Brandan Sandei Title/Position: Water Operator Backup Accompanied By? Yes Telephonic Contact? No | Name: Ryan Painter Title/Position: Water Operator Accompanied By? Yes Telephonic Contact? No | [7 empty] | To assist Water Plant Operator (WPO) and Ak Pump and Supply technician with identifying problems with both community lift stations. | Travel was completed Novewmber 8 to Grayling. Once into Grayling I met the WPO's at the water plant. I arrived with Mark Onalis. We immediately went to south lift station and checked the programming on pump two phase inverter. Upon further inspection we identified a float control problem, the float was tore off. After the replacement of the floats we were able to then get the lift staion operating but programming bugs needed to be reapired. After all was done the lift station ran as designed. We then went to the north lift station and found that pump one was inoperable. After troubleshooting the control panel, we found that the voltage monitor was functioning incorrectly. With a spare on hand we replaceed the voltage monitor and ran pump one, it ran normal again. Lift station maintenance was then completed by cleaning the interior of the lift station by washing it down, this process for this community should be done at least once week, twice is even better. We called it a day at 1930 hours, and went over to the city hotel. We began the day by inspecting both lift stations, both were operating normal. The next task was to complete inspection of all the components in the water plant , all six circulating pumnps were running normal. With all tasks performed we called for a charter pick up, as the scheduled passenger flights are very sporatic. | 13 | The water plant components are opertating normally, but the condition of the water plant structure is rotting at base of foundation, along with the plumbing that has been cobbled together, a new facility would be nice to get out of the flood plain. |  |  |  |  | None at this time. | No |  | No |  | No |  | No |  | No | Make sure WPO's are washing both lift stations down on a weekly basis. | Operator | [9 empty] | N/A | Other Documents | 2017-02-22 09:52
RMWTR-1620 | YKHC | Kwigillingok | Allan Paukan | 2017-01-26 | 2017-02-01 | Emergency | $1,320 | $288 |  |  | Ravn Connect and Renfro Alaskan Adventures, Inc | No |  | Name: John Carter Title/Position: Water Operator Accompanied By? Yes Telephonic Contact? No | Name: Darryl John Title/Position: Water Operator Backup Accompanied By? Yes Telephonic Contact? No | [8 empty] | To assist Water Plant Operator (WPO) with thawing the entire water and wastewater utilities. | January 23 the WPO called and said he needed assistance with thawing the raw water transmission line. It was froze from the last major weather system. Due to the weather and passenger load backed up at Ravn Connect, I finally made it onsite on the 26th. We began by inspecting the work performed so far to thaw the raw water transmission line. We inspected the line from the water plant to where he was currently working now, which was 180 feet from the well house, but it was thawed. We then proceeded to the old jobsite plumbing shop where we attempted to get the Mytana M80 of thiers operational, we were unable to get it to operate so I requested for an M80 and hot box along with a reel to thaw 300 foot sections at a time. We called it a day at 2000 hours. Jan 27 we began by rounding up jetter hose and reel that were onsite and brought them to the water plant to thaw. our jetter and hot box arrived and we set up our tent and started thawing up the up towards the well house, we were able to get three hundred feet into the 4" HDPE supply line and could go no further. We exposed the carrier pipe from the arctic pipe and went another 180 feet but could not go no more. Being late we drained the water main of water and called it a night at 2100. Jan 28 we began at the place where we got stuck the night before, once we reached the 180 foot mark we could not thaw anymore, again. So we backtracked and moved our water location back to the well house and thawed towards the water plant. By evening we had water all the way to the water plant, as it did not freeze all the way. In the begining after getting circulation on the raw water line, it quit immediately, We were either froze or broke on the 1 1/2" hdpe return line back to well house. While gathering our gear and taking them back the water plant we found the location of where the return line came apart on a hdpe coupling, I suspect it was the cause for the freeze up. We lost the constant heat from the circulation line. We called it a night at 2330 hours. Jan 29 we set up our tent and heater at the joint where the pipe broke. We then drained the line of all liquid. Once all components were at the same temperature we electrofused the hdpe pipe. We now had raw water circulation by 1330 hours. 1400 -1900 hours was spent thawing the water treatment plant drain line so we could produce water. 1900-0130 was spent in the water plant conducting maintenance to boilers, boiler two was going to run all night but lost the boiler during the night. Jan 30 we checked on our chemicals for the water plant and kept making water to fill the water storage tank. We then started thawing the gravity section of the forced main which was about 220 feet long. While the WPO's were thawing, I troubleshot boiler 2 and found that the igniter failed. With none on hand the WPO will have to order one. We called it a day at 2330 hours. Jan 31 today we thawed the forced main section of the wastewater collection system. The forced main was frozen 85 feet out of 160 feet. The forced main serves the washeteria. The water line also was frozen for the same amount, but the water line continues to the clinic. all frozen pipe was now thawed. We then monitored the water treatment system, where we fine tuned the treatment process. We called it a day at 2200 hours. Feb 1 I called for a charter pick up, while waiting for the charter pick up we fixed a leak on the water distribution system circulation line. I then explained to the WPO back up where were at with all the facility, the only thing left to do was to get the water storage tank level, as the guage needs to be recalibrated. The Renfro plane finally arrived about 1600 hours, I arrived back into Bethel with all our gear and brought them to the RMW warehouse. After this long trip I needed a break. | 50 | The Milton Roy Polymer pump needs a new motor, it quit working while we were out in the field thawing. |  |  |  |  | Probe needs to be purchased for water treatment train | Yes | Water plant boiler number two needs a igniter. | No | Boiler number three in the washeteria needs a new LWCO. | No | A Belimo motor needs to be purchased for the arctic entry/ office / bathroom heat. | No | HAch 1720 E needs calibration kit ordered. | Yes | Make sure the water storage tank has enough water to overcome any breaks that may deplete the water tank. | Operator | [9 empty] | N/A | Other Documents | 2017-02-23 15:17
RMWTR-1621 | YKHC | Bethel | Bruce Werba | 2016-12-06 | 2016-12-10 | Training/Meeting | $603 | $172 |  |  | Ravn Connect | No |  | Name: Brian Lefferts Title/Position: Environmental Health Officer Accompanied By? Yes Telephonic Contact? No | Name: Alyssa Gustafson Title/Position: Environmental Health Officer Accompanied By? Yes Telephonic Contact? No | Name: Robert White Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Billy Westlock Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Allan Paukan Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | [5 empty] | SDS meeting. | December 6th was travel day for all RMW attending a YKHC SDS Meeting. Dec 7th we began at 0800 with greetings and the meeting began at 0830 hours. We alphabetically went thru all YKHC area villages. We discussed items for all utilities that are in need of infrastructure and utility deficiencies. All this process took two days of meeting, we completed meeting on the 8th. During the afternoon of the 8th we went down to the RMW shop and looked over the gray water recycling research center. We made a parts list to purchase items to complete plumbing for the gray water stations. I checked in to Ravn and the weather didn't let me depart Bethel until the 10th, I arrived into Holy Cross about 1500 hours. | 0 | None at this time. |  |  |  |  | Could we write only one trip report for our group during these types of meeting, rather then all of us. | Yes |  | No |  | No |  | No |  | No | None at this time. | Unknown | [9 empty] | N/A | Other Documents | 2017-02-23 10:37
RMWTR-1622 | YKHC | Bethel | Bruce Werba | 2017-01-09 | 2017-01-12 | Training/Meeting |  | $144 |  |  | Ravn Connect | No |  | Name: Fred Braurman Title/Position: RUBA staff Accompanied By? Yes Telephonic Contact? No | Name: Carrie Bohan Title/Position: Other Accompanied By? Yes Telephonic Contact? No | Name: John Johnson Title/Position: Other Accompanied By? Yes Telephonic Contact? No | [7 empty] | To attend a coordination meeting with ANTHC, VSW, ADEC, RUBA and YKHC. | The meeting conducted lasted two days with discussing with all the agencies that fund projects in the YKHC region. It was a greast meet and greet for all that attended. Now we are all kind of on the same page for projects and shortcomings in the YKHC region. | 0 | None at this time. |  |  |  |  | None at this time. | No |  | No |  | No |  | No |  | No | Noen at this time. | Unknown | [9 empty] | N/A | Other Documents | 2017-02-23 11:06
RMWTR-1623 | YKHC | Quinhagak | Bob White | 2017-02-07 | 2017-02-07 | Routine |  |  |  |  | Raven Air | No |  | Name: Frank Jones Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Bill Mcdonald Title/Position: Consulting Engineer Accompanied By? No Telephonic Contact? Yes | [8 empty] | Trouble shoot well control problems. | When I arrived frank and I tried the control panel at the water plant and it would run for about 15 seconds after the pumps came on before the breaker would trip and shut the panel off. We checked voltages in the panel with it reset and found we had low voltage coming back from the river gallery. At the river gallery two of the three slant well disconnect breakers had the door interlock stem pulled out of the breaker.we could not reinsert the door inter lock mechanism as the plastic gear had broken. So we removed the interim well breaker and install them in the slant wells and we had the wells working again. Back at the water plant we everything was stable and running until slant well #3 tripped and the panel shut off again. I then called to talk over the issue with Bill Mcdonald and he suggested i try to find a spare return wire for the alarm circuit. Once I found one and changed over to it we had the system working again as it should. with the appropriate return voltages. We then replaced the mechanical seal on the transfer pump although they had the wrong one. I departed on the next flight to Bethel | 6 | The breakers were damaged by opening the panel with out releasing the latch first. | The wrong seals were purchased for the Transfer pump. |  |  |  | Transfer pressure switch has failed. | No |  | No |  | No |  | No |  | No | ARUC needs to order replacement breakers for the slant wells. | Other | ARUC needs to order correct Mechanical seals for transfer pump and pressure pump. | [8 empty] | N/A | Other Documents | 2017-02-23 15:38
RMWTR-1624 | YKHC | Bethel | Allan Paukan | 2017-01-09 | 2017-01-13 | Training/Meeting | $430 | $144 |  |  | Ravn Connect | No |  | Name: Carrie Bohan Title/Position: Other Accompanied By? Yes Telephonic Contact? No | Name: John Johnson Title/Position: Other Accompanied By? Yes Telephonic Contact? No | Name: Martin Suzuki Title/Position: Other Accompanied By? Yes Telephonic Contact? No | [7 empty] | To attend a coordination meeting at the YKHC Prematernal home. | Travel day was the 9th for all attendees. The 10th and 11th of Jan were for the coordination meeting, we began at 0800 and went till 1700. We discussed all aspects of every community in the YKHC region, from projects to permitting to operation and maintenace, along with community deficiencies. By the end of the meeting all agencies involved seen all the projects from both ANTHC and VSW in the meeting, along with a better understanding as to the state of the communities. | 0 | Hope more interagency communication will result from this meeting. |  |  |  |  | None at this time. | No |  | No |  | No |  | No |  | No | Check with village assigned engineers that need more information about the community they are assigned to. | Engineer | [9 empty] | N/A | Other Documents | 2017-02-24 07:38
RMWTR-1625 | YKHC | Shageluk | Bruce Werba | 2017-02-07 | 2017-02-07 | Emergency | $57 | $0 |  |  | Personal Snowmachine | Yes | 130 miles | Name: John Hamilton Title/Position: Water Operator Accompanied By? Yes Telephonic Contact? No | [9 empty] | To pull well pump and clean it, the well production declined. | To assist WPO with pulling well pump, the well production declined quickly. I departed at 0930 and arrived into Shageluk at 1130. We began by pulling the pump. Once pulled we cleaned the nine stage pump impellers and pump screen, along with the 1 1/2" drop pipe. By six o'clock we had it installedf and operating, but the well pressure or flow was not passing the water meter screen. The meter was taken off line and cleaned and reinstalled. The well production and pressure was now operating at normal level. I believe the quick loading of this iron build up was caused by the super chlorinating the well a couple months back. With the system operating at nomal levels I departed home at 2000 hours and arrived back into Holy Cross at 2200 hours. | 7 | The water meter needs a by pass line installed which is common in most water plants, water production wouldn't be halted and the washeteria could stay open during maintenance of the water meter. |  |  |  |  | Will order parts needed to install the by pass line for the water meter | No |  | No |  | No |  | No |  | No | Make sure the parts are ordered and the WPO notifies me when the parts arrive to complete installation of by pass line. | Operator | [9 empty] | N/A | Other Documents | 2017-02-28 10:37
RMWTR-1626 | TCC | Koyukuk | Wes Shales | 2017-01-25 | 2017-01-26 | Emergency | [5 empty] | No |  | Name: John Williams Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Alfred Dayton Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: Kay Dee Harris Title/Position: City Administrator Accompanied By? No Telephonic Contact? No | [7 empty] | Assist the community in repair/replacement of damaged/failing piping or components thereof as well as replacement of a supplemental heating system for the lower level of the washeteria/water plant. | Prior to my arrival a recent deep freeze in the weather caused the sewer system to freeze up at the outfall to the sewer lagoon. In addition the water plant piping to a pressure tank froze and burst. John and Alfred were able to thaw out the frozen outfall pipe. That condition allowed use of the hooked up building plumbing systems once again. They also were able to isolate piping to the pressure tank and stop the leaking and clean up the water. Also, just prior to my arrival John and I discussed what he could do to increase the heat in that lower area of the building. I had him loosen up linkage at a belimos controlled hydronic heating valve that was fastened too tight and not allowing full flow to a ceiling mounted unit heater. We also talked about him flushing out the rarely used fuel line that supplied heating fuel to a supplemental heat toyo stove. While being flushed “gunk” and air exited the line. John and Alfred also borrowed a toyo stove out of another building temporarily to replace the unreliable beat up unit currently there at that lower level area. Freezing conditions at the building were an result of failed heating system components as well as a massive inrush of cold air from the holding tank overflow vent that is piped so that it drains directly outside of the building. Although it had thawed prior to my arrival the Operators said that a large block of frozen ice/condensation actually formed inside the tank at above the normal high water mark of the water storage unit. I suggested that heat trace wrapped around the venting and/or insulation would help to alleviate that problem in the future. Also a flapper on the screened “outfall” of that piping located on the outside of the building might also contribute to an answer of the problem. Another answer might be to simply disconnect the piping during cold spells in the future. I’ll leave the final answer to that dilemma to a higher power. As a direct result of ANTHC supplying the community with spare parts inventory during recent upgrades we were able to locate cpvc piping and other material to properly replace the damaged pipe section to the pressure tank. Of obvious concern was that we didn’t want to use any non NSF 61 certified material to reconstruct the section of piping that went to hell. We followed all manufacturer recommendations during assembly as well as sanitized the tank and piping prior to recommissioning it. Next I helped John perform an engineered method to backwashing his GAC tank. I demonstrated to him how one of the two differential pressure gauges had failed. It read during operation an extremely unrealistic PSI reading of approximately 95 psi. I pointed out that his water collection/distribution system is not designed to allow operation at that high of a pressure. I showed him when isolated and removed from the system the gauge still read 25-30 psi. We replaced the gauge with another identical NSF/ANSI approved component that was part of the spare parts inventory. Last of all we did a professional permanent installation of a brand new toyo stove to help address the ongoing building heat issues experienced at the plant. | 8 | none |  |  |  |  | None | No |  | No |  | No |  | No |  | No | I concluded my short but extremely productive stay by working with Alfred on his continued diligent effort at maintaining proper chlorine residual including documentation of his efforts. Alfred and John do a two week on and two week off schedule but work together on major efforts or concerns like the recent frozen pipes or while I was there. Overall the plant runs good and without a glitch and the associated water and sewer systems are well designed and layed out. We talked about continued/increased maintenance and oversite of the facility especially during cold spells. I spoke with both Operators about attending upcoming training in Fairbanks. They still desire me to return to assist with upcoming needs and repairs/maintenance. Based on the recent events/work I also suggested they send in a bacti sample asap. | Operator | [9 empty] | N/A | Other Documents | 2017-02-24 10:39
RMWTR-1627 | TCC | Tanacross | Wes Shales | 2017-02-02 | 2017-02-03 | Emergency | [5 empty] | No |  | Name: Johnny Lillie Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Fred Kameroff Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Chris Denny Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: Agnes Denny Title/Position: Tribal Administrator Accompanied By? No Telephonic Contact? No | Name: Robert Title/Position: Local Laborer Accompanied By? No Telephonic Contact? No | Name: John Simms Title/Position: TUS Accompanied By? No Telephonic Contact? Yes |  |  |  |  | Installation of the water plant building heat circ pump. | Prior to beginning this trip Chris Denny called to us to report that the two hydronic heat pumps for the Water Plant were failed or failing. Johnny at the time was on a personal trip to Anchorage and confirmed with Chris that one pump was failed and the other going out. I immediately began phoning around Fairbanks then Anchorage and located one pump in Anchorage. Initially there was a slight challenge to properly confirm the exact model number of the pump. The pump data plate was missing but a plate on the power pack provided enough info; along with the measured specs to help determine the correct pump model number. Chris, Tech Support at Grundfos and the folks at Alaska Pump and Supply all contributed to the winning outcome of the situation. John Simms/ANTHC was a significant part in helping Tanacross to quickly obtain the pump and have it sent to us at the TCC/RMW program. John was also helpful in verifying it was the proper pump. We arrived at Tanacross and went over the next morning’s work plan. We began the next day by turning off the boilers and partially draining the system. The glycol in the system was extremely “muddy” and thick in nature and Johnny said he had never replaced it or added conditioner etc. We were ready to change out the glycol but found that the two drums intended to be used were only partially full. We did have enough already to re-pressurize to system so continued on with our plan. We removed the old pump and replaced it with the new one we brought with us. Johnny was back in town and was a huge part of our effort there. He immediately had the Tribal Office order enough glycol for a near future plan to replace the old glycol. | 1 | None |  |  |  |  | None | No |  | No |  | No |  | No |  | No | Fred and I wrapped up our work there and prepared for the journey home. We spoke with Johnny about ordering another pump for the system and he began the effort on that. | Operator | [9 empty] | N/A | Other Documents | 2017-02-24 10:49
RMWTR-1628 | TCC | Circle | Fred Kameroff | 2017-02-07 | 2017-02-10 | Emergency | [5 empty] | No |  | Name: angela Ludwick Title/Position: Tribal Administrator Accompanied By? No Telephonic Contact? No | Name: Jessica Feilds Title/Position: Tribal President Accompanied By? No Telephonic Contact? No | Name: Lawrence Crow Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Dennis Carroll Title/Position: Public Works Director Accompanied By? No Telephonic Contact? No | Name: Dick Hutchinson Title/Position: Other Accompanied By? No Telephonic Contact? No | [5 empty] | Thaw Transmission line Replace Hydronic Circulating Pump | Mr. Lawrence Crow Jr contacted me prior to my departure to Tanacross stating the Circulating pump for the building heat was out, and asked for my advice over the phone. I told him to turn on pump number 1 and bleed out the air on the motor and add pressure to the system. I called back Mr. Crow and checked on how he was doing and he stated the pump was running and heat was going through the building. On 02/06/17 I contacted Mr. Crow and he stated that there was no water coming into the building from the well, he mentioned the heat tape for the transmission line had tripped out when the power for the village had shut down and he reset the breaker for the transmission line. Mr. Wes Shales and I arrived Circle on 02/07/17 and met with Mr. Crow and Mrs. Jessica Fields at the water plant, I asked Mr. Crow to turn on the pump to see if there was any water coming it but the lined was frozen. We than checked the heat tape and it was going out into the transmission line warm, Mr. Shales then checked the voltage on the pump leads and they were going out good. Once we checked the pump control panel we made our way down to the well vault and set up the space heater with 4 gallon propane tank and the Honda generator and started to heat up the well vault. After attempting to thaw out the well vault we called it a day and restart in the morning. by the next day we reset the space heater at the well vault and started to reheat the vault, as Mr. crow was keeping the vault heated Me and Mr. Shales started to remove the worn out pump and installed the new pump head, once the task was done we recharged the Hydronics and purged out the air on the motor and any air in the line and put the circ pump back on line. Once the well vault was good and warm we pumped out the water inside the vault, all the water was from ground water from all the rain last fall. Mr. Shales then opened the bypass valve inside the well vault and we confirmed the well pump is working and pumps water. On 02/09/17 we had ordered 100 foot by 1 inch water hose to pump water into the fire truck from the well vault using the bypass valve to deliver water up the water plant tank. We also added chlorine into the water tank in the fire truck. After delivering water into the storage tank we turned on the pressure pumps and using hot water we recharged the transmission line and sending hot water down the line to thaw out the frozen line, we also used a vacuum to blow warm air into the transmission line carrier pipe, and sucking warm air from the laser heater anything to help get it thawed out. As we were pumping water into the fire truck circle residents were getting water from the well. We then shut off the bypass valve in the well vault and water started to flow into the water plant, once the well transmission line thawed out we pumped out water from the water storage tank into the fire truck water tank and Mr. Crow pumped in fresh water. RECOMMENDATIONS/CONCLUSION Boil water notices were posted at the school and at the water plant and people were also told to boil water, I contacted Mr. Crow and checked if the water was still running and he stated that it is still running. | 24 | none |  |  |  |  | none | No |  | No |  | No |  | No |  | No | operartor | Operator | [9 empty] | N/A | Other Documents | 2017-02-24 10:42
RMWTR-1629 | TCC | Circle | Wes Shales | 2017-02-07 | 2017-02-10 | Emergency | [5 empty] | No |  | Name: Fred Kameroff Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Lawrence Crow Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Dennis Carrol Title/Position: Public Works Director Accompanied By? No Telephonic Contact? No | Name: Jessica Fields Title/Position: Tribal Council Member Accompanied By? No Telephonic Contact? No | Name: Dick Hutcheson Title/Position: Other Accompanied By? No Telephonic Contact? No | [5 empty] | Assist with effort to diagnose and correct no flow situation from well pump and help address water plant heating issues. | Arriving in Circle we immediately checked the control operations and voltage/amps of the well pump. All readings were normal. The well pump was obviously deadheading when called to operate. Also, indications were that the electric heat trace to the utilidor from the water plant was working. It was drawing about 7 ½ amps and warm to the touch (at the water plant). Upon opening up the well pump vault we observed sub-freezing conditions within. Approximately a 1 ½ foot of ice was formed at the bottom of the vault. Supply piping exited the pitless adapter and t’d off for a tap and then onto the supply loop point. That area of pipe took a somewhat p trap like route that was located within the iced up bottom section of the vault. The pipe like utilidor that entered the vault was located just above the ice. When the well pump was switched on at the plant we heard a “hum” coming from within the well casing. We used a propane torpedo heater to add heat to the vault and continued on with that effort for a couple hours that evening. Throughout our continued efforts we maintained during the day and into each evening to apply heat to the vault using the torpedo heater. We were able to thaw out the ice at the bottom of the vault and used a sump pump to completely drain the vault. We also rigged a setup where we blew hot air into the utilidor (arctic piping) from the water plant. At the pipe t within the vault we were soon enough able to find that normal water flow conditions now occurred up to that point. After continued efforts at thawing out the frozen water transmission line to the plant we decided to activate plan B which would utilize a water haul fire truck to use the tap at the vault and hdpe pipe to fill up the sanitized/flushed out tanker and use that water to fill up the holding tank at the water plant. Water/sanitation needs for the entire community as well as fire suppression (water supply) concerns at the school and for the tanker (fire truck) itself demanded that water storage existed at the water plant. (The storage tank was totally dry)! The entire community was put on a boil water notice. Batch chlorination occurred at each tanker haul to the water plant. On the second to last day we used heated/treated water at the properly isolated return loop to the well vault. That effort continued into the evening and on the last morning of our trip. Water delivered from the tanker was clean and clear looking. Unfortunately the inside of the tank is heavily coated with iron and manganese deposit and turned the water delivered to the taps and toilet at the water plant (washeteria) a murky rust looking color. Apparently this condition occurs a lot under normal operating conditions at the plant when low water levels in the tank allow for incoming water from the well to “stir things up”. Inline basic (paper) filtration occurs for the water at the community water point at the plant. On our final day in Circle all the combined efforts at battling the frozen pipe(s) resulted in resumed water flow in the transmission line from the well. Prior to our arrival Fred had assisted the community in obtaining a replacement circulation pump head for the hydronic heating system at the water plant/washeteria. In addition to complete failure of the pump head constant leaking occurred from the pump assembly. This condition resulted in boiler water on the floor and a repeated need to re-pressurize the heating system. The valves that isolated the pump on each side of the pump ports had slightly failed and were contributing to the mess. We didn’t waste any time correcting the situation by installing the new pump head. | 8 | Aged water plant infrastructure. |  |  |  |  | Inadequate water filtration equipment. | No |  | No |  | No |  | No |  | No | If it were up to me I would totally upgrade the entire well pump and water treatment facility at Circle to include a large capacity storage tank and including green sand filtration. In the mean time continued and or increased preventative maintenance would be beneficial in prolonging the life span of the aged operation. Even though Lawrence is doing an exceptional job lately, Jessica is actively seeking help for him by attempting to hire a good alternate Operator. | Construction Project | [9 empty] | N/A | Other Documents | 2017-02-24 11:02
RMWTR-1630 | TCC | Nulato | Wes Shales | 2017-02-15 | 2017-02-17 | Emergency | [5 empty] | No |  | Name: Grefg Patsy Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Neil Title/Position: Local Laborer Accompanied By? No Telephonic Contact? No | Name: Van Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: Clifford Title/Position: Local Laborer Accompanied By? No Telephonic Contact? No | [6 empty] | Greg Patsy requested help to determine if the well pump or return loop circ pumps had possibly failed and/or if the transmission line had frozen up. | Upon arrival I quickly set out to do electrical checks on the well pump and the two return loop circ pumps. Both voltage and amp draw were normal. No flow from the well pump was the main issue. It was at this point definitely considered to be frozen. I inquired with Greg as to why the heat loops were not running and he stated he had never used them in all the years he had worked at the water plants there in Nulato. The pressure in the heat loops at the gauge read about 5 psi. Even though it hadn’t been used in years, if ever, it was definitely low. I said if it was a properly constructed and sealed (glycol) loop the fluid would not just evaporate or disappear. It might expand or contract with temperature changes but otherwise should have maintained much of its integrity. A partial drum of glycol was brought to the plant and as we added it to the loop the psi gauge increased in pressure but immediately dropped back to the original reading upon stopping the transfer pump. After 20 gallons was added to the loop I suggested we stop. Greg had stated that he wasn’t sure if the glycol loop was fully connected and that during upgrades to the system it might not have been fully completed or reconnected. Greg at this point wanted to continue with his plan to start up the Blackberry Well and he stated he would have to replace a valve that had cracked during a freeze up. It was stated the Blackberry Well there in Nulato had never been used since its construction about four years ago. The tie in to the distribution system/transmission line was in a nearby vault. The vault was accessed and found to be relatively free of any ice and actually had a little bit of standing water at the bottom of it. After the cracked valve was replaced the well pump was activated and a heat trace from the well house to the vault energized. All proper procedures were followed as to activating the well including flushing it out with a hose from the vault. Greg did an operational check down at the upper water plant after it was properly valved into the system at the vault. It was pointed out that an auto air vent at the blackberry well house was cracked. It had a leak coming from it during operation of the pump. Also, an expansion/ pressure tank needed to be verified that it hadn’t been compromised. I didn’t have a pressure gauge on me. Greg said he would check it out later. These two situations were noted because the well pump would fluctuate in flow/pressure and that these could be fully or partially responsible for that problem. My focus was redirected back to the problem of no flow from the lower well pump in town. I suggested we attempt at adding water back into the return loop. That was done and it was observed that water flow was almost immediately stopped. It was apparent at that point that possible freeze up had occurred at the water plant end of the old town transmission line. After Greg and I were discussing that he took me out side and showed me the point where the arctic pipe entered the building from underneath and it was fully concluded that was a weak link in the (non) heat traced/not working heat loop transmission line water pipes. We spoke about thawing the water line out and how to go about it. Greg had a plan and would work out the details soon. I offered some suggestions on essentially the same plan and to immediately help out with it. We were just completing another very full day of activity and with the Blackberry Well up and running there seemed to be no rush or need to work overtime during evening hours. | 1 | None |  |  |  |  | Inadequate working freeze protection for lower town well transmission line. | No |  | No |  | No |  | No |  | No | Lee Meckel is the assigned RMW for Nulato and was busy at another community during this need to provide assistance to Nulato. Greg planned on attempting hot water jetting of the transmission line from the lower water plant location and stated he had all necessary clean "peks" water line to perform it with. As of the submission of this report Lee is currently in Nulato assisting Greg with his efforts. | Operator | [9 empty] | N/A | Other Documents | 2017-02-24 11:21
RMWTR-1631 | YKHC | Mtn. Village | Billy Westlock | 2017-02-07 | 2017-02-07 | Emergency | $55 |  |  |  | Personal sno go | Yes | 140 miles | Name: Charlie Long Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Donald Kokrine Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | [8 empty] | Assist trouble shoot cannery well | I arrived into mtn village where I met with Charlie Long wpo and Donald Kokrine where we troubleshot the cannery well. What happened was that the fuse box blew up, and the cannery well had lost its power to the vfd.after troubleshooting the panel electrician David Blanket was able to change out the fuses and get the cannery well back in operation. When I arrived to mountain village the wpo's had found a break in the upper loop and repaired the leak. | 2 | I think this summer we need to take out most of the repair bands and replace with electro fusion couplings, most of the leaks I think is from the repair bands getting loose. |  |  |  |  | Loose repair bands need to be replaced with electro fusion couplings. | No |  | No |  | No |  | No |  | No | None at this time | Unknown | [9 empty] | N/A | Other Documents | 2017-02-24 12:05
RMWTR-1632 | YKHC | Alakanuk | Billy Westlock | 2017-02-09 | 2017-02-09 | Other | $25 |  |  |  | Personal sno go | Yes | 20 miles | Name: Cyprian Augline Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [9 empty] | Assist wpo Cyprian Augline troubleshoot the vfd for the pressure pumps. | I received a call from wpo Augline wanting assistance troubleshooting the vfd for the pressure pumps. The vfd was tripping causing the pressure pumps to shut down. I was on the phone with anthc electrician Kolt Garvie trying to figure out why they were wanting to trip, on the vfd there was an alarm causing this problem, with electrician Garvie help we were able to remove the alarm to keep the pressure pumps running. Now pressure pumps back in good order. | 2 | None at this time |  |  |  |  | None at this time | No |  | No |  | No |  | No |  | No | I will keep in touch with wpo Augline to make sure there is no more tripping. | RMW | [9 empty] | N/A | Other Documents | 2017-02-24 12:31
RMWTR-1634 | YKHC | Kasigluk | Bob White | 2017-02-22 | 2017-02-22 | Routine |  |  |  |  | Snow Machine | Yes | 58 miles | Name: Tom Bobo Title/Position: Other Accompanied By? Yes Telephonic Contact? No | Name: Alysa Gustefson Title/Position: Environmental Health Officer Accompanied By? Yes Telephonic Contact? No | Name: Nickfer Nicholas Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [7 empty] | To troubleshoot the Contact clarifier and speak at the community meeting. | When I arrived we opened the contact clarifier and looked at the media. The media had visible mud balls on the surface and as we dug down in we found large layers of very dense mud lens in the media. So we decided to agitate the material by hand some before air scouring and back washing. While we were air scouring the contact clarifier the the power shut off and we were unable to backwash for several hours until it was restored. Since it was time for the community meeting I went and joined the others at the council office and we each spoke to the community about their water and answered question they had about water and sewer. Once power was restored we were unable to resume the air scour as it would blow the pressure release valve. When we put it to backwash we could only get 7.5 GPM of flow. no matter what we did we could not get the media to lift and clean in backwash. In filter to waste it would flow around the mid 40 GPM range. Since there was no progress being made we decided to head back to Bethel. | 4 | The Contact clarifier has developed a sever case of mudballs and became cemented. |  |  |  |  | The contact clarifier has had ongoing problems and needed additional maintenance to operate. even with this is has developed Mud Balls. | Yes |  | No |  | No |  | No |  | No | Agitate the clarifier manually with the jetter as we discussed and supersaturate the material with KMnO4 to see if we can break up the mud and recover the media. | Operator | We need to coordinate samples of home owners water tanks with the operator in Old Kasigluk to answer question raised at the community meeting. | [8 empty] | N/A | Other Documents | 2017-02-27 16:14
RMWTR-1636 | YKHC | Quinhagak | Bob White | 2017-02-15 | 2017-02-16 | Routine |  |  |  |  | Raven Air | No |  | Name: Michael vincente Title/Position: Environmental Health Officer Accompanied By? Yes Telephonic Contact? No | Name: Frank Jones Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Fannie Moore Title/Position: City Clerk Accompanied By? No Telephonic Contact? No | [7 empty] | Troubleshoot transfer line pressure switch. Assist with trouble some service connection freeze up. Collect samples from Lifewater treatment units. | When we arrived Frank was busy with a service line freeze up so we went and discussed the the Lifewater units with Fannie at the office. We discussed the operation of the haul system and the transition of that to ARUC. She agreed that it made sense to have weekly top offs for a flat fee as the most efficient way to run the haul system. Once we were back at the water plant we prepared our power meters for installation and gathered our needed sampling supplies. We then departed to install the power meters. While installing the power meters we also came up with a plan to draw the sample from the final sump in the Lifewater unit. When we returned to the plant we decided to check in on the troublesome service line and it was still frozen even though the heat trace was on for several hours now. We were also unable to get circulation on the glycol loop to the house. After pulling the glycol pump we found we had no pressure on the return line, so we went to the mainline and pulled off the shroud and insulation and found the return line valve was closed. We also found the heat trace was not installed properly and the check valve was frozen. We rewrapped the heat trace to have 2 wraps around the check valve and ball valve pay attention to make sure the heat tape was actually in contact with the valves. The next morning we gathered the samples we needed from the Lifewater units, then we returned to the water plant worked on the transfer line pressure switch but we were unable to adjust it to make it work but we did find another with some spare parts left from the project. We installed the part even though it looked used we were able to adjust it to make it work properly. We then returned to Bethel. | 12 | Willard Church service line heat trace was not in contact with the components it should have been and had insufficient wraps according to manufacture instructions. | the Eone pump at the water plant kept giving a nuisance alarm at the end of each run. |  |  |  | None at this time | No |  | No |  | No |  | No |  | No | As you have problems with service line heat trace open shrouds and re wrap the components as I showed you then insulate and close. | Operator | [9 empty] | Attachments | Other Documents | 2017-02-28 08:11
RMWTR-1637 | DEC | Angoon | Kevin Schoneman | 2017-02-21 | 2017-02-24 | Other | [5 empty] | No |  | Name: Floyd Murphy Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Brenton Alexander Title/Position: ANTHC Engineer Accompanied By? Yes Telephonic Contact? No | Name: Brian Menghini Title/Position: ANTHC Engineer Accompanied By? No Telephonic Contact? No | Name: Dan Fredrickson Title/Position: Wastewater Operator Accompanied By? No Telephonic Contact? No | Name: Kevin Mitchell Title/Position: Wastewater Operator Backup Accompanied By? No Telephonic Contact? No | Name: Harriet Silva Title/Position: Mayor Accompanied By? No Telephonic Contact? No | Name: Albert Howard Title/Position: City Council Member Accompanied By? No Telephonic Contact? No | Name: Edward Jack Title/Position: City Council Member Accompanied By? No Telephonic Contact? No | Name: Paul Thomas Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Albert Kookesh Title/Position: City Council Member Accompanied By? No Telephonic Contact? No | Flush and inspect approximately 1400 feet of 8" gravity sewer main, and record the inspection for repairs or replacement purposes. | I arrived at the airport in Anchorage @ 0630 Tuesday February 21 and check in for the 0800 flight to Juneau. I was joined by RMW, Floyd Murphy at the gate and we departed Anchorage on time. We arrived in Juneau at 1050, we both checked in at Alaska Seaplanes for our flight to Angoon at 1300. While we were waiting at the gate for our flight to Angoon we met up with Brenton Alexander, Project Manager for Angoon with ANTHC. We all departed Juneau for Angoon at 1315 and arrived in Angoon at about 1410 we were met at the seaplane terminal by Brian Menghini with ANTHC, we then proceeded directly to the City Office to attend a scheduled community meeting. When we arrived at the city office and immediately into the meeting that had just begun. We were all introduced to the City Council and the public in attendance. Brent gave a summary of the purpose of our visit the work we would be doing while we were in Angoon for the week. Several of the council members and a couple of people from the audience expressed concern as to the condition of the waste water gravity main on Front Street. Brent stated this would be our primary focus for the next few days. There was also some concern with several of the council members as to the condition of the water isolation valves and fire hydrants. We were all thank by several members of the council and public for coming to Angoon. After the meeting was adjourned we met with the operators and labors that would be working with us on the Front Street line flushing and camera inspection. They showed us where they had stored our equipment that we had sent down to Angoon a week prior to our arrival. We briefly inspected the equipment to make sur all of it was there and intact. As a group we all decided to meet by the Kootznahoo Lift Station to look at the pumps that the operators and Brian Menghini had started working on the day before. The wastewater operators were looking at replacement of the ware plate in the right hand pump and they asked for directions on how to do so. There had also apparently had issues with priming the pumps in the past and they been working on an alternative method. We took a quick tour of town and checked in at the Kootznahoo Inlet Lodge. The next day we all met at the city office to get the equipment for the line flushing, we were met by Brent, Brian from ANTHC. From the city of Angoon operators, Paul Thomas, Dan Fredrickson, Kevin Mitchell and John the firetruck operator. Brian and Paul left to finish some electrical work at the water plant they started the day before. The rest of the group started the line flushing of the 8” Gravity Main that runs in the center of Front Street. We started flushing at Manhole MH-5 which is on the West end of Angoon and flushed downstream to MH-4 which is a length of 96 feet. We then proceeded from MH-4 to MH-3 which is a length of 285 feet. For this run of the gravity main we first flushed down stream approximately 150 feet then flushed up steam from MH-3 up to about half way to MH-4. This was done this way because of the weight and drag of the hose on a long run. After flushing the line we found a root ball approximately the size of a volleyball in the upstream invert of MH-3. We were able to grab it using a hose attached to the city vacuum truck that the operators were using to suck up any debris as we flushed the lines. We resumed flushing the line from MH-3 to MH-2 and then on from MH-2 to MH-1, MH-1 has an “emergency overflow outfall” which consists of an 8” that exits the manhole about half way up the barrel and serves as an overflow outfall line. This line would only be utilized in the event of a lift station failure or some sort of line blockage. There is normally there is no flow through this line and is for emergency only. It was also noted there was a considerable amount of grease build up between MH-2 and MH-1. We then flushed from MH-1 to MH-1A, the transition between the upstream invert and the downstream invert in MH-1A is very rough and stair stepped. This would most likely would collect solids and would interfere with velocity. We then proceeded to flush from MH-1A to MH-1B, MH-1B collects gravity flow from two directions then discharges into the Front Street Lift Station and from there pumped up to the community septic tanks. After we completed flushing the lines to be inspected, we then returned to MH-5 to start the camera inspection of all the lines on Front Street. After picking up the sewer see snake equipment we set everything up at MH-5 and began the inspection and recording. We found it to be easier for one person to be inside the Manhole and one or two monitoring the camera and laptop computer. The city crew assisted with the manhole access and traffic control. We were able to inspect about half of the 1400 feet of sewer line when the battery on the laptop began to get low on power so we decided to shut down for the evening and pick up where we left off the next day. The next morning we all met back at the city office to load up the equipment and resume the camera inspection. We completed the camera inspection of Front Street, this completed the scope of work requested. Approximately 1400 feet of gravity 8 inch sewer main and seven manholes. The work was saved on the RMW Sewer Cam Laptop and would later sent to ANTHC. After a short lunch break we met back with the city crew and started cleanup of the camera equipment and line flushing gear. After the gear was cleaned and disinfected we loaded everything up and drove to the airline office for shipment back to Anchorage. After we dropped everything off, Floyd drove me out to the Water Treatment Plant, Floyd gave me a tour of the plant and the source for the Village of Angoon. The next morning Floyd and I met the float plane for our return to Juneau for the connection back to Anchorage. We arrived back in Anchorage at about 4:00 pm Friday the 24th. | 16 | Annual sewer line flushing. |  |  |  |  | Sewer nozzels | No |  | No |  | No |  | No |  | No | Annually flush all of the sewer gravity mainlines. | Operator | Purchase hoses and nozzles for sewer line maintenance. | [8 empty] | Attachments | Other Documents | 2017-03-10 09:49
RMWTR-1640 | YKHC | Shageluk | Bruce Werba | 2017-02-09 | 2017-02-09 | Routine | $57 |  |  |  | Personal Snowmachine | Yes | 130 miles | Name: John Hamilton Title/Position: Water Operator Accompanied By? Yes Telephonic Contact? No | [9 empty] | To install by pass line for the water meter. | After getting parts from the Holy Cross water plant I departed for Shageluk. Once into Shageluk I met John at the water plant. We began by making sure that all components needed were onsite to place a 1 1/2 copper by pass line in, we did have everything. We now cleaned all copper and prepared pipe for soldering. I then demonstrated to the WPO how to perform a good solder weld. With all the by pass installed we then performed maintenance to the water meter. Once it was cleaned we conducted a flow test between the meter and the by pass line, the flow was about the same. With all tasks now performed I now departed for Holy Cross at 1700, I arrived back home at 1900 hours. | 5.5 | None at this time. |  |  |  |  | None at this time. | No |  | No |  | No |  | No |  | No | None at this time. | Unknown | [9 empty] | N/A | Other Documents | 2017-02-28 10:56
RMWTR-1641 | YKHC | Holy Cross | Bruce Werba | 2017-02-22 | 2017-02-22 | Emergency | $0 |  |  |  | Personal Snowmachine | Yes | 5 miles | Name: David Walker Title/Position: Water Operator Accompanied By? Yes Telephonic Contact? No | Name: Bernard Edwards Title/Position: Water Operator Backup Accompanied By? Yes Telephonic Contact? No | [8 empty] | To assist water plant operator with a service line break. | After receiving a call from the WPO at 1030 hours with a freeze up and break on the water service line in the arctic box, I told the WPO that I would assist him by 1100 hours. Once at the residence I found out from the WPO that the home owner was elderly and now hospitalized, while away the house froze. We began by thawing the arctic box, we then used the boiling hot water method. Putting about five boiling kettles into the service box, it thawed and had water to the box, now a leak developed on the flex line (food grade hose), it came apart on thawing. We then turned the water loop off to complete repair to the service flex line. After repair the service loop was now normal. The next task for the WPO was to make sure all fixtures were operating normal, he had to change a the bathroom one, now the house was safe for having water, before the elderly home owner came back the following day. We called it a day at 1630 after putting tools away. | 4.5 | None at this time. |  |  |  |  | None at this time. | No |  | No |  | No |  | No |  | No | Have the WPO check for any possible leaks in the next few days. | Operator | [9 empty] | N/A | Other Documents | 2017-02-28 11:17
RMWTR-1642 | YKHC | Atmautluak | Bob White | 2017-02-28 | 2017-02-28 | Routine |  |  |  |  | Snow Machine | Yes | 30 miles | Name: Shane McIntyre Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Louie Nicholai Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [8 empty] | Hook up Emergency electric heat trace. | When we arrived they had the cover of the arctic box open and the insulation removed we located the conduit with the heat trace in it and removed the end junction box so we could reroute it through the wall. Once we had a hole cut through the wall we fed the conduit through and tied it into the old heat trace junction box. We then went to the heat trace control box and we were unable to power up the heat trace. We found the control panel fuse on the control circuit was blown and we had no replacements. We then further found that we had lost one leg of the 3 phase power coming from the transformer in the water plant. We then decided to instead hook the heat race to a old unused contactor. Once running new conduit and wire we were able to power up the heat trace. | 4 | This is the second time we have lost a leg on a transformer. | Something shifted on the glycol line tearing the 90 apart. |  |  |  | The controls for the heat races are complete inoperable without the transformer. | Yes |  | No |  | No |  | No |  | No | We will return with the Electro fusion machine when we get one back to make repairs to the glycol line. | RMW | [9 empty] | N/A | Other Documents | 2017-03-01 08:30
RMWTR-1644 | YKHC | Chefornak | Allan Paukan | 2016-12-16 | 2016-12-16 | Emergency | $0 |  |  |  | Grant Aviation Charter | No |  | Name: Brian Lefferts Title/Position: Environmental Health Officer Accompanied By? Yes Telephonic Contact? No | Name: Robert White Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Robert Jimmy Title/Position: City Administrator Accompanied By? Yes Telephonic Contact? No | Name: Daniel Alexie Title/Position: Water Operator Backup Accompanied By? Yes Telephonic Contact? No | Name: Jeff Beatty Title/Position: Project Superintendant Accompanied By? Yes Telephonic Contact? No | [5 empty] | To conduct inspection of burnt water plant. | After receiving a call from Robert Jimmy that there was a fire in the water plant on the 15th of December, I told my Superviser and we scheduled a charter with Grant Aviation to get onsite the following day. Today we spent all our time at the water plant after we arrived into Chefornak. We met everyone at the water plant. It was obvious that the electrical disconnect panel needed to be changed, one of the legs was totally fried from the fire. Along with that the wiring for the pressure pumps needed changing, the well pump needed new wiring, the pressure pump control wiring needed replacing, the lighting needed replacing, the boiler wiring needed to be traced out to make sure we have the boiler operational, the last was the unit heaters needed rewiring. With the inspection completed we completed a walk thru of the new water plant and washeteria with the Project Superintendant Beatty. The water plant was almost completed enough to get online. The new washeteria was almost completely shelled. We then spoke with the City Administrator Jimmy to discuss course of action for the burnt water plant. It was decided that I am going back to Bethel and getting all materials needed to get the water plant back online before the entire system froze. We departed for Bethel on the charter we came in on. | 0 | Purchase all electrical materials from Bethel, to get the water plant operational. |  |  |  |  | None at this time. | No |  | No |  | No |  | No |  | No | Make sure that I purchased enough material to get the water plant functional again. | Operator | [9 empty] | N/A | Other Documents | 2017-03-02 08:44
RMWTR-1646 | TCC | Manley | Fred Kameroff | 2017-02-21 | 2017-02-21 | Emergency | [5 empty] | No |  | Name: Ray Woods Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Wes Shales Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | [8 empty] | Diagnose well problem | Mr. Ray woods contacted TCC OEH Engineer Mr. Brian Bearden stating the well pump was not working. Mr. Bearden and I contacted Mr. Woods and tried to help him over the phone to diagnose the control box and the pressure switch but he was unsuccessful in getting the pump to run. We figured it might have frozen, but that was not the case. Mr. Wes Shales and I drove up to Manley after the weekend and opened the well control box and found there were two reset buttons hiding under the control box. Once we reset the buttons the well pump turned on and water was coming in the pressure tanks. As the pump was running Mr.Shales checked the amps and the volts and everything checked out OK. After about an hour the starting capacitor started to overheat and smoke. Mr. Woods shut the pump off. We asked Mr. Woods if he had a spare control box or a capacitor and he stated he did not have one on hand, Mr. Shales then wrote down the size of the control box and since we had nothing to work with we drove back to Fairbanks and find a new box and make another trip out the Manley to make the repair. RECOMMENDATIONS/CONCLUSION Once we have purchased a new control box we will head back out to Manley and install the new box for the well pump. | 3 | well control box out |  |  |  |  | control box needs to be replaced | No |  | No |  | No |  | No |  | No | TCC/ RMW travel back once new control box is found | RMW | [9 empty] | N/A | Other Documents | 2017-03-01 11:38
RMWTR-1649 | YKHC | Chefornak | Allan Paukan | 2016-12-19 | 2016-12-22 | Emergency | $575 | $192 |  |  | Ravn Connect | No |  | Name: Jeaff Beatty Title/Position: Project Superintendant Accompanied By? Yes Telephonic Contact? No | Name: Thomas Mael, Jr. Title/Position: Local Laborer Accompanied By? Yes Telephonic Contact? No | Name: Casey Panuruk Title/Position: Local Laborer Accompanied By? Yes Telephonic Contact? No | Name: Daniel Alexie Title/Position: Water Operator Backup Accompanied By? Yes Telephonic Contact? No | Name: Robert Jimmy Title/Position: City Administrator Accompanied By? No Telephonic Contact? No | [5 empty] | To assist Water Plant Operator (WPO) with getting water plant in working order after fire burnt all major components in water plant. | Dec 19 I travelled back to Chefornak to assist WPO with getting the plant back online with materials from Bethel. Once into Chefornak the WPO picked me up at the airport. We immediately went to the water plant where the City Administrator (CA) was waiting. We discussed how many laborers we needed for the emergency repair. The project supplied two individuals and the city supplied one, the back up WPO. We began by getting the lighting circuit online. We were able to get two of the four lights operational. Our next task was to eliminate the wiring we had no idea where they went. We called it a night about 2300 hours. Dec 20 started by finishing off the lighting system with LED fixtures. Our next objective was to dismantle the electrical distribution panel. While we were taking the panel apart we labeled the wiring that we knew where they went. We were able to pull the panel out, connect all wires that were labeled. We then ran new wire for the pressure pumps and controls. We then identified the wiring for the boiler and circulation pumps, one was inoperative when we started but got it operational after rewiring. Our next task was to get the two unit heaters operational, after locating wiring and changing them out we had both operational. We then double checked the well pump and controls, they were intact. With it being late we called it a day at 2300 hours. Dec 21 We started by properly labeling all circuits in the panel, with that complete I called for a flight back to Bethel with some left over gear. Once onto Bethel I dropped my gear to the RMW shop. With it being to late to catch a connecting flight to St. Mary's I over nighted in Bethel. Dec 22 I checked in at Ravn Connect and arrived home at 1300 hours. | 20 | Make sure the water distribution loop still has circulation in the next few days. |  |  |  |  | None at this time. | No |  | No |  | No |  | No |  | No | Make sure missing front cover is placed back on electrical distribution panel. | Operator | [9 empty] | N/A | Other Documents | 2017-03-03 11:05
RMWTR-1650 | YKHC | Bethel | Allan Paukan | 2016-12-07 | 2016-12-09 | Training/Meeting | $215 | $144 |  |  | Ravn Connect | No |  | Name: Brian Lefferts Title/Position: Environmental Health Officer Accompanied By? Yes Telephonic Contact? No | Name: Ayssa Gustofson Title/Position: Environmental Health Officer Accompanied By? Yes Telephonic Contact? No | Name: Robert White Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Billy Westlock Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Bruce Werba Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Shane McIntyre Title/Position: RMW Accompanied By? Yes Telephonic Contact? No |  |  |  |  | To bethel for attending a YKHC regional SDS meeting. | I piggy backed this trip with another trip I took to Toksook Bay. That's why the low airfare. In Bethel we conducted our meetings on the 7th and the morning of the 8th. We covered all the villages in regards to the SDS point system. On the after noon of the 8th till the afternoon of the 12th I worked in the YKHC RMW Shop/ Grey Water Recycling Research Center getting plumbing and electrical done that is needed to complete research by the YKHC OEHE program. With all tasks complete I departed for home on the evening schedule of Ravn Connect on Dec 12. | 0 | None at this time. |  |  |  |  | None at this time. | No |  | No |  | No |  | No |  | No | None at this time. | Other | [9 empty] | N/A | Other Documents | 2017-03-06 09:42
RMWTR-1651 | YKHC | Toksook Bay | Allan Paukan | 2016-12-05 | 2016-12-06 | Routine | $605 | $96 |  |  | Ravn Connect | No |  | Name: Alyssa Gustafson Title/Position: Environmental Health Officer Accompanied By? Yes Telephonic Contact? No | Name: Jeff Curtis Title/Position: Water Operator Accompanied By? Yes Telephonic Contact? No | Name: Jonathan Charlie Title/Position: Water Operator Backup Accompanied By? Yes Telephonic Contact? No | [7 empty] | To assist WPO and YKHC EHO with conducting a water plant survey. To conduct a Practical examination waiver for WPO, waiver wqas for minimum education for operator certification. | Aftery leaving for Bethel on the eveniong schedule of Ravn Connect I arrived into Bethel and stayed at a friends house. The morning of the 6th I departed to Tooksok Bay with EHO Gustafson. Once into Tooksok Bay the WPO picked up the both of us from the tarmac area. We got to the water plant and began the water plant survey. I assisted the WPO only when he didnt either understand the question or parts of the plant he did not know. We were able to complete the survey in about three hours. My next task was to complete a waiver for the WPO; Minimum Education for Operation and Maintenance certification. We went thru the entire waiver with the WPO Curtis there to clarify any questions we could not answer. The WPO back up showed a lot of knowledge of the plant and was able to perform all tasks with out any supervision. It was my recommendation to grant the waiver, we will see if op/cert grants waiver. Having completed all tasks we departed for Bethel on the evening schedule of Ravn Connect. | 0 | None at this time. |  |  |  |  | None at this time. | No |  | No |  | No |  | No |  | No | See at a later date if the waiver was granted to the WPO. | Other | [9 empty] | N/A | Other Documents | 2017-03-06 10:11
RMWTR-1652 | YKHC | Newtok | Allan Paukan | 2016-12-12 | 2016-12-16 | Routine | $800 | $196 |  |  | Ravn Connect | No |  | Name: Michael Vicente Title/Position: Environmental Health Officer Accompanied By? Yes Telephonic Contact? No | Name: Alexie Kilongak Title/Position: Water Operator Accompanied By? Yes Telephonic Contact? No | [8 empty] | To conduct a water plant and clinic survey with YKHC EHO and WPO. | December 12 was my travel day to Bethel to meet the EHO heading to Newtok. In Bethel I stayed at a friends house. We checked in for the morning Newtok flight at 0800 hours, we arrived into Newtok about 11:30. We met the WPO at the water plant, where we began immediately on the water plant survey. I assisted where the WPO and EHO were having trouble. It was not long that before we completed the water plant survey. We went overt to the clinic to conduct a clinic survey. I assisted with the components in the plant that he wasn't familiar with. It took a little while to complete. Once the clinic survey was done I went back over to the water plant and looked over some items that the WPO wanted to repair. With all tasks completed we departed Newtok on the evening flight of Ravn Connect. In Bethel I stayed at a friends house. The following day until friday I helped the YKHJC OEHE Gray Water Research Center with plumbing and electrical for the research units. I departed Bethel on friday the 16th's evening flight to St. Mary's. I arived into St. MArys at 1830 hours. | 1 | None at this time. |  |  |  |  | None at this time. | No |  | No |  | No |  | No |  | No | None at this time. | Unknown | [9 empty] | N/A | Other Documents | 2017-03-06 10:42
RMWTR-1653 | TCC | Minto | Lee Meckel | 2017-01-14 | 2017-01-14 | Emergency | [5 empty] | No |  | Name: Jeremy Charlie Title/Position: Wastewater Operator Accompanied By? No Telephonic Contact? No | [9 empty] | Assist operator with running the water plant on back-up generator, at the request of the Village Council. | We were called by Ms. Melanie Titus Friday afternoon and asked to send someone to assist the water operator with starting the generator. The operator was able to get the backup generator started without our assistance. Ms. Titus stated that she wanted us to come out there anyway, because the Village Council had voted to request RMW assistance, because of the power plant problem and they wanted an RMW to be there in case something went wrong with the backup generator, because they were not confident that the operator had the necessary skills to deal with generator problems. | 4 | I left Fairbanks and upon passing through Fox I found myself driving through blizzard conditions. Once I began approaching Ptarmigan Pass the wind was blowing snow drifts across the roads that were as tall as the grill on my GMC Sierra. The snow was dry and light so I was able to push through them to get there. I drove past multiple abandoned vehicles that had slid off the road and become engulfed in blowing snow. The power plant’s generators were being serviced by A.V.E.C. (Alaska Village Electric Power Co-Op) in such a manner that required the water plant to run off of the backup generator. |  |  |  |  | . Mr. Charlie had to charge the battery to the generator to get it running and did on his own accord before I arrived. I spoke with the A.V.E.C. representative once I got to Minto. I was informed that the power plants generators would be back on line by Wednesday the 25th of January 2017. Mr. Charlie and the A.V.E.C. rep had serviced the backup generator for the water plant and had changed a fuse and determined the battery had not been holding a charge. Once this was remedied the generator was online running all systems associated with the water plant. Mr. Charlie had already completed his daily checks and measurements at the water plant by the time I had arrived and everything was running and operating as it should be with the exception of the day tank on the generator. The solenoid valve on the fuel day tank for the generator has still not been replaced. Mr. Charlie was able to work around this issue by manually pumping fuel to the tank via hand pump and 55 gallon drum of fuel. | No |  | No |  | No |  | No |  | No | Replace solenoid on the day tank to generator. | Operator | [8 empty] | Mr. Charlie is more than capable of his responsibilities and proved so this past weekend, I have confidence that he will be able to ensure the community of such during the course of his employment. | N/A | Other Documents | 2017-03-07 10:42
RMWTR-1654 | TCC | Nulato | Lee Meckel | 2017-01-24 | 2017-01-26 | Routine | [5 empty] | No |  | Name: Greg Patsy Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Van Madros Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | [8 empty] | Look at boiler for potential leaks and assess leaks in upper town site water distribution line. | Upon arrival to Nulato I was taken to the washeteria in the upper town site. We looked at the boiler in question. Mr. Madros and I removed the skins on the boiler and looked in the area that Mr. Patsy had noticed glycol pooling on the floor. I could notice no clear signs of leaking in the actual cast iron that makes up boiler. I inspected the threaded plugs and could see signs of very old cooked glycol that had reached the surrounding air and cured hard no longer leaking. I did detect an old glycol stain on the floor that had flowed underneath the boiler and pooled in the same area that Mr. Patsy had noted. Mr. Madros and I began to investigate the origins of the glycol staining. We thought that the leak may originate from the threaded plug on top of the boiler that is hidden under the boiler skins. Just as we were preparing to open the skins on top, the boilers PRV (pressure relive valve) leaked glycol on same spot as the staining. This was strange because the boiler in question was shut down and was isolated via valves on both the supply and return lines. This told me either the supply and or return valves are not closing all the way and the PRV was susceptible to the pressure changes from the rest of the hydronic heating due to poor expansion absorption, or the static pressure was so strong it was able to create more than 30 psi to pop the PRV. The amount of glycol lost from the PRV was minimal however if the boiler was running under direct heat it would be much more. I manually released more pressure from the boiler PRV to see how the liquid would flow once on the ground. Close to the PRV on the ground is a drain that has risen above the grade of the concrete slab. This rise in the floor was causing a portion of the lost glycol from the boiler to flow away from the drain and underneath the boiler finally pooling in the same area that Mr. Patsy was noticing glycol. Mr. Madros and I began testing the expansion tanks in the array and noticed that there were a few that were water logged and needed to be pressured back up. Mr. Madros and I removed one that was completely backed up with glycol and pressured it up with an air compressor only to find that the bladder inside had become compromised and no longer functioned accordingly. We located a new one but needed to reduce from ¾” threads to 1/2” in order to fit in the current expansion tank array. | 16 | The leaks in the distribution loop seem to slow when Mr. Patsy adds heat to the system. |  |  |  |  | Change PRV in leaky boiler and replace expansion tank. Hopefully this will curb the loss in the heating systems psi. | No |  | No |  | No |  | No |  | No | I was able to follow up with Mr. Patsy and am happy to report he was able to seal the carrier pipe. He also added a repair clamp to the carriers plug as it began to leak once pressurized. Mr. Patsy also added some follow up information stating that he tried increasing the water main temp 40 to 58 degrees overnight and that water use dropped from 21,000 gpd to 14,000 gpd in the following 24 hours from final completion of the carrier pipe repairs. This indicates that the leak is probably in a joint that has separated. Keeping the water temperature elevated may be a good way to minimize leaks until the pipe can be more easily excavated in the spring for repairs. Mr. Patsy stated that he would be experimenting with temperature to obtain a good balance between leak reduction and energy use. | RMW | [9 empty] | N/A | Other Documents | 2017-03-07 10:53
RMWTR-1655 | TCC | Tetlin | Lee Meckel | 2017-01-23 | 2017-01-25 | Emergency | [5 empty] | No |  | Name: Mike Sam Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Walace Title/Position: Local Laborer Accompanied By? No Telephonic Contact? No | Name: Luke Title/Position: Local Laborer Accompanied By? No Telephonic Contact? No | [7 empty] | Assist with trouble shooting boiler #2 issues and rewire old florescent lights to accommodate led bulbs. | I received an update regarding the boilers in Tetlin shutting off. Prematurely and blowing out black smoke. I arrived and was greeted by Mr. Wallace and Mr. Luke. Mr. Wallace showed and explained what the burner had been doing and the course of action he had taken. I fired up boiler in question and immediately realized that something was off in the drawer assembly. I was able to see inside the boiler using the view glass. The flame looked dark orange and looked as though it was not getting enough air even though I had set the air band my previous trip. We shut down the boiler and opened up the burner and removed the high pressure fuel line and pulled the drawer assembly out. I then realized that the one I had removed and replaced was now back inside the boiler and the electrodes were bent out of shape. There was also soot all over the inside of the blast/air tube and cadmium sulfide cell, we cleaned it all off. The amount of soot that was inside the boiler is often the bi product a rich fuel air mixture. I looked closer at the nozzle and put a wrench on it to make sure it was tight and I was able to put another 45degrees of torque in to it. Mr. Wallace and Mr. Luke helped out by taking the skins off the boiler and brushed it out while I was making some adjustments to the drawer assembly. I put the assembly back together and while doing so tired to tighten the porcelain insulator that houses the electrodes and could not. The fastener holding these had been tightened down all the way and the porcelain would still move freely, I set them the best I could and from there carefully put them back in to the burner. We put the boiler back together and test fired it, the boiler ran and the flame looked better inside the view glass. I shut it off and was not satisfied with the look of the flame. The next day we let boiler two run and it almost heated up to the high limit when the burner shutdown prematurely. I decided to put the newer drawer assembly back in to the burner and found an old nozzle that had been removed and placed it into the new drawer assembly and again test fired the boiler. This time the boiler would not start at all. I hit the reset on the side of the burner motor and it began to cycle. The boiler fired up and this time the flame looked much brighter and cleaner with distinct fingers of fire off the flame that ended shortly before the back of the inside of the boiler. It ran and again cut off before reaching the high limit. I then realized that it was the burner motor itself that had failed. We did not have the parts on hand to make the final repairs so Mr. Wallace and Mr. Luke decided to change the PRV I had picked up on my previous visit. We also changed a bad expansion tank with a new one that is undersized but was readily available. We changed both fuel filters and adjusted the limits switches on boiler two to run in as the lag in a lead lag configuration so that boiler two is not responsible for producing as much B.T.U./heat as boiler one. Mr. Sam has purchased some L.E.D. lights for the washateria and we wanted to put them in but could not find the latter to get up to them. Mr. Sam took a water sample and I followed Mr. Sam to Tok and priced out a few latter’s as well as unsuccessfully looked for boiler parts at the local hardware store. I returned to Fairbanks and the following day I was able to locate the part needed for all boiler repairs and turned in the water sample to Analytica via Arctic Couriers. | 16 | Expansion Tank is undersized but a new one is on the way. |  |  |  |  | The water make up to the boiler only works on manual mode. | No |  | No |  | No |  | No |  | No | make sure burner motor is running properly | Operator | [9 empty] | N/A | Other Documents | 2017-03-07 11:06
RMWTR-1656 | TCC | Venetie | Lee Meckel | 2017-02-01 | 2017-02-03 | Routine | [5 empty] | No |  | Name: John Frank Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [9 empty] | Fix waste heat system and replace heat exchanger for the WST | I contacted the operator for Venetie to arrange travel to install the parts purchased through ANTHC after the assessment by Mr. Cody Uhlig. Mr. Frank had let me know over the phone which copper plumbing fittings would be needed to swap the WST add heat exchanger. I was greeted by Mr. John at the washeteria and began assessing the materials available. We found all the pluming fittings and prepped them by cleaning and adding flux and cutting half inch copper stubs to be soldered in place. We shut down the circulation pump moving water to the WST and used valves to isolate both upstream and downstream of the heat exchanger. We then isolated the glycol lines and bled the water from both the hydronic heating side and the treated water side of the heat exchanger. There were unions sweated in line that we loosened to remove the heat exchanger. Mr. Frank and I then strapped the old heat exchanger to a pipe vise and heated up the four male threaded unions in an attempt to salvage the union fittings and pre-soldered angles. We were able to save three of four and had to rebuild one section that was damaged while being heated. We were able to find a critical fitting in the water plant and use some I had purchased in town to get the add heat exchanger prepared and ready to install. Once every piece was built and soldered we placed the heat exchanger back into place and fastened the unions. We pressured it up to 12 psi and had to blead the air out to get the hydronic heating side to circulate. The following day we began working on the circulation pump hp-7. We found the breaker and flipped it on and still did not get power to the pump so we traced the power back to the boiler control panel and hit the thermal overload reset while the power to the pump was off. We were getting power to the pump so we bump tested it and it started. We opened the valves on the hydronic heating side that had been isolating the waste heat exchanger from the power plant. We had to add make up water to pressure up the loop and then started pump hp-7. The circulation loop to the generators was operating fine. The gauges from the power plant generators read that the heat from the power plant was coming in at 167 degrees and out at 165 degrees stripping 2 degrees of heat at these lower temperatures. The water plant boiler gauges were putting off readings of 156 degrees in and 158 out right before the boiler fired up from reaching its controls preset low limit of 160 degree with a five degree differential. I did notice that when the boiler was firing up it would actually heat up the return line to the power plant generators. That heat is then stripped and delivered to the clinic, from the waste heat return line to the power plant generator after leaving the washateria. So when the boiler is heating up to the high limit of 180 degrees its warming the clinic until the mid-170’s when the heat seems to start to transfer to the washateria hydronic side. To stop this from happening Mr. Frank has set the boilers aqua stat controls high limit temperature to 170 to match that of the power plants waste heat output. Boiler 2 has the return valve stuck shut and I could only open supply valve 1/2 way. Despite definitely being purchased and shipped no one seemed to be able to locate the fusible link oil shut off valve. Mr. Frank was hesitant to force the boilers return valve open without anyway to repair if it were to break, I agreed. I also removed and disassembled a pump from a leaking washer and found some steel shot in the pumps impeller. I then conducted a continuity test; the motor was good so I reinstalled and then test ran it. The washer still leaked at the gasket and may need to be replaced as it feels torn. Mr. Frank and I were able to resolve and address the major issues I would like to thank A.N.T.H.C. who stepped in and helped to procure materials to be successful and have the heating system operational. I would still like to see the leaky portions of both supply sides of the boilers fixed. I would also like to run a treatment flush on the heating system to flush out any remaining build up especially in the plate waste heat exchanger. | 16 | The well transmission line is thawed out form the man hole to the plant. However the lower end is still frozen. |  |  |  |  | Boiler supply and return valves are both seized in their current positions. | No |  | No |  | No |  | No |  | No | I would like to use fernox to flush the boilers and heating lines that were exposed to acidic glycol. | RMW | [9 empty] | N/A | Other Documents | 2017-03-07 11:33
RMWTR-1657 | YKHC | Tuntutuliak | Bob White | 2017-03-06 | 2017-03-06 | Routine | $330 |  |  |  | Raven Air | No |  | Name: John White Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Jonathan Pavila Title/Position: Tribal Administrator Accompanied By? No Telephonic Contact? No | [8 empty] | Trouble shoot transfer pump controls. | When I arrived I was picked up at the airport by Tribal office staff and taken to the Washeteria. John and I started to look over other issue he wanted me to look at. Tribal Administrator Jonathan Pavila stop by and we talked about the work we were going to do and some other things we would make plans to do in the future. We made a list of parts that we would need to replumb the unit heater over the washeteria door to have appropriate size pipe so it would deliver enough heat to be effective. We then started tracing wires from the float that had been replaced. We had some difficulty tracing the wires as none were labeled and we had to sort out over 20 pairs of black wire in the wire chase. We finally had the wires traced out and found they were capped off in the wire trace above the mag-starter for the transfer pump. We traced the wires from the mag starter to see what they were hooked to and found they were hooked to the new control panel that was installed by the last VSW project. When they installed the new control panel they disconnected the floats that start and stop the the transfer pump. The auto signal from the control panel was only related to a high turbidity in the finished water and not if there was water in the tank. This has caused the operator to have to work many extra hours just watching water transfer as the pumps would burn up if the the water would run out in the raw water tank or the finished water tank would overflow. We then reconnected and tested the floats to make sure they would shut off the pump if the raw water tank was low or the finished water tank was full. We finished off the day making a parts list and plan to remove the grey water tank and go right from the grey water lift station to the lagoon. John dropped me off at the airport at 1730 hrs. | 7 | The last improvements made to the plant have been a failure and have caused more problems then they solved. | They grey water surge tank is was not sealed on top or vented so the grey water starts to stink from going septic as it sits overnight or over the weekend when there is no use. | The control panel to control mixer and high turbidity has never worked right and was a need less complication to a simple treatment system. | The in line plastic Wirsbo shut off valves to the heater units are all leaking in the future use Brass shut offs. |  | GAC filter has not been replaced since it froze and broke. | No | Boiler circulator #1 has failed. | No |  | No |  | No |  | No | Order parts when I get you the quote then let me know when they arrive so we can schedule a time to make the changes. | Community | Install the back up boiler circulation pump. | [8 empty] | N/A | Other Documents | 2017-03-09 08:30
RMWTR-1658 | DEC | Gulkana | Floyd Murphy | 2017-02-28 | 2017-03-03 | Routine |  | $220 |  |  | Company Truck | No |  | Name: Clinton Maxim Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Angelia Vermillion Title/Position: Tribal Administrator Accompanied By? No Telephonic Contact? No | [8 empty] | New operator training | 2/28/17 I departed Anchorage for Gulkana arriving around 1:00 pm. I met the New Operator Clinton Maxim at the water plant. Clint has experience working at the Gulkana water plant and had level 1 water treatment certification at one time but got out of water works and let his certification laps. There was a 2 inch elbow glycol leak in the corner of the building, the boiler pressure was down. The building was getting cold. Clint hand been adding glycol to the boiler system to keep heat in the building. We were unable to locate any rubber inner tubes or clamps at the water plant so we went to the community shop and found some clamps and several pieces of rubber that we would attempt to make a band aid type of repair until weather permits to make a permanent proper repair to the copper pipe. I went to Napa in Glennallen and bought some temporary repair equipment. In the meantime Clint was able to locate additional rubber material and was able to get the glycol from leaking. Clint went to the wood pellet plant and got some propylene glycol to add to the boiler to get the pressure for it to operate as normal. The Water plant had warmed back up by 6 pm when I departed for Glennallen for the night. 3/1/17 I arrived in Gulkana around 8:00 am. The temporary glycol leak was inspected and was holding with no additional leaks. The boiler pressure was normal. Clint and I cleaned the MIEX contact tank the water and media had gone septic. We cleaned the settling tubes at the top of the tank, removed the resin and flushed the inside of the tank as well as the effluent lines. Once this was completed we started installing the new resin in the tank using a pump and making a slurry to be able to pump it into the contact tank. Total installed was a drum and about a half container of resin. Additional resin should be added to get the level up about 8 more inches to the proper level. 3/2/17 We reloaded the salt hopper that the prier operator had removed from the hopper. We called MIEX prier to loading the used salt. Topped off the salt hopper with new salt. The MIEX was run through the regeneration cycle so it is ready for use the next time water is filtered. The State Boiler Inspector arrived and inspected the boilers along with the compressors. I am sure he will be sending a report to the community. The Fire-rite valves on the boilers should be replaced and not used for shut off valves once replaced. These valves are for fire safety. Had the new valves been of the right size we would have replaced them also. We thawed the add heat line to the water storage tank and replaced the circulation pump for it and put it on line. The connection going from the water plant to the water storage tank should have additional insulation added to it and covered in plastic to keep it dry. 3/3/17 Clint and I inspected all items that were worked on. We calibrated the two turbidimeters, raw water and finished water. The plant was fully functional when I departed. Per the Gulkana Water System Survey completed by: Sarah Ramey of Alaska Rural Water Association on August 3, 2016 the following should be resolved. Significant Deficiencies: 1) The operator should apply and take the operate certification tests and work toward the level 2 water treatment classification. 2) The hose connection to the filtered water line must have a vacuum breaker backflow device installed. The hose should be disconnected when not in use.) Minor Deficiencies: 1) The systems inactive well must be properly maintained, which includes instillation of a sanitary seal, or decommissioned. 2) Backflow prevention assemblies in the water system inspected annually. Annual routine testing schedule must be developed. Recommendations: 1) Water Storage tank is leaning. Work with ANTHC to correct this problem. 2) The MIEX Ion Exchange system has not been used for over a year. (The MIEX system was cleaned and flushed, salt tank cleaned and refilled, brain tank cleaned and refilled, resin replaced with new resin and regenerated by Floyd Murphy DEC RMW and Clinton Maxim, Gulkana Water Plant Operator on 3/2/17) 3) The Real UVT fixed. (The Real UVT was tested and calibrated by Floyd Murphy and Clinton Maxim 3/2/17.) Compliance Items: 1) The system received monitoring violations in April- July and November of 2016. (These violations can be avoided by ensuring that a monthly total coliform bacteria sample with a distribution chlorine residual is collected every month and submitted every month. 2) The system’s emergency response plan must be reviewed and updated every two years. The system’s next biannual update is due by 12/31/17. 3) The next sanitary survey completed during the 2019 calendar year. The raw water and finished water turbidimeters were cleaned and calibrated on 3/3/17. They should be calibrated every three months per manufacturer’s ligature. HACH Formazin Turbidity Standard 4000 NTU, 100 mL Cat. 246142 should be ordered for turbidity calibrations. 3 drums of MIEX resin for addition and standby media. An additional hose bib vacuum breaker should be ordered for the filtered water line in case the operator forgets to disconnect it after use. The backflow preventers should be inspected annually. Alaska Rural Water Association can do this for a fee. A sanitary well seal should be ordered for the abandoned well. The add heat line from the water treatment plant to the water storage tank should have additional insulation attached to it where it comes out of the building and the insulation covered with visqueen to keep it from getting wet. | 18 | Boiler fuel line safety valves needd replaced they were held open with vice grip pliers |  |  |  |  | Turbidity meters need to cleaned and calibrated every three months. | No |  | No |  | No |  | No |  | No | Operator should clean and calibrate turbidimeters every three monthe. | Community | [9 empty] | Attachments | Other Documents | 2017-03-10 09:44
RMWTR-1659 | TCC | Manley | Fred Kameroff | 2017-02-28 | 2017-02-28 | Routine | [5 empty] | No |  | Name: Ray woods Title/Position: Wastewater Operator Backup Accompanied By? No Telephonic Contact? No | [9 empty] | Replace worn out Well pump Control box. | Based on our recommendations during the previous trip, Mr. Ray Woods, Manley Washateria operator, purchased a new control box for the well pump here in Fairbanks and I and Mr. Wes Shales picked it up from Frontier plumbing. I contacted Mr. Woods and told him I would be heading up with Wrights air on 02/28/17. I arrived at Manley on Tuesday February 28th and Mr. Woods picked me up and escorted me to the Washsetria. I then removed the burned out control box and installed the new one. The new control box was the exact same kind and wired the same way. Once that was done I asked Mr. Woods to turn on the main breaker for the well pump and once he did the breaker tripped out. I then looked at the wire diagram that I had drawn and everything looked the same, but the breaker kept tripping out. I contacted TCC/OEH Engineer Mr. Brian Bearden and told him what we were having trouble with, he then told me to check the wire leads for the well pump to ground, and the meter indicated that all were shorted out. We were thinking there was a short somewhere on the wiring or the motor maybe burned out. The resistance measurement for the primary and starting coils looked good, though. RECOMMENDATIONS/CONCLUSION I mentioned to Mr. Woods the motor maybe burned out and he would have to purchase a new pump and I and Mr. Shales would have to make another trip out to get the pump running. | 3 | well pump not operating |  |  |  |  | well pump | No |  | No |  | No |  | No |  | No | TCC RMW'S head back up once pump is purchased | RMW | [9 empty] | N/A | Other Documents | 2017-03-10 16:41
RMWTR-1660 | DEC | Akutan | Steve Evavold | 2017-02-27 | 2017-03-30 | Routine | $1,350 | $270 |  |  |  | No |  | Name: Joe Bereskin Mayor Title/Position: Accompanied By? No Telephonic Contact? No | Name: Matthew Bereskin WTP Operator Title/Position: Accompanied By? No Telephonic Contact? No | Name: Jerod Jones ANTHC Const Mgr Title/Position: Accompanied By? No Telephonic Contact? No | Name: Joe Hess ANTHC Design Engr Title/Position: Accompanied By? No Telephonic Contact? No | [6 empty] | Trip was scheduled to coincide with preconstruction analysis of a new dam/reservoir project. Water plant inspection was needed to document upgrade needs for water plant. | Arrived in Akutan and met with Matthew. The water plant has several operational issues. The HACH SC100 controllers for the turbidimeters stopped displaying accurate turbidity after a couple of low voltage power failures. I tried calibrating and couldn't get the controllers to identify a 20ntu standard. The alarm indicators on the four 1720E's were flashing red. I called HACH technical service for assistance with troubleshooting the controllers. After a couple efforts at calibration and reprogramming, the technician advised that the SC100's controllers be sent in to HACH or just replaced with the newer SC200's. The water plant has a 2100Q portable turbidimeter. I showed Matthew proper technique for sampling and handling the vial. I requested that he use the instrument for daily recording until the new SC200's are installed. Joe and Jerod, ANTHC design and construction engineers, arrived and we assessed other plant deficiencies. A "Decant Vat" for chlorine batching and a new exhaust fan are needed. The chlorine pump was originally installed for flow switch shut off and is not working. Matthew has to "manually" turn off the chlorine pump when not making water. Pressure gauges for "pre" and "post" filtration for the bag filter trains should be replaced, as well as the pressure differential Gauge for the pressure sand filters. We discussed the need to replace the SC100's with new SC200's. The HACH 1720E turbidimeters might need replacing also. Operational status of the units will be determined when programming the controllers. Flow control valves and tubing for the turbidimeters need replacing; the tubing needs rerouting. The pressure transducer indicating water level in the storage tank will be replaced, and will be relocated from the water plant up to the storage tank. We left the plant to climb up to the reservoir. The project scope is to replace the dam impoundment with a smaller concrete structure; and to replace the 1200' 4" transmission line down to the water plant. The existing transmission line is 4" Schedule 40 PVC arctic pipe that has fallen, broken, and repaired many times. The routing is almost straight down the drainage ravine and is elevated an average of 6' above the ground on wooden supports. We walked the route up and down a couple of times for Joe to inspect top soil depth and a new route down to the water plant. Current plan will be to bury the first 250' down from the dam along the hill side and then up out of the ravine on a downhill course to alleviate the problems of snow avalanche or mud slide. An archaeologist was hired to interview residents and inspect the route for burial sites and other historical land use. | 4 | Nothing noted this trip |  |  |  |  | Nothing noted this trip. | No |  | No |  | No |  | No |  | No | A trip will be scheduled early fall for hydrant inspection and project completion punch list for the water plant. | RMW | [9 empty] | Attachments | Other Documents | 2017-03-16 15:44
RMWTR-1661 | DEC | Angoon | Floyd Murphy | 2017-02-21 | 2017-03-24 | Routine | $1,087 | $210 |  |  | Airplane | No |  | Name: Harriet Silva Title/Position: Mayor Accompanied By? No Telephonic Contact? No | Name: Albert Howard Title/Position: City Council Member Accompanied By? No Telephonic Contact? No | Name: Edward Jack Title/Position: City Council Member Accompanied By? No Telephonic Contact? No | Name: Albert Kookesh III Title/Position: City Council Member Accompanied By? No Telephonic Contact? No | Name: Kevin Frank Title/Position: City Council Member Accompanied By? No Telephonic Contact? No | Name: Paul Thomas Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Daniel Fredrickson Title/Position: Wastewater Operator Accompanied By? No Telephonic Contact? No | Name: Kevin Mitchell Title/Position: Wastewater Operator Backup Accompanied By? No Telephonic Contact? No | Name: Brian Menghini Title/Position: ANTHC Engineer Accompanied By? No Telephonic Contact? No | Name: Brenton Alexander Title/Position: ANTHC Engineer Accompanied By? No Telephonic Contact? No | Flush and inspect around 1400 feet of 8 inch gravity sewer main, Closed Circuit Television CCTV) inspection for replacement or repair before upgrades to Front Street in Angoon. | 2/21/17 Upon arrival at Angoon around 2:00 pm, Kevin Schoneman, Brenton Alexander and I were met by Daniel Fredrickson, Paul Thomas, Angoon Water Plant Operators and Brian Menghini, ANTHC Utility Support Associate Engineer. We were brought to the city office to meet with the city council.The council meeting was in session on our arrival. During the meeting agenda where we were included, Kevin and I explained that we were there to assist with cleaning the sewer main on Front Street and to run a camera up it to access the condition of it. We explained that we would need a fire truck for flushing the sewer line using the fire hose and nozzle we had shipped down prior to our arrival. After the meeting we looked at Front Street to see what we would be working on. Kevin and I made arrangements to meet the flushing crew to meet at the city office at 8:00 am. After looking over the system and the Kootznoohoo lift station we went to our place of lodging at the Kootznoohoo Inlet Lodge. 2/22/17 Keven and I met the crew at the city office to gather our tools and fire truck driver John Howard. John was the past fire Chief and was familiar with running the fire truck. Paul, Kevin Mitchell, Danny and Kevin S and I along with Brent went started flushing at MH-5 as we were unable to locate MH 6 which is up line from MH – 5, we continued to flush to MH -1B. At MH -3 we removed a root ball from the sewer line. Between MH – 1 and MH – 2 we removed a lot of grease and another root ball. After flushing the sewer line we started using the sewer camera to access its condition. Keven, Brent and I again started at MH – 5 and worked to MH – 1 with the CCTV. The computer battery got low when we were about half way through the sewer line CCTV. The city crew was able to observe and learn about operating the CCTV. 2/23/17 Keven, Brent and I continued with the closed –circuit television (CCTV) operation and the city crew worked with Agnes Marszalik, ANTHC Engineer, flushing by the Kootznoohoo lift station for Agnese’s wastewater study. We wanted to complete the CCTV work before Brent departed on the afternoon flight. Once this was complete we cleaned our equipment in preparation for shipment. The firehoses were washed by the city crew and Kevin and I cleaned the sewer camera. Kevin and I delivered the equipment to Alaska Seaplane. I brought Keven to the water treatment plant and water storage tanks so that he would also be familiar with the Angoon water and wastewater facilities. The Sewer line on Front Street should be replaced or rehabilitated. From observing the sewer line problems with the (CCTV). : 1) Large perforation at the top of the cast iron pipe near MH # 5. 2) By MH # 4, 19 feet from the MH, Inflow and Infiltration (I & I) Appears to be clean water. 3) From MH – 3, steady stream of water 3 to 4 gallons per minute (gpm), flowing through MH-3 and not through MH-4, water appears clean. A root ball was also found in MH-3. 4) From MH-1, Camera was under water most of the observation indicating a sag in the sewer line, not bedded properly. 5) Camera under water unable to see, possibly blockage around 10 feet from MH-2 6) MH-1 Pipe appears to be full of water. This 86 feet section of pipe appears to be not properly graded and is a long sagged line. This causes the fluid to flow slowly and solids to settle out in this section of line. 7) MH-1 at 67 feet on the top of the pipe appears to be another I & I around a service connection. This section of line also had sags in the line indicating improper bedding, causing water and debris to flow in slugs. 2/23/27 Keven and I departed Angoon on Alaska Seaplane for Juneau around 8: 45 am and arrived back in Anchorage around 4:00 pm. | 16 | The sewer lines should have annual flushing done. |  |  |  |  | 1) Large perforation at the top of the cast iron pipe near MH # 5. 2) By MH # 4, 19 feet from the MH, Inflow and Infiltration (I & I) Appears to be clean water. 3) From MH – 3, steady stream of water 3 to 4 gallons per minute (gpm), flowing through MH-3 and not through MH-4, water appears clean. A root ball was also found in MH-3. 4) From MH-1, Camera was under water most of the observation indicating a sag in the sewer line, not bedded properly. 5) Camera under water unable to see, possibly blockage around 10 feet from MH-2 6) MH-1 Pipe appears to be full of water. This 86 feet section of pipe appears to be not properly graded and is a long sagged line. This causes the fluid to flow slowly and solids to settle out in this section of line. 7) MH-1 at 67 feet on the top of the pipe appears to be another I & I around a service connection. This section of line also had sags in the line indicating improper bedding, causing water and debris to flow in slugs. | No |  | No |  | No |  | No |  | No | The sewer collection system should be flushed annually. | Community | [8 empty] | A 1 1/2 inch Whirlaway sewer cleaning Nozzle for flushing the collection system is available for purchased from: Best Products 1590 Dutch Road Dixon, Illinois 61021 Telephone: 1-800-323 - 1604 or through ANTHC, AUSC program: John Sims at 907-729-3525 4 @ 50 foot sections of 1 1/2 inch fire hose will be needed for this flushing procedure. | Attachments | Other Documents | 2017-03-15 10:28
RMWTR-1662 | YKHC | Emmonak | Allan Paukan | 2016-11-17 | 2016-11-18 | Emergency | $150 | $96 |  |  | Ravn Connect & Charter Grant | No |  | Name: Arthur Redfox Title/Position: Water Operator Accompanied By? Yes Telephonic Contact? No | Name: Jamie Agwiak Title/Position: Water Operator Backup Accompanied By? Yes Telephonic Contact? No | Name: Brian Lefferts Title/Position: Environmental Health Officer Accompanied By? Yes Telephonic Contact? No | Name: Robert White Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | [6 empty] | To assist WPO with getting water plant/ vacuum collection system building back into working condition after fire. | Nov 16th I was contacted to assist with fire damage repair in the water plant in Emmonak. I told OEHE Directer that I can depart on the morning schedule flight of Ravn Connect. We discussed what items to bring to get the structure, electrical and control damage and vacuum pump repair completed. Nov 17th I checked in at 0830 for Emmonak. At 0945 I arrived into Emmonak where the WPO picked me up and we discussed on the way to the water plant what items were destroyed in the fire. At the plant, the WPO was able to locate all the piping needed to connect the vacuum collection system pump to the sewer plumbing. We almost had the pump replumbed by the time the rest of the YKHC OEHE and Construction staff arrived. After they arrived I gave them a briefing as to my task at hand. The YKHC Construction crew immediately began on the structural repair, RMW White and YKHC Electrician began to work on the electrical control wiring and power flex unit, while the WPO's and I completed all maintenance needed to get the vacuum pump operational. By evening we were looking very good, the building structure was stabilized, the vacuum pump was operational. Not long later we were able to get electrical controls operational. We called it an evening at 2100. Nov 18th we began by placing a vacuum guage above the vacuum pump, made sure the vacuum system was operating, it was running normal. We then tweaked the water filtration system to hopefully increase the filter run time. With all tasks completed we all returned home by the evening. | 10 | Make sure vacuum is on every morning, to keep on top of maintenance issues. As the vacuum system is operating on one pump until the project is done with the new pump install. |  |  |  |  | None at this time. | No |  | No |  | No |  | No |  | No | Check on project status for new vacuum pump installation. | Engineer | [9 empty] | N/A | Other Documents | 2017-03-15 11:24
RMWTR-1663 | YKHC | Chevak | Allan Paukan | 2016-11-01 | 2016-11-03 | Routine | $891 | $96 |  |  | Ravn Connect | No |  | Name: Patrick Patrick Title/Position: Water Operator Backup Accompanied By? Yes Telephonic Contact? No | Name: Andrew Choluk Title/Position: Water Operator Backup Accompanied By? Yes Telephonic Contact? No | [8 empty] | To assist WPO with getting a break repaired in the wastewater collection system forced main to lagoon. Assist WPO with reprogramming power flex 70 after brown out occured. | Nov 1 I traveled to Chevak to assist the WPO with repairing two items; complete HDPE 6" forced main repair. And reprogram power flex 70. Once into Chevak the WPO picked me up from the airport and we went to the location where the forced main was leaking to see what we would need to complete the job. We went to the water plant and tooled up. After tooled up we went to the work site and prepared pipe for repair, once the heat was even on the pipe we electrofused the 6" HDPE pipe. After pressure testing the electrofusion coupling we buttoned up the pipe and went back to the water plant. After having lunch we tackled the fower flex 70 reprogramming, the pump would operate but not get to vacuum. After going thru a few parameters on the operator interface, we found that we only had to reverse the polarity to get the pump to operate in the right direction. It was now operating normal. Having completed tasks I departed on the evening schedule of Ravn Connect. In Bethel I stayed at a friends house for the night and departed on the evening schedule for St. Mary's. | 5 | None at this time. |  |  |  |  | None at this time. | No |  | No |  | No |  | No |  | No | For the vacuum pump controls, make sure they are spinning in the right direction for proper operation. | Operator | [9 empty] | N/A | Other Documents | 2017-03-14 11:45
RMWTR-1664 | YKHC | Bethel | Allan Paukan | 2016-10-03 | 2016-10-05 | Training/Meeting | $420 | $96 |  |  | Ravn Connect | No | [11 empty] | To assist the YKHC OEHE Training Program with instructing the "Intro to Small Water Systems" course. | Travel day was Monday for all who attended. After arriving into Bethel I assisted with the set up of training room, then found accommodations for the evening. Tuesday thru Thursday was the instructional portion of the class. During the class I received a phone call that I had to attend to in the village. So the 6th I went to Kongiganak. | 0 | None at this time. |  |  |  |  | None at this time. | No |  | No |  | No |  | No |  | No | None at this time. | Unknown | [9 empty] | N/A | Other Documents | 2017-03-23 10:11
RMWTR-1665 | DEC | Hydaburg | Steve Evavold | 2017-03-06 | 2017-03-08 | Routine | $825 | $160 |  |  |  | No |  | Name: Anthony Christiansen Mayor Title/Position: Accompanied By? No Telephonic Contact? No | Name: Natasha Peele City Administrator Title/Position: Accompanied By? No Telephonic Contact? No | Name: Stacia Miller City Clerk Title/Position: Accompanied By? No Telephonic Contact? No | Name: Donald Bell WTP Operator Title/Position: Accompanied By? No Telephonic Contact? No | Name: Allen Minch Alt Operator Title/Position: Accompanied By? No Telephonic Contact? No | Name: Dean Edenshaw Wastewater Operator Title/Position: Accompanied By? No Telephonic Contact? No | Name: David Reed ANTHC lead Electrical Engineer Title/Position: Accompanied By? No Telephonic Contact? No |  |  |  | Trip was scheduled for inspection and/or repairs to Turbidimeters, Honeywell data logger reprogramming, Polymer add system, and low voltage protection panel, with ANTHC Electrical Engineer. An inspection of the new lift station was asked for by the ANTHC PM. | Arrived in Hydaburg and met with Donald and Allen at the water plant. Effluent turbidity was 0.027ntu's and plant production was 60gpm. Chlorine residual leaving the plant was 1.6mg/l. David and I looked at the turbidimeters and Honeywell data logger. Over the last year there had been low voltage "Brown Out" events that had damaged some of the instrumentation and controls. That caused loss of IFE and raw turbidity metering, the chlorine analyzer, polymer and soda ash pumps. Some instruments recovered, some did not. On a previous trip I reinstated IFE monitoring capability by moving the "Raw" water turbidimeter to Filter 1 effluent. The SC200 for that turbidimeter had shorted(burned) out. AN ANTHC electrician had gone down to install a new SC200, but hadn't established the communication with the Honeywell data logger. I asked David to assist and give training to the operators in the programming. I was asked to address the council at a meeting. There were eight persons seated for the meeting. I introduced myself and explained the RMW program, Operations Certification, EPA requirements, and DEC contacts. I was asked about water quality, the ongoing lead and copper issues, and some more about the disinfection requirements. We discussed the costs associated with operating the water plant. They will need to absorb the cost for a new "Voltage Monitoring Relay" for surge and brown-out protection. A cost estimate and components list will be generated for Mayor Christiansen. They have a significant leak identified and located currently estimated at 10-15gpm. I am in discussion with ANTHC about cleaning the water storage tanks this spring and possibly eliminating the need for one of the tanks. Contact time and disinfection by-products are factors in the decision. I returned to the water plant as David was finishing with setting up the programming, pen assignments, and other inputs on the Honeywell. The display is returned to what the operator requested, and IFE is being recorded as required. In the morning we inspected the lift station with Dean Edenshaw, wastewater operator for the community. David checked the functions, operations, displays, and programming with Dean. Donald and Allen were there to observe. David and I left for Klawock shortly after. | 8 | A Voltage Monitoring Relay Panel needs installation for protection of all instrumentation in the water plant against voltage variance. | The located leak is between 15,000-20,000 GPD. |  |  |  | Nothing noted at this time. | No |  | No |  | No |  | No |  | No | Discussions with ANTHC reps have concluded that the storage tanks demand on chlorine are excessive. RMW assistance has been requested with cleaning and inspecting the tanks. | RMW | [9 empty] | Attachments | Other Documents | 2017-03-24 15:24
RMWTR-1666 | TCC | Manley | Wes Shales | 2017-02-21 | 2017-02-21 | Emergency | [5 empty] | No |  | Name: Fred Kameroff Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Ray Woods Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Elizabeth Woods Title/Position: Tribal Administrator Accompanied By? No Telephonic Contact? No | [7 empty] | Diagnose and assist with possible resolution of no flow from well pump. | Per the special request from Ray we drove to Manley to assist the community with their situation. Both Tribal and non-native members of the community rely on the laundromat and bathroom/shower facility that is part of the small “distribution system” the non-working well supplied. Having an onsite view and access to the problem it was quickly found that a reset of the well control box was necessary. Before and after the reset button was pushed electrical testing of the supply voltage/continuity/ohms of resistance and amp draw after reset showed proper normal/acceptable readings and no improper grounding of circuitry. It was quickly explained to Ray that the resettable overload didn’t tripped for no reason. Black or brown outs from the local utility, defective or failing electrical equipment on the same service as well as a failing/overworked well pump or its power supply/components, etc. could be the cause. It was noted that the water plant design didn’t incorporate a holding tank as part of the operation. Anyway, after an hour the well pump control box experienced a meltdown in the form of a burnt up capacitor. Supply voltage was good and electrical checks otherwise still acceptable. | 2 | None |  |  |  |  | None | No |  | No |  | No |  | No |  | No | We told Ray we would assist him in either finding a replacement capacitor or an entire well control box which would sometimes be easier to find in Fairbanks anyway and that a return to Manley to assist in the change out would be arranged. | RMW | [9 empty] | N/A | Other Documents | 2017-03-14 15:19
RMWTR-1667 | TCC | Kaltag | Wes Shales | 2017-02-27 | 2017-03-01 | Emergency | [5 empty] | No |  | Name: Conrad Semaken Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Richard Burnham Title/Position: Consultant Accompanied By? No Telephonic Contact? No | Name: Jackie Nicholas Title/Position: City Clerk Accompanied By? No Telephonic Contact? No | [7 empty] | Assist the new operator with determining (and possibly resolving) the extent of a small section of frozen sewer main. In addition, demonstrate/review some daily checks/maintenance routines at the water plant etc. | Prior to my arrival I arranged for a hotsy to be sent out as freight after receiving a call from the previous Operator (Jeremy). The transition from the previous Operator to the new Operator was unfortunately the cause for a delay in travel to Kaltag. As the dust settled I made a plan centered around resolving the problem and provided myself with all the necessary job and personal supplies and equipment to complete the initial objective just mentioned. I traveled out to Kaltag and Conrad and I proceeded to access some of the snowed over manholes and survey the situation at a couple of affected houses. The section of the community that had problems had experienced a reduction in houses serviced. We presented the situation to Richard and he had experience dealing with it in the not too distant past. Because of the continued freeze ups that would occur coupled with other extenuating circumstances such as the deeper than usual permafrost and including the reduction in flow for that area: which causes the sewer line to slowly layer up with ice and eventually clog the entire pipe as well as the manholes a plan was made to hold off on the effort to unclog/thaw out the sewer main. Although Conrad had assisted Jeremy a little in the past as well as others, he requested assistance with performing the backwash routine at the water plant. We went through the motions and he was instantly understanding of the process. We did a complete review of testing for chlorine as well as the operations and basic maintenance of his turbidimeter. In addition we reviewed his daily routine as well as other maintenance needs at the plant. I emphasized the need for preventative maintenance and went over examples of what that entailed. I discussed how important his record keeping was and that proper documentation was vital to the overall success of the water plant operation and how that affected his BP score. We reviewed an extremely old preventative maintenance plan and decided it was too obsolete so I am going to assist in the writing of an updated copy to complete at a later date in the near future. I also assisted Conrad with obtaining a part number for a broke coin drop for his newer model washer/extractor. We placed an order for that with a local Anchorage vendor. Last of all I went over the upcoming water treatment course in Fairbanks coming up and speaking with Jackie had him sign up for it. I went over an older training manual briefly with him as well. | 12 | None |  |  |  |  | None | No |  | No |  | No |  | No |  | No | The hotsy that was dropped off at the airline freight department during the previous week of my arrival was scheduled to fly out to Kaltag on a few different occasions but unfortunately didn’t arrive until the Wednesday that I returned to Fairbanks. Nevertheless, and anyway, the effort to thaw out the frozen pipes as explained was postponed. I am looking forward to assisting them very soon with that project. That may be as I am told a month or so away. Conrad was quick to provide warm storage for the unit until that happens. | RMW | [9 empty] | N/A | Other Documents | 2017-03-14 15:39
RMWTR-1668 | TCC | Manley | Wes Shales | 2017-03-06 | 2017-03-08 | Emergency | [5 empty] | No |  | Name: Fred Kameroff Title/Position: RMW Accompanied By? No Telephonic Contact? No | Name: Ray Woods Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Elizabeth Woods Title/Position: Tribal Administrator Accompanied By? No Telephonic Contact? No | [7 empty] | Resolve ongoing problem of failed water supply operation from well pump that by all accounts appears to be electrical in nature. Possible burnt up well pump motor. | After the 2/21/17 trip Fred Kameroff returned to Manley to install a replacement well pump control box while I was away to another TCC community. Unfortunately after the installation of the replacement control box an instant trip of the pump circuit breaker at the building breaker panel occurred. He found that electrical tests at the control box circuitry revealed unacceptable continuity between windings of the pump as well as direct short to ground. It would be easy to conclude that the well pump might be fried. A replacement pump that met all parameters as well as NSF certification and a control box compatible to that pump was acquired with intent to install it. Upon arrival in Manley we performed/verified a LOTO of the appropriate breaker and did an instant physical/visual check of the entire pump circuitry within the mechanical room and exiting the building that was not buried underground. It was quickly determined that a well pump circuit j-box on the outside of the building and that was attached to a crudely constructed arctic box around the piping/supply wiring conduit had been pulled tight and furthermore the j-box had its access door popped/left open. The conduit exiting the j-box and containing supply wiring for the well pump had been pulled extremely tight from freeze/thaw action. Poorly placed/knotted up wiring had been pinned down in the box by the lock ring to the connector as well as was pulled tight against the connector and had “rubbed” up against the connector threading. The arctic box and the electrical j-box were pinned up against the fragile railing to the porch and received a little bit of bumping movement every time the railing was touched or individuals walked up the small wood porch. The entire mess of the j-box and the small arctic box were fully covered in snow the first trip and still partially covered in snow this trip. A direct short had occurred within the j-box. Testing of the well pump circuitry after the shorted wiring/melted conduit connector were removed showed that the pump motor was still good! Because of the long run of cable to the well pump that combined with the depth of the well equaled many hundreds of feet a good electrician or installer would account for voltage drop among other things in determining a size of wire to feed the motor pump. The wire ran from the control box to the j-box outside was completely replaced with #10 awg wire and received a waterproof inline splice instead of the wirenuts previously used. In addition to all of this a complete new run of cord was upsized and used to feed the heat trace that protected the transmission line pipe. Two separate extension cords connected together supplied the heat trace in that arctic box and were in an extremely deplorable state of operation. Burnt up/melted connectors at each end of both cords were a good indication that overheating of the cords was occurring. One cord was one of those cheap 16-18 awg cords that should only be used for like maybe a simple night stand lamp or an alarm clock. The first cord was missing its ground prong. | 1 | None |  |  |  |  | None | No |  | No |  | No |  | No |  | No | After all repair/replacement work was completed both the well pump operation and the heat trace resumed normal and acceptable operation. Both Ray and Elizabeth were extremely accommodating and helpful during our stay there. I can easily recognize both do a lot of good hard work for their community and both Fred and I are impressed. Extension/SOOW cords should be inspected continuously during operation and replaced if necessary. In addition, slack should exist within the underground run of flexible cable/conduit such as is possible with mchl or liquid tight and a gooseneck like bend just above ground to allow for freeze/thaw cycles or earth “shifting”. | Engineer | [9 empty] | N/A | Other Documents | 2017-03-14 15:50
RMWTR-1669 | YKHC | Quinhagak | Bob White | 2017-03-13 | 2017-03-13 | Routine | $340 |  |  |  | Raven Air | No |  | Name: Michael Vincente Title/Position: Environmental Health Officer Accompanied By? Yes Telephonic Contact? No | Name: Frank Jones Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Francine Moore Title/Position: City Clerk Accompanied By? No Telephonic Contact? No | [7 empty] | Test Life water units. Replace Filter plate on DE filter. | When we arrived we started by uncrating and preparing the spare plate. Once we had the hardware installed on the new plate we needed to let the caulking set before we could install it. While we were waiting for the caulking to cure we headed to the office and met with Fannie about how the water haul systems were working and collect the last months questionnaire. We then headed out and took samples from the Lifewater units. Once we completed all the samples and meter reading we headed back to the water plant. At the water plant we installed the new plate and cleaned the filter then put it back into service. | 6 | We had some small cracks developing on the top 3 plates in each filter stack at screws in the plate. | The life water units that were not used in the last month used more power than the ones thad had been used. |  |  |  | The front Wall of the water plant has moved and is cracking as well as separated over a inch from the slab. | No |  | No |  | No |  | No |  | No | Drain Life water units if house in unoccupied to save on power. | Community | [9 empty] | N/A | Other Documents | 2017-03-15 08:17
RMWTR-1670 | YKHC | Kwethluk | Bob White | 2017-03-14 | 2017-03-14 | Routine |  |  |  |  | YKHC Truck | No |  | Name: Evan Olick Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Varlum Jackson Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Joseph Spien Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Larry Lee Title/Position: Project Superintendant Accompanied By? No Telephonic Contact? No | Name: Borris Epchuk Title/Position: City Administrator Accompanied By? No Telephonic Contact? No | [5 empty] | Install Sensaphone equipment project purchased for remote Monitoring. | We started with unboxing and checking that we had all the required parts. Then we placed the sensors were they would go and started running Cat6 cable back to the Node unit. Once we had each cable made we verified proper wiring before plugging into the Node unit. After lunch before we finished up with the Node installation Evan and I headed to the office to talk with Borris about parts they need at the Washeteria building and for the Eone pumps. We then went and inspected the progress on the Eone repair station in the old water treatment portion of the Washeteria. While we were looking over the progress and talking with Larry we were called back to the plant for a problem with the streaming current detector. When we arrived back at the plant we found the SCD was off and so was the rapid mixer. We started tracing the power to check where we were losing power and after checking several control panels that play a part in controlling the SCD we found a relay in the Chemical pump control panel was not engaging on the contact for the SCD. After tapping on it, it engaged. We looked for another relay but we were unable to find one as this is the only 11 pin relay in the entire building. We then closed up all the panels and wire chases and checked that the remote monitoring was working before I returned to Bethel. | 6 | The failing relay in the chemical pump control panel. |  |  |  |  | They are short on E-One pump parts and unable to rebuild any at this time do to a lack of stators and rotors. | No |  | No |  | No |  | No |  | No | Order 2 11 Pin relays one to replace the current one and another to have as a standby. | Community | Place a order for Stators and rotors for the E-one immediately. | [8 empty] | N/A | Other Documents | 2017-03-15 08:50
RMWTR-1671 | YKHC | Akiachak | Bob White | 2017-03-07 | 2017-03-07 | Routine |  |  |  |  | YKHC Truck | No |  | Name: Henery Pasitnick Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Ronald Noes Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [8 empty] | Teach operators proper way to rebuild LMI injection pumps. | When I arrived I looked at some fuses that Henry had found that he thought might fit in the High demand pump panel. We were unable to make any of the fuses work so we started to clear the bench so we could rebuild the LMI pumps. With all the rebuild kits matched to the LMI pumps I had ronald work on one and Henry on another with one on each side of me so I could watch them work and show them the proper way to do things. Once we had the pumps rebuilt we put them back online and then verified that they were pumping correctly. Henry's pump would not pump and kept loosing its prime. We tried to prime it but kept having it draw the tube dry. We tried a spare pump and had the same issue. After some time struggling with the pump we went back to the one just rebuilt and checked each part one by one and found one of the check valves installed back wards. This turned into a great opportunity to teach troubleshooting and checking ones work. We reassembled the the pump correctly and it worked perfectly. We then turned to reviewing the Preventive maintenance checklist. After going over each page of the check list making sure they understood what each component was and what they should be checking I made a couple list of parts needed and headed back to Bethel. | 6 | The water supply line to Loop #1 is leaking. |  |  |  |  | The back up generator is still broken, need linkage to solenoid replaced. | Yes | High Boost pump needs fuse on the electrical controls. | Yes | Terminal lift station has one broken Mag starter. | Yes |  | No |  | No | Order fuses for High Boost pump panel. | Community | Order solenoid and linkage for back up generator. | Community | Order Mag starters for terminal lift station. | Community | When the weather warms fix leak on Loop #1 supply. | Operator |  |  |  | N/A | Other Documents | 2017-03-16 08:29
RMWTR-1672 | DEC | Klawock | Steve Evavold | 2017-03-08 | 2017-03-10 | Routine | $815 | $160 |  |  |  | No |  | Name: Barry Peratrovich Public Works Director Title/Position: Accompanied By? No Telephonic Contact? No | Name: Bennett Charles WTP operator Title/Position: Accompanied By? No Telephonic Contact? No | Name: Harry Jackson WWTP Operator Title/Position: Accompanied By? No Telephonic Contact? No | Name: David Reed ANTHC Electrical Engr Title/Position: Accompanied By? No Telephonic Contact? No | [6 empty] | The trip was scheduled for inspection of water and wastewater treatment plants, mainly instrumentation and process controls. | Arrived in Klawock and met with Bennett at the water treatment plant. We conducted a walk through the plant to inspect and test operation of the instrumentation ANTHC electrical had recently installed. The plant was rebuilt a few years earlier, after the plant had been damaged in a fire. Everything was operating as designed. David and I left to meet Harry at the wastewater plant to inspect the operations. Again we did a brief walk through as Harry explained the sequence of the treatment process. David left shortly after back to Anchorage. I returned to the wastewater plant in the morning to discuss needs and the proposed upgrades in a project this year. The headworks for the wastewater plant is to be replaced. Currently the headworks is a large rotating drum covered with a microscreen that screens off the larger debris from the raw sewage, which falls into a large vat. The vat is manually emptied by shoveling the solids into trash cans by the operator. Lime is added before taking the cans to the dump. After the screening, the sewage flows through a clarifier where scum and settleable solids are removed. The solids, still holding a large percentage of water, are conditioned with a polymer for coagulation. Sludge is then augured up through through a screw press for dewatering, treated with lime, and is hauled to the dump by truck. The Bayview lift station has a control problem with the alternating lead/lag sequence, but both pumps are operational. Pump #1 displays a "Seal" alarm LED light at times. The pump has not failed and both Harry and I have called the Vendor to inform them of a possible issue. The floats had a grease build up that needs cleaning. The East lift station guide rails for pump #2 have come loose. The pump will not seal to the discharge piping until repaired. Pump #1 is operational and keeping up with flows. Bennett planned to start a backwash procedure in the morning. I asked him to show me the process. Barry Peratrovich, the public works director, arrived to observe the process. the water plant is performing as designed. Production is averaging 181,000GPD, CFE turbidity is 0.025ntu, and distribution Chlorine residual is kept at 0.60 mg/l free. | 2 | The manual process of the operator having to "Shovel" raw sewage from vat to trash can needs to be addressed. With the upgrades scheduled and the use of a vacuum type removal, the chance of biological and sanitary health issues will be lessened. |  |  |  |  | Nothing noted this trip. | No |  | No |  | No |  | No |  | No | Public works director, city manager, and operators, are concerned with lack of certified back up support for operations. The RMW program and Operations Certification program in Juneau will continue with communications until issue is resolved. | RMW | A trip will be scheduled when upgrades to the Waste Water plant are in effect. Also to follow up with an invite from Craig for a site visit to the water plant there. | [8 empty] | Attachments | Other Documents | 2017-04-04 09:49
RMWTR-1673 | TCC | Manley | Fred Kameroff | 2017-03-06 | 2017-03-08 | Emergency | [5 empty] | No |  | Name: Ray Woods Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Elizabeth Woods Title/Position: Tribal Administrator Accompanied By? No Telephonic Contact? No | Name: Wes Shales Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | [7 empty] | Diagnose well pump problem and well pump control box. | Mr. Wes Shales and I traveled to Manley on 03/06/17 and met with Ms. Elizabeth Woods at the tribal building, she told us the Mr. Ray Woods will be up shortly after taking care of personal matter. The purpose of our trip was to follow up on the tripped well pump I had diagnosed the week before. We were prepared to pull and replace the well pump, if needed, and had arranged for the purchase of a new pump the week before. Mr. Shales and I first went to the Utility building on back of the Washsetria and started to inspect the control box for the well and the J- box outside the building. After close inspection Mr. Shales found a burned wire inside the J- box that was connected to the main motor leads. Once we located the problem we started to look for number # 10 awg wire and connectors also to change out all the motor leads wires from the control box down to the J- box outside the building. All 4 wires were replaced and spliced with water proof inline splice. Once we were done changing out the wires with proper code size, Mr. Shales then removed the 3 way plug for the heat trace and replaced it with a new one, and also exchanged the extension cord for heavier wire. After all the outside work was completed Mr. Shales turned his attention to the well control box putting the wires in place. Everything checked out good and once the work was done, we energized the main power and the motor pumped water into the pressure tanks and into the washsetria. RECOMMENDATIONS/CONCLUSION Once we were done with the work we kept an eye on the water pressure and control box to make sure it wasn’t overheating. Everything was working properly and the well pump is back in operation. Mr. Woods decided to keep the new pump he purchased as a spare. | 8 | none |  |  |  |  | none | No |  | No |  | No |  | No |  | No | water plant operator | Community | [9 empty] | N/A | Other Documents | 2017-03-16 09:53
RMWTR-1674 | YKHC | Napakiak | Bob White | 2017-03-08 | 2017-03-16 | Routine |  |  |  |  | YKHC Truck | No |  | Name: Greg Aluskuk Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Herald Ilmar Title/Position: Local Laborer Accompanied By? No Telephonic Contact? No | Name: Leo Kusayak Title/Position: City Administrator Accompanied By? No Telephonic Contact? No | Name: Alexander Evan Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [6 empty] | Replumb dryers with appropriate size piping and install second heating coil. | This was a multi day trip comprising of March 8,9,15 and 16. Each time the trip was made by YKHC truck. We started by powering down the first set of dryers and isolating the plumbing before removing the existing plumbing. We then installed the new heat exchangers and required sheet metal work before starting the new plumbing. We completed the first set of dryers on the 9th and put them back into service. We started working on the second set of dryers in the same fashion as the first but we were able to complete this set in a third less time as they learned well on the first set how to sweet pipe joints. This was a great opportunity to do some practical training on pipe sizing and layout as well as proper sweeting technique. With the dryers operating correctly for the first time since installed 3 years ago the operators can be proud of there installation work and are better equipped to do it themselves next time. | 21 | The dryer piping was under sized. |  |  |  |  | None at this time | No |  | No |  | No |  | No |  | No | Order extra filters for the dryers. | Community | [9 empty] | N/A | Other Documents | 2017-03-16 16:47
RMWTR-1678 | YKHC | Pilot Station | Billy Westlock | 2017-03-01 | 2017-03-03 | Other | $95 |  |  |  | Personal snogo | Yes | 200 miles | Name: Ben Alick Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [9 empty] | I received a call from wpo Alick wanting assistance with water pressure on loop 1. | For a few weeks we were puzzled on why pressure from return line was weak. The pressure going out was about 40 and returning at 10 psi. We thought it was a break in the water main but the water usage was normal for a long period of time and not showing any sign of waterloss. We did some water metering for a couple days and all water usage was normal. I had looked over the water lines in the water plant and noticed that there was a in line screen right before the water circulation pump, there was a valve with a hose bib, I hooked it up to a garden hose and in that screen was a lot of debris which is a indication of the screen being dirty. In order for us to clean the screen we will need to rotate the screen housing in order to remove the screen once the weather is much warmer to shut down the system. I departed pilot station on the morning of the 4th and arrived the afternoon of he 4th | 10 | Monitor the psi for next few days. |  |  |  |  | We need to rotate the inline screen 90 degrees at a later date. | No |  | No |  | No |  | No |  | No | None at this time. | Unknown | [9 empty] | N/A | Other Documents | 2017-03-21 15:53
RMWTR-1679 | DEC | Chistochina | Floyd Murphy | 2017-03-20 | 2017-03-20 | Routine | $0 | $45 |  |  | Truck | No |  | Name: Rick Pitts Title/Position: Project Superintendant Accompanied By? No Telephonic Contact? No | Name: Roy Handcock Title/Position: Local Laborer Accompanied By? No Telephonic Contact? No | [8 empty] | Assist with troubleshooting and repairs to community office E-ONE lift station repairs. | Chistochina 3/20/17 Rick Pitts, KAE Inc. picked me up at my residence at 6 am to travel to Chistochina to assist with troubleshooting and repairs to the community office building. We arrived in Chistochina 11 am. We stopped at the community office, unfortunately no one was at the building. We met Roy Handcock, at the community maintenances shop. He informed us that the wastewater operator had to bring his son to Anchorage for immediate medical reasons. Freddy Nicholai had called Rick Pitts of KAE Inc. Friday the 17th and requested assistance with the E-One lift station, it was not pumping and they had to shut off the water system to the building to keep from getting wastewater on the ground. This is when I received a call from George Wilson, DEC Engineer for Chistochina requesting assistance with troubleshooting and repairing the problem. I than called and left a message with Carrie Bohan DEC RMW Director for approval to travel to Chistochina. With Roy’s assistance we were able to locate keys needed to access the office building. We opened the manway to the lift station which was full of liquid. Rick turned on the power to test the pump water, the pump operated but the sprayed effluent. This indicated that the effluent Grommet had failed. Rick had brought along tools to dewater the lift station. The supernatant was pumped to the old lift station for the community building. We set up a tripod to pull the E-ONE pump and replaced the Grommet. It was also noted that the frost covers for the wet well had been damaged and were waterlogged and therefore did not operate as designed. Once we replaced the Grommet we reset the pump in place and tested it. The grommet immediately failed indicating that there was something wrong with the pressure sewer line after the E-ONE pump station. Rick inspected the heat trace in the city office crawlspace. Rick stated that the heat trace plugin for winter use had been cut off for unknown reasons. The heat trace should be plugged in during the fall when it starts to freeze and unplugged after the ground has thawed. This had caused the pressure sewer line from the E-ONE to the sewer main to freeze and fail. 1) The electric heat trace should be plugged in during the fall and unplugged during the summer months after the ground has thawed. 2) At least 2 spare blue grommets should be on hand for replacement in case of a failure or damage to the grommet. (Northwest Pump & Equipment) This problem could have been prevented had the heat trace been plugged in to keep the sewer force line from the lift station to the sewer main warm. Rick reattach the community building to the old sewer system which is a septic and drain field system. Rick plans to go back to Chistochina during the summer to put the building on the E-ONE system and also reattach a new electric plug on the heat trace for the sewer force line from the community building. We depart Chistochina around 2:30 pm arriving back around 6:45 pm. | 4 | Heat trace line from the lift station from the list station to the sewer main was not electrically energized. The plug end was disconnected and removed. | The frost covers were damaged and did not serve as designed. Rick had contacted the E-ONE vendor and was made aware of a better designed frost cover for the E-ONE and will be working with the community to purchase the new frost covers for instillation. |  |  |  | Electrical plug needed for heat trace to operate. New frost covers for replacement of the failed frost covers. | No |  | No |  | No |  | No |  | No | Electric plug purchased and attached and plugged in during the fall and disconnected during the summer after the ground is thawed. Install new frost covers. Reattach the sewer from the temporary set up to the permanent sewer system as designed. | Construction Project | [9 empty] | Attachments | Other Documents | 2017-03-23 08:50
RMWTR-1680 | YKHC | Kongiganak | Allan Paukan | 2016-10-06 | 2016-10-06 | Routine | $340 |  |  |  | Ravn Connect | No |  | Name: John Phillip, Jr. Title/Position: Water Operator Accompanied By? Yes Telephonic Contact? No | [9 empty] | To bring a part to the water plant operator for the desludge pump for the lagoon. | After receiving a call from the WPO about having a problem with dewatering pump for the lagoon, he said he needed a reducer to complete connection for current operational pump. I told him I will travel the following morning after getting reducer. Oct 6 I departed with Ravn Connect. After arriving into Kongiganak I met the WPO at the water plant. We dropped my gear and proceeded to the lagoon to check on pumps that needed to be repaired. We looked at both the Godwin Pumps onsite. Unfortunately for Kongiganak the two pumps are manufactured in different countries and are unacceptable to swap parts to get one running. It also makes it difficult to locate parts. We were unsuccessful in getting a Godwin pump running. The WPO is using another pump from ADEC-FCO but is slow in dewatering the lagoon. I will research where we could locate the proper parts needed. With all tasks scompleted I departed on the evening schedule of Ravn Connect. I departed from Bethel the following day after checking in with the offrice. | 3 | The lagoon at the time was close to overflowing the dike wall. The parts for either Godwin pump needs to be purchased for future need to dewater the lagoon. |  |  |  |  | None at this time. | No |  | No |  | No |  | No |  | No | See if the correct parts were ordered after they arrive into Kongiganak. | Operator | [9 empty] | N/A | Other Documents | 2017-03-23 10:50
RMWTR-1681 | YKHC | Bethel | Allan Paukan | 2016-10-12 | 2016-10-14 | Other | $420 | $144 |  |  | Ravn Connect | No |  | Name: Robert White Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Shane McIntyre Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | [8 empty] | Assist RMW White with installing plumbing and electrical controls for Gray Water Research facility. | During the prior weeks training RMW White and I scheduled time to complete the plumbing needed for gray water research project. Due to high travel out of St. Mary's I finally made it out the 12th. Once into Bethel RMW McIntyre picked me up from the airport and we proceeded to the warehouse. Once at the ware house we made a parts list and got the necessary plumbing parts to complete the gray water research plumbing and electrical controls. We went along ways but did not quite finish the electrical control installation. With the week completed I departed on the evening flight of Ravn Connect on the 14th. We will schedule a future date to complete the graywater research plumbing. | 0 | Nnoen at this time. |  |  |  |  | None at this time. | No |  | No |  | No |  | No |  | No | None at this time. | Unknown | [9 empty] | N/A | Other Documents | 2017-03-24 08:25
RMWTR-1682 | YKHC | Mekoryuk | Allan Paukan | 2016-08-03 | 2016-08-03 | Other | $550 |  |  |  | Ravn Connect | No |  | Name: Alyssa Gustafson Title/Position: Environmental Health Officer Accompanied By? Yes Telephonic Contact? No | Name: Marka Peterson Title/Position: Water Operator Accompanied By? Yes Telephonic Contact? No | [8 empty] | To assist with a water plant survey. Also to assist with clinic survey. | After EHO Gustafson scheduled a trip with the WPO, we departed on the morning schedule of Ravn Connect. Once into Mekoryuk the WPO met us at the water plant. At the water plant we completed the water plant survey, I answered any questions both of them had for facility. This took about two hours. We then went to the clinic and completed the clinic maintenance survey. All deficiencies are listed in EHO Gustafson report. With all objectives complete we departed for Bethel on the evening schedule of Ravn Connect. | 0 | For the clinic, the outside sewer collection houses needs to be reveled. |  |  |  |  | none at this time. | No |  | No |  | No |  | No |  | No | Check with WPO if the community conducted the releveling the sewer houses needed. | Operator | [9 empty] | N/A | Other Documents | 2017-03-24 09:51
RMWTR-1683 | YKHC | Kwigillingok | Allan Paukan | 2016-08-02 | 2016-08-02 | Other | $0 |  |  |  | YKHC Charter | No |  | Name: Elizabeth Buckingham Title/Position: Environmental Health Officer Accompanied By? Yes Telephonic Contact? No | [9 empty] | Accompany EHO on clinic survey, | Accompanied EHO to Kwigillingok to complete clinic survey for the maintenance deficiencies of clinic. All notes were compiled by EHO. After survey done we jumped on charter to Kongiganak. | 0 | None at this time. |  |  |  |  | None at this time. | No |  | No |  | No |  | No |  | No | None at thsi time. | Other | [9 empty] | N/A | Other Documents | 2017-03-24 10:00
RMWTR-1684 | YKHC | Kongiganak | Allan Paukan | 2016-08-02 | 2016-08-02 | Other | $0 |  |  |  | YKHC Charter | No |  | Name: Elizabeth Buckingham Title/Position: Environmental Health Officer Accompanied By? Yes Telephonic Contact? No | [9 empty] | Clinic survey with EHO. | This was a trip that went on a three village visit with a YKHC charter and Kongiganak was the last of three villages. We went to the Kongiganak clinc that was one of the oldest in the YKHC region. We completed the survey for this clinic, all noted problems were recorded by EHO. We departed on the YKHC Charter back to Bethel. | 0 | None at this time. |  |  |  |  | None at this time. | No |  | No |  | No |  | No |  | No | None at this time. | Other | [9 empty] | N/A | Other Documents | 2017-03-24 10:29
RMWTR-1685 | YKHC | Kipnuk | Allan Paukan | 2016-08-02 | 2016-08-02 | Other | $0 |  |  |  | YKHC Charter | No |  | Name: Elizabeth Buckingham Title/Position: Environmental Health Officer Accompanied By? Yes Telephonic Contact? No | [9 empty] | Conduct a clinic survey for YKHC. | Completed a clinic survey for Kipnuk with EHO. This was the first of a three village visit. We inspected all of the clinic and its components and EHO notated problems. After the clinic survey was complete we met the charter at the airport to continue trip. | 0 | None at this time. |  |  |  |  | None at this time. | No |  | No |  | No |  | No |  | No | None at this time. | Unknown | [9 empty] | N/A | Other Documents | 2017-03-24 10:37
RMWTR-1686 | YKHC | Chevak | Allan Paukan | 2016-07-06 | 2016-07-08 | Other | $920 | $144 |  |  | Ravn Connect | No |  | Name: Elizabeth Buckingham Title/Position: Environmental Health Officer Accompanied By? Yes Telephonic Contact? No | [9 empty] | Conduct a clinic survey. | After EHO scheduled trip for Chevak I met her in Bethel for the morning flight of Ravn on the 7th of July. After arriving into Chevak the Chevak Clinic Maintenance man picked us up from the airport and we went to clinic to inspect the entire facility. All deficiencies were notated by EHO. Once the clinic survey was done we went to the water plant for the rest of the day to conduct a walk thru. The WPO brought us to the airport when it was time to leave on the evening schedule. | 0 | None at this time. |  |  |  |  | None at this time. | No |  | No |  | No |  | No |  | No | None at this time. | Unknown | [9 empty] | N/A | Other Documents | 2017-03-24 10:56
RMWTR-1687 | YKHC | Chefornak | Allan Paukan | 2016-07-26 | 2016-07-28 | Other | $840 |  |  |  | Ravn Connect | No |  | Name: Michael Vicente Title/Position: Environmental Health Officer Accompanied By? Yes Telephonic Contact? No | [9 empty] | Conduct clinic survey with YKHC EHO. | After EHO scheduled trip for us, I departed St. Mary's the 25th and met EHO Vicnte on the morning of the 26th. Once into Chefornak the WPO picked us up from the airport and brought us to the clinic where we completed clinic survey. The WHO notated all problems with the clinic. After the clinic survey was completed the WPO picked us up and we completed a walk thru of water plant and washeteria. We got on the evening schedule back to Bethel. In Bethel I completed clerical and gray water work. I departed home on the 28th. | 0 | None at this time. |  |  |  |  | None at this time. | No |  | No |  | No |  | No |  | No | None at this time. | Other | [9 empty] | N/A | Other Documents | 2017-03-24 11:06
RMWTR-1691 | TCC | Ruby | Lee Meckel | 2017-02-15 | 2017-02-17 | Training/Meeting | [5 empty] | No |  | Name: Malcomb Nickoli Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Ryan Madros Title/Position: Other Accompanied By? No Telephonic Contact? No | [8 empty] | Respond to Ruby/Operator phone call to assist thawing out sewer. | Ruby has had issues in the past with the ground moving and sinking along the sewer line. The sewer is fed to the lift station via a gravity main. Then once to the lift station the effluent is assisted by the lift station pumps up a slight grade towards the lagoon, where it takes a 90 degree turn under the road and discharges into the lagoon. The section of sewer that was frozen and uncooperative is within 60ft of the 90 degree bend that goes under the road and to the lagoon. There is a manhole/access point for the sewer in between the 90 and the lagoon that also has effluent that accumulated and has frozen the majority of the diameter of the outlet pipe towards the lagoon. There is still a small amount of space that would allow partial flow. This same scenario has already been remedied once this winter by Mr. Nickoli with assistance from Clifford Cleaver, who has since moved away. They used a small portable hot water maker with a high pressure transfer pump that was no longer available to the operator. We had been told that there was a large hot box that had been used in the past on this same sewer line. Mr. Nickolai and I started looking for the hot box and located it at the local V.P.S.O. office. V.P.S.O. Mr. Nate Titus showed us the box and helped us cut the lock off of it so that we could use it. Once back at the water plant we were able to hook up water to test fire the hotbox. It did not work. We were able to ascertain the hotbox system was not getting fuel. The solenoid would not open in the fuel line. There was no literature on the model at the time and so I asked that the operator take down the make and model so that he may work with City officials to repair the hotbox. Mr. Nickoli had mentioned that they had also used a space heater in the past for freezes in the same area that was frozen along the sewer force main but that the space heater they had used was no longer working. We asked the Tribe if we could barrow theirs and they were happy to help. After tracking down the space heater we attempted to fire it up and it would not start. Mr. Nickoli noticed that one of the rubber fuel lines was cracked and drawing air when trying to start. We brought the space heater to the city shop and took it apart. We located some fuel hose that was slightly larger in diameter then the old ones so I used some small hose clamps that I keep in my tool box to synch down the gaps in the new fuel line. I had to adjust the air intake on the blower fan to get the space heater to fire. Mr. Nickoli removed the man hole cover to access the 90 in the sewer so that the warm air could flow more freely towards the frozen section. We brought a generator to the 90 degree section in the road and found some old steel chimney stack and directed the hot air from the space heater down into the frozen sewer line at the 90 degree section. The following day Mr. Nickoli and I went over rough draft of template of a preventive maintenance plan. We are going to be implementing and adjusting the new plan and will continue to update until we have a finalized product that will help to keep operations running smoothly. We found some ¾” PEX that could house electrical heat trace so I had fellow RMW Mr. Kameroff purchase and ship some pre-assembled submersible heat trace to stick inside the pex after we capped off one end and then inserted the pex inside of the sewer main. I had to leave before the heat trace arrived but Mr. Nickoli let me know that he had made it about six feet and then had been pulled away from the sewer to pursue other duties. Mr. Nickoli has been using the septic pump truck to drain the lift station and discharge to the lagoon. | 16 | We need to thaw the sewer main with the hotbox. I have spoken briefly with Mr. Cody Uhlig of ANTHC regarding repairs that he and former RMW Mr. Arlo Bante had made in the past to correct the grade of the sewer main. We may have to consider another similar effort this summer to prevent similar issues. I will follow up with Mr. Uhlig to see if he has any additional insight. |  |  |  |  | There is also some water damage to the interior flooring and exterior flooring inside the bathrooms of the water plant from leaky plumbing in the past. The leaks are believed to have been fixed but the water damage needs to be repaired to prevent further damages to the building | No |  | No |  | No |  | No |  | No | There is also some water damage to the interior flooring and exterior flooring inside the bathrooms of the water plant from leaky plumbing in the past. The leaks are believed to have been fixed but the water damage needs to be repaired to prevent further damages to the building | Operator | [9 empty] | N/A | Other Documents | 2017-03-27 13:47
RMWTR-1692 | TCC | Nulato | Lee Meckel | 2017-02-22 | 2017-02-24 | Emergency | [5 empty] | No |  | Name: Greg Patsy Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Van Madros Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | [8 empty] | Thaw Nulato River frozen transmission line | I arrived to attempt to thaw well transmission line using PEX tubing and hot water. We opened well transmission line at the lower town site water plant. We hooked up to the school’s hot water system via double check valve and garden hoses. From the garden hoses we transitioned to ¾” PEX. We put the PEX into the well transmission line at the highest point by removing an auto vent. We then attached a discharge hose at a lower point to a water sample spigot valve in same transmission line so we could purge the water we added to line as it came back to the surface. The first day we made it 100 feet. The previous assumption by Mr. Patsy was that the pipe between the arctic pipe carrying the transmission line from the ground to the bottom of the building had become frozen. We had gone many times further than that distance leading Mr. Patsy to believe that freeze may be at a bend in the transmission line about 200’ away from the building. We had a 300’ role of pex that was due to arrive the following day so we went to the upper town site emergency well (known as the Blackberry Well) that fellow R.M.W. Mr. Shales had helped get online the week before while I was working in Ruby. When we got to the Blackberry Well I immediately noticed that a 2" air relief valve in the transmission line had freeze damage and the flow of water to the bleeder had been shut off by a valve to prevent leaking. The transmission line flows from well directly to upper town site distribution line and pressure pumps where it is valved off before entering the system. While the well pump was running in auto with the damaged air vent valved shut, the well began to draw down and was unable to recharge fast enough to keep up with the demand of the circulation system. The well then began picking up an air and water mixture which was then disbursed into the circulation system. The air was causing loss of pressure in distribution lines, and complaints of cloudy water among residents. The distribution lines became air locked and we began to lose adequate flow to homes on the highest point in each distribution circulation line in the upper town. We stopped the pressure pumps for a while to allow the air to settle and purge out throughout the distribution lines. We also changed many upper town site air release vents in the upper town site distribution system allowing air to better purge after the well came on line. We got the circulation and pressure pumps back and running. As a result of the added air the water being provided had some visible turbidity from the air. The water would quickly become clear once allowed to settle. The next day we thawed the lower town site well transmission line another 200' for a total of 300. We still had no flow. We decided to perform a pressure test on the glycol heat trace that was installed with the transmission line in the early 1990s, which no one was sure would work because it had not been used in over 20 years. We hooked up a compressor to the glycol heat trace piping. Then Mr. Madross and I pumped in air to test the integrity of the heat trace system. We brought the psi up to 30 and let it hold for an hour over lunch break. When we returned to the water plant the psi had dropped about five psi. We attributed this loss to cold air inside the line condensing. We added more air and waited overnight to see if it would hold. My final day in Nulato we noted that the psi had dropped slightly overnight but had held at 24psi for the reminder of my trip. We also opened up a valve on the return side of the glycol heat trace, and it released air with some glycol, which told us that the pipes were still connected all the way around the loop. I was able to get the glycol pressure pump for the heat trace running but only manually by holding down motor starter inside control panel. I also ran a windings and ground test on the Nulato River well pump and it all checked out. We did not know how much, if any glycol was left in the heat trace, which we computed could require as much as 1000 gallons. There was no additional glycol available at the water plant, but we did consider the possibility of filling the heat trace with hot water from the school. At this point, Mr. Patsy decided not to attempt any further work on getting the glycol heat trace working, and instead to focus on running the water system off the backup Blackberry well. | 16 | Mr. Brian Bearden TCC R.M.W. supervisor had found as built drawings of the Nulato River transmission line and let me know that there was no real grade to the well transmission line that would allow water to flow back towards the well in the event of pumping systems failure. This led me to believe the transmission line was either frozen solid the entire length or at the very least in multiple low spots along the way. |  |  |  |  | None not already mentioned. | No |  | No |  | No |  | No |  | No | Use glycol heat trace to thaw transmission line. | RMW | [9 empty] | N/A | Other Documents | 2017-03-27 14:03
RMWTR-1693 | YKHC | Lime Village | Bruce Werba | 2017-03-08 | 2017-03-08 | Other | $560 |  |  |  | Ak Scenic Air | No |  | Name: Mike Vicente Title/Position: Environmental Health Officer Accompanied By? Yes Telephonic Contact? No | Name: Asela Calhoun Title/Position: Other Accompanied By? Yes Telephonic Contact? No | Name: Ateline Mael Title/Position: Other Accompanied By? No Telephonic Contact? No | Name: Jennifer John Title/Position: Other Accompanied By? No Telephonic Contact? No | Name: Lori Bobby Title/Position: Tribal Council Member Accompanied By? Yes Telephonic Contact? No | [5 empty] | To inspect clinic to see if we could get it operational again. | I met them in Aniak, where we continued on with the YK clinic charter. Once into Lime we met with the YKHC Health Aid. We then inspected the clinic: the flooring needed new vinyl. We then got measurement for replacement. We then inspected each room for any maintenance needed, next was to the exterior of the building which needed front step releveling, needs paint. After the inspection we proceeded to the water plant and met with the Tribal Member about the clinic, after the locals left we made an administrative decision, of which the clinic would be moved closer to the utilities. We made an effort to meet with some of the locals with an objective to get local input on clinic start up but no one commented. With objective completed we headed towards the airport to meet the plane for Aniak. Where I was dropped off and caught a connecting plane to Holy Cross. | 0 | None at this time. |  |  |  |  | The building should not be used for the purpose of a clinic, better accommadations were found at the water plant. This would be no added cost for an entire building, that the village can not afford. | No |  | No |  | No |  | No |  | No | Nopne at this toime. | Other | [9 empty] | N/A | Other Documents | 2017-03-27 15:34
RMWTR-1695 | TCC | Nulato | Lee Meckel | 2017-03-01 | 2017-03-04 | Emergency | [5 empty] | No |  | Name: Greg Patsy Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Ryan Madros Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | [8 empty] | Thaw Nulato River Well | I arrived in Nulato and was greeted by Mr. Patsy at the airport. This was my second (and TCC’s third) trip to Nulato to assist with this situation. The purpose of this trip was to attempt to thaw the lower town site well by starting the old glycol heat trace system, which had not been used since the 1990s. Upon arrival we went to the lower town site treatment plant and located four 55 gallon drums of new glycol that we loaded up and brought inside. We added 25 gallons to the glycol heat trace system that runs alongside of the frozen well transmission line. We did not know how much glycol we would need to fill the line, which if empty would have required require 1,000 gallons, so we were a little surprised that it only took 25 gallons. The transmission line is close to a mile long and is also plumbed with a circulation loop to prevent this sort of freeze up. We found some leaks in this line at a union next to the circulation pump of the well transmission line that may have contributed to the failure of the circulation leading to the freeze. The next step of our plan was to see if the glycol heat trace would hold pressure after being filled (we had tested it with air on my previous trip). After using a ½ horse power pressure pump to pressure it up with the 25 gallons of fresh glycol, we focused our attention on the inline pressure pump for the heat trace system. The pump would not run in hand or auto mode. I could only get it running by manually holding down the thermal overload relay contactor while having the control box opened up. There are two pressure pumps mounted inline to run the glycol heat trace. One had been disconnected from power and removed from the plumbing to repair some rotting that had occurred to the floor beneath the pump. Inside the control box one of the thermal overload relays had been completely removed. We mounted the pump back in to the system but it still needs to be wired back to thermal overload relay motor starter in control box. I used my meter to trace the power and found an Allen Bradly relay was missing from control panel supplying the 120 volt portion of power. Mr. Madros quickly located an extra and the pressure pump started but in the hand mode only. The glycol pump started running and we had full circulation of the glycol loop from the heat exchanger being warmed by the boilers glycol. We let the glycol run overnight. The glycol loop that would be thawing the well transmission line was entering in the heat exchanger at 90 degrees and after traveling the mile there and back the glycol temperature returned at 33 degrees. The next day at 6:00 am we went up town to the emergency Blackberry well and turned on the pump and opened the freeze damaged valve that bled the air out of the transmission line to the upper town site circulation loop. Once the air was bled out at the Blackberry well head we went to the upper town site washateria where we opened a valve allowing the Blackberry well water to enter the upper town sites upper circulation system. To combat the additional air in the line that was not removed during our initial purge at the well head we shut down the pressure pumps in the upper town site to allow the air to purge in the array of auto air vents before and after the circulation pumps. Once that air is removed we powered up the pressure pumps back up to normal operational psi. The Blackberry Well is an emergency well that was never meant for continual operation, and had not previously been used for such a long period of time. We found that even after we had bled the air from the circulation system, additional air finds its way in and causes people’s homes at the highest points in both upper town circulation systems to lose water pressure and there is also noticeable turbidity that quickly settles out once exposed to the atmospheric pressure. While I was in town the water samples from Blackberry Well had returned clean, confirming that this turbidity is related to air entrainment. We found that once the air is purged the well produces water problem free for two to three hours, before beginning to become a problem again. What we figured was happening was that the aquifer is being drawn down faster than it can recover, which allows the well pump to start sucking in air. As a result, we began running the well on a schedule of three hours on and three hours off. Every morning the water level inside the holding tank was at 80% capacity so the system did work and allowed the town to freely use water. I was told many times that people could notice the difference in taste so I sampled for myself and there is a difference in taste though the water samples came back free of any contaminants. The pressure was on to thaw the lower town site well. We returned to the lower town site and noted that the temperature of the glycol was returning at 32 degrees and was leaving the heat exchanger supply at 74 degrees. We looked at a three way valve that wasn't working on the boiler supply side of the heat exchanger. Before glycol from the boiler side of the heat exchanger mixes with the glycol from the heat trace side it goes through a path regulated by a three way actuator or zone valve. The function of the three way valve was to regulate the temperature of the glycol going into the heat trace portion of the run, by the amount of hot glycol mixed with the cool return. This was installed so as not to damage the HDPE joint welds according to an old O&M. manual that surfaced the same day. We got the valve to operate in a manual mode however it was allowing the glycol to absorb too much heat. The operation manual had a warning not to exceed 130 degree supply. The actuator being disabled was allowing in temperature of 150 degrees. We trouble shot 3 way valve, found the thermostat that is connected to a thermocouple that senses the temp inside the outgoing side of the glycol heat exchanger. We set it for the recommended 130 degrees and got the actuator back on 3 way zone valve stem and fastened. We also redirected flow of the glycol heat trace using a series of four valves as recommended in the O.M. we had found the day before. It started to work as designed. The following morning we returned to the lower town site at 6:30 am after starting the Blackberry Well. The return was up to 34 degrees and going out at 130. We redirected the flow again. By 11:00 am the return was 37 degrees. Mr. Madros and I added glycol to make up lost pressure after the system had quit circulating due to airlock from the air bubbles in the glycol not being released. To ensure that the bubbles were purged we use our ½ horse pressure pump to add in new glycol from the 3-½ remaining 55 gallon drums. As we depleted the new glycol that was up to room temperature of about 76 degrees we added the old, very cold glycol back into the new glycol drums. This helped to heat up the glycol faster and purge the air that gets trapped in the cold glycol much faster. We repeated this step multiple times through the day always adding the ambient air-warmed glycol into the heat exchanger to maximize the effect. Around 9:30 pm Friday night the pressure pump for the heat trace shut down and quit working. Mr. Patsy checked the alarm panel and removed an under frequency voltage monitor relay from alarm panel and the motor started. We speculated that this may have contributed to what made the well circulation pump quit working leading to the original freeze. We also had to reset the breaker once to turn on the actuator motor on the three way valve. | 32 | We had debated about redirecting the inlet for Blackberry Well directly to the water storage tank as this would reduce the need for the air reducing procedures, but this would not eliminate the problem with the well recharge. |  |  |  |  | I would also like to wire up the other pressure pump for the glycol heat trace. | No |  | No |  | No |  | No |  | No | none | Operator | [9 empty] | N/A | Other Documents | 2017-03-28 15:12
RMWTR-1696 | TCC | Rampart | Lee Meckel | 2017-03-08 | 2017-03-10 | Training/Meeting | [5 empty] | No |  | Name: Ben Newman Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Mike Wiehl Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | [8 empty] | Assist with troubleshooting and repairing the new burner provided by ANTHC | I arrived and was greeted at the airport by Mr. Newman. We loaded up my tools and went to the water plant. We started discussing what had taken place with the burners since I had last been in Rampart. Mr. Newman gave me a tour of the energy upgrades that had been provided by ANTHC. Everything looked good and was working great with the exception of the burner on boiler #2. The new Becket burner that had been installed on boiler one was working as designed; it is the same burner and assembly kit. I trouble shot the boiler and was able to ascertain that tiger loop filter had been missing one of the smaller o-ring style gaskets. The high pressure line from the burner’s solenoid valve off the fuel pump was also letting in air do to faulty factory provided flair. We were able to replace the high pressure fuel line and swap filters with boiler one to try to fire boiler two. The boiler did not fire so I pulled out the drawer assembly and looked at the nozzle and I replaced it with a new one in case sediment from inside the fuel tank had gotten clogged inside the burner’s nozzle. I also made an adjustment to the electrodes based off of the 45 degree angle spray pattern that was provided by the nozzle. The boiler had gone into a hard lock out. We adjusted the fuel pressure using an old gage from the old Carlin burners. I used the old gage because the fuel line on the new one provided by ANTHC had a small kink in the line I believed may have contributed to an inaccurate reading of the fuel psi. We added some psi to the fuel pump coupled with the new nozzle and high pressure lines as well as the electrode adjustments. The boiler fired and ignited the entire amount of diesel that had been sprayed into the boiler causing a hard start that flung massive amounts of soot from the damper and stack pipe. The amount of soot was unusual for a boiler that had been cleaned this past summer. I realized then that the positioning of boiler two in such close proximity to boiler one had made the job of brushing out the “fingers” of the boiler nearly impossible. To remedy this we took apart the boilers skins and removed the plenum to access the internal cast iron. We also noted that the right side of the plenum had been missing bolts allowing soot and gas to escape when operating. We then gave it a true brush out and sealed it back up to reduce any amount of exhaust gas from leaking inside the boiler room. After these many adjustments I was able to get the boiler to cycle but not without back firing some soot and visible flame out the adjustable air band. The following day we went back to the boiler and decided to call Mr. Hartvigson of ANTHC. He had some helpful insight. I removed the burner and completely rebuilt it using the factory specifications from step one only to have it not fire at all. After rebuilding and researching the boiler I concluded that the blast tube itself may be the culprit in this particular burner. The blast tube has been dented in and deformed from the set screws that are supposed to hold it in place allowing the burner to hang at a greater angle than called for in the installation manual. This may be causing the spray pattern of the fuel to be hitting the roof of the boilers internal cavity causing the fuel to condense and drip back down instead of being aerated. Diesel needs to be aerated to ignite by the burner’s ignition transformer. There was a small electrical fire that had started under the school prior to my visit to Rampart. The fire had rendered some of the drain pipe to the interior plumbing frozen. Although this system is not a part of the public water system, the operator and other staff were busy working on this part-time while I was there, and I saw this as an opportunity to provide some relevant training. We went into the schools mechanical building and with some pex and a taco 007 series pump we were able to tap in to and old abandoned heating loop and add a pump and 15’ piece of ¾” pex to connect the supply and return sides of the glycol heat. The heat is still working and allowing the school to remain open. | 16 | Boiler 2 is out of commission. |  |  |  |  | Missing gasket in fuel filter. | No |  | No |  | No |  | No |  | No | Mr. Hartvigson has let me know that he plans to replace the entire burner or “Gun”. If he can get back out there and make it work that would be great. If it doesn’t work out we can always put the Carlin burner back on and look for a top notch burner like the Rielo. | RMW | [9 empty] | N/A | Other Documents | 2017-04-05 09:07
RMWTR-1698 | DEC | Nanwalek | Steve Evavold | 2017-03-21 | 2017-03-21 | Routine | $278 | $45 |  |  |  | No |  | Name: John Kvasnikoff Nanwalek 1st Chief Title/Position: Accompanied By? No Telephonic Contact? No | Name: John Moonin IRA Council Treasurer Title/Position: Accompanied By? No Telephonic Contact? No | Name: Gwen Kvasnikoff Tribal Administrator Title/Position: Accompanied By? No Telephonic Contact? No | Name: Emily Swenning IRA Housing Title/Position: Accompanied By? No Telephonic Contact? No | Name: Desiree Swenning IRA Council member Title/Position: Accompanied By? No Telephonic Contact? No | Name: Nick Tanape IRA Council Member Title/Position: Accompanied By? No Telephonic Contact? No | Name: Kelly Yeaton WTP Operator Title/Position: Accompanied By? No Telephonic Contact? No | Name: Brenton Alexander ANTHC PM Title/Position: Accompanied By? No Telephonic Contact? No | Name: Jeff Beatty VSW inspector/RMW Title/Position: Accompanied By? No Telephonic Contact? No | Name: Kevin Schoneman SouthCentral RMW Title/Position: Accompanied By? No Telephonic Contact? No | Trip was scheduled for WTP inspection and familiarization for DEC RMW and VSW project inspector; and to coincide with inspection of WTP project progress in Seldovia. | Arrived in Nanwalek and met with 1st Chief John Kvasnikoff, IRA council members, and other community representatives. We had asked for the meeting to discuss proposed projects, issues, and matters of concern in Nanwalek. There are several projects outlined in applications with BIA and ANTHC. Progress on the road construction to an area south of the community for a new landfill and septage lagoon has slowed due to allotment issues and approvals. The new septic tanks have not been pumped and a disposal site is getting critical. The current landfill is long past capacity. The PVC piped distribution system is aging and failing more on an annual basis in recent years. A 3 phase project is proposed by ANTHC, but approval with that is dependent on funding scoring, compliance, and staying on top of admin requirements. We discussed water loss and were made aware of a broken hydrant and a break in the PVC water main by the school. The small reservoir is influenced by hillside erosion and has significant reduced storage capacity. Low precipitation in recent years have caused water shortages for the large community of 280 and the school with 80 in attendance. The supplemental water source from a small runoff further up on another drainage needs improvement this spring. We adjourned the meeting and went up to the water plant. The water plant needs upgrades. Instrumentation and equipment for the polymer add system has failed. The SCD(Streaming Current Detector), and Milton Roy pump are no longer operational. The turbidimeters and controls for them are of concern. The 1720D model used for CFE turbidity is outdated and not longer supported by HACH. When calibrating turbidimeters I saw the 1720D used for raw water turbidity, has a corroded wiring harness and no longer works. Kelly, operator, wasn't able to use the air scour compressor in filter backwash; wasn't functioning correctly. Kevin worked on that, and found the belt needed adjusting and overall inspection. We backwashed the filters and saw that the air scour is operational. Kevin also replaced the light bulbs for filter observation. Jeff removed the flow meter/sensor for raw influent, cleaned the paddles, and returned the Signet monitor to recording flows. When done in the water plant we inspected the leaking hydrant on the north end of town. When hydrant replacement was done in 2001, this hydrant was operational. Also set in a concrete slab with bollards, we elected not to replace it at that time. We also checked on a leak reported on the east side of the school. The 3" PVC transmission line had cracked on a previous repair and again has cause a significant leak. We left at 1700. | 4 | The water plant is in need of serious upgrades in order to return to compliance with the SWTR and other issues as explained. The distribution system is in a deteriorated state and constant repairs are necessary. A critical hydrant, in close proximity to several houses, needs replacing. | The septic tanks need pumping this year, the new lagoon and landfill project needs priority level status. |  |  |  | As explained. | No |  | No |  | No |  | No |  | No | Scoring for funding applications and compliance needs regular attention. Community needs more aggressive communication with RMW, RUBA, and ANTHC representatives. | Community | [9 empty] | Attachments | Other Documents | 2017-04-11 10:04
RMWTR-1702 | YKHC | Bethel | Billy Westlock | 2017-03-12 | 2017-03-17 | Training/Meeting | $600 |  |  |  | Grant aviation | No |  | Name: Yk region operators Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Lksd region operstors Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | [8 empty] | Take the training on water treatment level 2. | I arrived into bethel on the twelth on March and attended a training every morning from Monday until the seventeenth. The trainer name Kay Curtin which she taught all week about water treatment. On Friday we took the exam and I departed bethel and arrived back to emmonak at about three p.m. | 32 | I was good to see many students trying to get a higher level of certification. |  |  |  |  | None at this time | No |  | No |  | No |  | No |  | No | None at this time | Unknown | [9 empty] | N/A | Other Documents | 2017-04-04 07:37
RMWTR-1704 | TCC | Huslia | Fred Kameroff | 2017-03-22 | 2017-03-23 | Routine | [5 empty] | No |  | Name: Darrell Vent Sr Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Derrick Star Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: Darrell Vent Jr Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | Name: Josh Olin Title/Position: Tribal Council Member Accompanied By? No Telephonic Contact? No | [6 empty] | Assist in replacing the Chemical exhaust fan; Diagnose and replace circulating pump | Mr. Darrell Vent Sr contacted me stating he has received the new chemical room exhaust fan and asked for my assistance on getting it replaced. I told him I could be there on 03/22/17. Also he wanted to replace the circulating pump on the airport loop. I arrived at Huslia on 03/22/17 and was greeted and escorted to the water plant by Josh Olin, Wrights Air agent. Mr. Olin contacted Mr. Vent Sr of my arrival on VHF radio. Mr. Vent Sr then came by and stated he had a teleconference he needs to get to and he would be available by 1pm. Mr. Vent Sr said the other two alternate operators will be here at 1pm also to help replace the exhaust fan. Mr. Derrick Star and Mr. Darrell Vent Jr came just after 1pm and we began to discuss the plan of action on the work that needed to be done. We started with the chemical room exhaust fan. Mr. Vent Sr and Mr. Star started to remove the worn out exhaust fan and the lower exhaust ducting, once that was all removed they started to install the new fan and screwed it in place and then the ducting for the fan. Once everything was put back in place I hooked up the power to the fan and turned on the power. The fan started to operate and we placed it in normal operation. Mr. Vent Sr also wanted to replace the circulating pump for the old airport loop. I asked him to turn on the pump and run it, the pump ran and operated normally and I could not find anything wrong with it. The pump stayed on the whole time I was there without any noise and operated normally. RECOMMENDATIONS/CONCLUSION Mr. Vent Sr stated if the circulating pump fails he will wait until late spring to have it replaced due to the fact that the main breaker controls both circulating pumps and he didn’t want to take a chance on getting any service line froze up. | 8 | none |  |  |  |  | none | No |  | No |  | No |  | No |  | No | water operator | Operator | [9 empty] | N/A | Other Documents | 2017-04-04 10:39
RMWTR-1706 | TCC | Northway | Lee Meckel | 2017-02-20 | 2017-02-21 | Training/Meeting | [5 empty] | No |  | Name: Terry Albert Title/Position: Water Operator Accompanied By? No Telephonic Contact? No | Name: Carl Carbon Title/Position: Other Accompanied By? No Telephonic Contact? No | Name: Harold Gene Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | [7 empty] | Install grit separator to well transmission line. | I arrived in Northway and was warmly greeted by the local water plant crew. We went down to the water plant and everything was already laid out waiting. We cut in to the well transmission line and added a few ¾” tees to house the grit separator and some valves and unions to service the grit separator in the future. We looked over our material list for the water storage tank in the back of the washateria to make any amendments to the proposed work we are planning to finish the week of March 20th. I had purchased some NSF 61 approved gasket rubber for the tank access hatch but it had not arrived in time. I will return to finish the repairs to transmission line entry point at the tank and give it a cleaning. | 8 | none |  |  |  |  | none | No |  | No |  | No |  | No |  | No | finish repairs | RMW | [9 empty] | N/A | Other Documents | 2017-04-05 09:31
RMWTR-1707 | TCC | Northway | Lee Meckel | 2017-03-20 | 2017-03-24 | Training/Meeting | [5 empty] | No |  | Name: Harold Gene Title/Position: Water Operator Backup Accompanied By? No Telephonic Contact? No | [9 empty] | Make repairs and clean washeteria water storage tank; move chlorination point in well transmission line. | I gathered plumbing materials and galvanized nuts bolts and washer from multiple vendors the morning before I departed Fairbanks. I arrived in Tok and called Mr. Gene to let him know that I was going to be there in the morning and we would be shutting down the washateria for repairs. The following morning I departed to Northway and was met by Mr. Terry, Mr. Carbon and Mr. Gene. We began working on draining the water storage tank (WST) that required repairs to the well transmission line where it enters the tank. The transmission line had undergone some repairs in the past and needed to be sealed at the point of entry to the WST. There were also issues with the float valve getting stuck open on the end of the transmission line inside the WST. In the past the valve had been known to stick open and cause the tank to overflow. The WST had bolts removed to allow the float valve to be worked on. The tank was still needing to be pieced back together to ensure that potential outside contaminates could not enter. We looked at the chlorination point and where best to move it upon the request of Mr. Albert (re wanted to relocate it to allow for the future removal of the unused filter vessels located behind the piping). We had a plan and focused on the repairs to the transmission line entering the WST. I started by removing the existing 2” galvanized pipe and old valve with broken handle. I removed the galvanized pipe that had been stuck through a larger diameter entry point to the tank. There used to be a custom flange that sealed the transmission line entry point but had since been abandoned. I noticed that the entrance point to the WST was slightly smaller than the new PVC flange I had purchased. Mr. Gene had helped me out by finding a circulator grinder with a cutting wheel that I was then able to use to cut in to the tank and expand the opening. I got the new entrance point about a 1/16” to a 1/32” smaller than the new flanges threads and used a file and pipe “reamer” to smooth the edges. I was able to thread the new flange in to the new cut I had made. The tank still had about a foot of water left to drain and Mr. Gene volunteered to stay at the plant until it was done draining. I removed the float valve and brought it to Tok so that I could soak it in a gallon of vinegar to help remove the scaling that had built up over the years. The following day we enlisted the help of a local man named Josh to help us with the actual tank cleaning. We called Mr. Bearden, TCC RMW supervisor to assist in the calculations for a chlorine tank cleaning solution. We proceeded to clean out the old sediment and rust that had built up on the spines that hold the tanks bolts in place, many of which were in very poor shape. To help better clean the tank I left to Tok to secure some wire brushes and a hard bristled push broom that could be sanitized and used in the cleaning of the WST. Mr. Gene and Mr. Josh were able to remove the majority of rust and all the buildup on the walls and floor of the WST. We used a shop vacuum to remove the small amount of water from the bottom of the tank and plumbed in the float valve to the new flange. Then we used the 200 mg/L chlorine solution to scrub the surface of the interior of the wst and let it sit overnight. There was a union that needed to be sweated off of the copper to allow enough copper exposed for a secure solder to the new dielectric union I would be using. Once I had the new union secured in place I measured out the 2” copper length I would need to complete the repair. I soldered one more end of the union to the new copper and used a crimping tool to secure a new 2” brass, lead free valve inline to the new tank flange. I had Mr. Gene and Mr. Josh bolt the tank back together while I plumbed the chlorine pump to its new location. We used the NSF approved gasket material I had purchased to seal the entry point to the tank and bolted it back together. We then wired up a new LMI chlorine pump that had been purchased. I had Mr. Gene and Mr. Josh assemble it as a training opportunity while I provided the splice to the power cord. We turned on the well pump when we were all done and noticed that the chlorine pump didn’t work. I checked my splice and it was fine. I traced the power using my electric meter from the control box and found that the outlet had no power. I traced the power lines from the outlet up through the conduit and through the electric gutters to a flow switch in the well transmission line. The wires to the flow switch had all been disconnected though no one seemed to remember doing it. Further examination revealed that the lock nut that holds the conduit in place to the flow switches housing had not been fastened. I believe that while working on the transmission line and tank that the ladder or one of us had bumped in to the overhead conduit and ripped the wires off of the terminals of the float switch. I reattached the conduit correctly and wired up the flow switch and the chlorine pump got power. I had to make some minor adjustment to the LMI pump and it started working. We dialed it in using the old pump’s settings. Mr. Gene checked his Chlorine levels and cross referenced them with his daily logs and found that they were almost the same as before we started. We had some leaks from the WST entry hatch where the new bolts held the hatch in place. We tighten up the leaky bolts and had to replace one with a new bolt because the threads had been stripped out allowing water to weep past the threading. We also had to tighten up the overhead union on the transmission line. | 32 | The repairs went smoothly. Mr. Gene is doing a great job of picking up where Mr. Albert had left off. Though he is new he is willing and able to accomplish his duties. |  |  |  |  | The WST hatch had a slow drip on one of the bolts. | No |  | No |  | No |  | No |  | No | If the tank hatch still has some leaking there is left over gasket materials that can be cut to size and be used as gaskets or washers to stop any additional leaking. I would also continue to evaluate the LMI pump setting as it is a newer model and may require different settings to meet the plants chlorine demand. | RMW | [9 empty] | N/A | Other Documents | 2017-04-05 09:22
RMWTR-1710 | YKHC | Bethel | Bruce Werba | 2017-03-21 | 2017-03-24 | Training/Meeting | $147 | $144 |  |  | Personal Vehicle | Yes | 340 miles | Name: Robert White Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | Name: Shane McIntyre Title/Position: RMW Accompanied By? Yes Telephonic Contact? No | [8 empty] | To assist the YKHC OEHE Training program with instructing the Boiler Maintenance training course. | With airlines being unpredictable lately I decided to travel to Bethel by snow machine. I departed for Bethel on the morning of the 20th. After a day of travel I arrived and stayed with family. The 21-23rd were the days the class was held at the RMW/ Gray Water Recycling Research Center. Class began after introductions. All instructional were hands on, this is giving the class real time environmental applications. The class room time should be real beneficial for the attendee's. | 0 | None at this time. |  |  |  |  | None at this time. | No |  | No |  | No |  | No |  | No | None at this time. | Other | [9 empty] | N/A | Other Documents | 2017-04-10 13:44