## Slide 1: CHAPTER 9
Sedimentation and Clarifiers

## Slide 2: Process Description
Sedimentation (or “clarification”) removes most of the particles from the water formed during coagulation and flocculation prior to sand filtration
The primary process is gravity settling in a sedimentation (settling) basin or tank
Also used to remove chemical precipitates formed during lime softening (see Chapter 16)
Monitoring of the influent (incoming) and effluent (outgoing) water is used to determine process efficiency
  Turbidity tests are a common monitoring parameter
Settling basins are designed for slow flow rates with a minimum of turbulence to prevent high velocity currents from inhibiting settling
  Short-circuiting: high velocity currents that inhibit proper settling
Notes: Background photo: closeup of a tube settler bundle in a package water treatment plant

## Slide 3: Sedimentation Facilities
Types of Basins:
Conventional rectangular basins
Conventional center-feed basins – circular or square, using radial flow
Peripheral-Feed basins
Spiral-Flow basins
Copyright © 2016 the American Water Works Association

## Slide 4: Rectangular Sedimentation Basins
Copyright © 2016 the American Water Works Association

## Slide 5: Sedimentation Basin Zones
Copyright © 2016 the American Water Works Association
Influent Zone – decreases velocity of incoming water
Settling Zone – quiescent settling area where particles settle
Effluent Zone – provides a smooth transition from the settling zone to the effluent channels
Sludge Zone – receives and manages the settled solids at the bottom of the basin

## Slide 6: Parts of a Sedimentation Basin
Copyright © 2016 the American Water Works Association

## Slide 7: Sedimentation Basin Weirs and Launders
Copyright © 2016 the American Water Works Association
Effluent weirs may be located at the circumference of a circular clarifier, at the end of a rectangular clarifier, or across the top of the clarifier
Weir plates can be flat or V-notched
Effluent troughs are also called launder channels
Notes: Background photo – picture of a large clarifier in a conventional surface water treatment plant in southcentral Alaska

## Slide 8: Shallow-Depth Sedimentation
Shallow Basins:
  Reduce the settling time of solids being separated
  May be constructed in multiple levels
  Designed on the principal that surface area is more important than depth
Plate and Tube Settlers:
  Usually constructed in modules
  Plates or tubes may be constructed of steel, fiberglass, or plastic (Figure 9-7)
  Set in at an angle from horizontal, ranging from 7° to over 60° (Figure 9-8)
  Steep angles (>50°) are self-cleaning (Figure 9-9)
  Plates or tubes are only a few inches apart and 3 to 6 feet in length (Figure 9-10)
  Plate settlers are also called Lamella®️ Plates (Figure 9-11)

## Slide 9: Tube Settlers
Copyright © 2016 the American Water Works Association

## Slide 10: Tube Settlers and Lamella®️ Plates
Copyright © 2016 the American Water Works Association

## Slide 11: Sludge Removal
Copyright © 2016 the American Water Works Association
Settled solids must be removed from the bottom of the sedimentation basin before they get too thick and to prevent resuspension of the particles
If the sludge remains in the bottom of the sedimentation basin too long, tastes and odors can develop

## Slide 12: Video Clip: Sedimentation and Clarifiers
www.awwa.org/wsovideoclips