## Read Me
Air Pollution Control Cost Estimation Spreadsheet
For Selective Catalytic Reduction (SCR)
U.S. Environmental Protection Agency
Air Economics Group
Health and Environmental Impacts Division
Office of Air Quality Planning and Standards
(May 2016)
This spreadsheet allows users to estimate the capital and annualized costs for installing and operating a Selective Catalytic Reduction (SCR) control device. SCR is a post-combustion control technology for reducing NOx emissions that employs a metal-based catalyst and an ammonia-based reducing reagent (urea or ammonia). The reagent reacts selectively with the flue gas NOx within a specific temperature range to produce N2 and water vapor.
The calculation methodologies used in this spreadsheet are those presented in the U.S. EPA's Air Pollution Control Cost Manual. This spreadsheet is intended to be used in combination with the SCR chapter and cost estimation methodology in the Control Cost Manual. For a detailed description of the SCR control technology and the cost methodologies, see Section 4, Chapter 2 of the Air Pollution Control Cost Manual (as updated in 2016). A copy of the Control Cost Manual is available on the U.S. EPA's "Technology Transfer Network" website at: http://www3.epa.gov/ttn/catc/products.html#cccinfo.
The spreadsheet can be used to estimate capital and annualized costs for applying SCR, and particularly to the following types of combustion units:
| (1) | Coal-fired utility boilers with full load capacities greater than or equal to 25 MW.
| (2) | Fuel oil- and natural gas-fired utility boilers with full load capacities greater than or equal to 25 MW.
| (3) | Coal-fired industrial boilers with maximum heat input capacities greater than or equal to 250 MMBtu/hour.
| (4) | Fuel oil- and natural gas-fired industrial boilers with maximum heat input capacities greater than or equal to 250 MMBtu/hour.
The methodology used in this spreadsheet is based on the U.S. EPA Clean Air Markets Division (CAMD)'s Integrated Planning Model (IPM) (version 5.13). The size and costs of the SCR are based primarily on five parameters: the boiler size or heat input, the type of fuel burned, the required level of NOx reduction, reagent consumption rate, and catalyst costs. The equations for utility boilers are identical to those used in the IPM. However, the equations for industrial boilers were developed based on the IPM equations for utility boilers. This approach provides study-level estimates (±30%) of SCR capital and annual costs. Default data in the spreadsheet is taken from the SCR Control Cost Manual and other sources such as the U.S. Energy Information Administration (EIA). The actual costs may vary from those calculated here due to site-specific conditions. Selection of the most cost-effective control option should be based on a detailed engineering study and cost quotations from system suppliers. For additional information regarding the IPM, see the EPA Clean Air Markets webpage at http://www.epa.gov/airmarkets/power-sector-modeling. The Agency wishes to note that all spreadsheet data inputs other than default data are merely available to show an example calculation.
Instructions
Step 1: Please select on the Data Inputs tab and click on the Reset Form button. This will clear many of the input cells and reset others to default values.
Step 2: Select the type of combustion unit (utility or industrial) using the pull down menu. Indicate whether the SCR is for new construction or retofit of an existing boiler. If the SCR will be installed on an existing boiler, enter a retrofit factor between 0.8 and 1.5. Use 1 for retrofits with an average level of difficulty. For the more difficult retrofits, you may use a retrofit factor greater than 1; however, you must document why the value used is appropriate.
Step 3: Select the type of fuel burned (coal, fuel oil, and natural gas) using the pull down menu. If you select fuel oil or natural gas, the HHV and NPHR fields will be prepopulated with default values. If you select coal, then you must complete the coal input box by first selecting the type of coal burned from the drop down menu. The weight percent sulfur content, HHV, and NPHR will be pre-populated with default factors based on the type of coal selected. However, we encourage you to enter your own values for these parameters, if they are known, since the actual fuel parameters may vary from the default values provided. Method 1 is pre-selected as the default method for calculating the catalyst replacement cost. For coal-fired units, you choose either method 1 or method 2 for calculating the catalyst replacement cost by selecting appropriate radio button.
Step 4: Complete all of the cells highlighted in yellow. If you do not know the catalyst volume (Volcatalyst) or flue gas flow rate (Qflue gas), please enter "UNK" and these values will be calculated for you. As noted in step 1 above, some of the highlighted cells are pre-populated with default values based on 2014 data. Users should document the source of all values entered in accordance with what is recommended in the Control Cost Manual, and the use of actual values other than the default values in this spreadsheet, if appropriately documented, is acceptable. You may also adjust the maintenance and administrative charges cost factors (cells highlighted in blue) from their default values of 0.005 and 0.03, respectively. The default values for these two factors were developed for the CAMD Integrated Planning Model (IPM). If you elect to adjust these factors, you must document why the alternative values used are appropriate.
Step 5: Once all of the data fields are complete, select the SCR Design Parameters tab to see the calculated design parameters and the Cost Estimate tab to view the calculated cost data for the installation and operation of the SCR.

## Data Inputs
Data Inputs
Enter the following data for your combustion unit:
Is the combustion unit a utility or industrial boiler? |  |  |  |  | What type of fuel does the unit burn?
Is the SCR for a new boiler or retrofit of an existing boiler?
Please enter a retrofit factor between 0.8 and 1.5 based on the level of difficulty. Enter 1 for projects of average retrofit difficulty. |  |  | 1.5 | * NOTE: You must document why a retrofit factor of 1.5 is appropriate for the proposed project.
Complete all of the highlighted data fields: | [13 empty] | 3 | Utility |  | 3 | New Construction
[5 empty] | Provide the following information for coal-fired boilers: | [9 empty] | Industrial |  |  | Retrofit
| What is the rating at full load capacity (MMBtu/hr)? | 495 | MMBtu/hr |  | Type of coal burned: | [12 empty] | SO2 Emission Rate (lbs SO2/MMBtu) = | 0.66138
[16 empty] | Bituminous |  | SO2 Emission Rate | 2
| What is the higher heating value (HHV) of the fuel? | 7560 | Btu/lb |  | Enter the sulfur content (%S) = |  |  | 0.25 | percent by weight |  |  |  |  | 1 |  | Sub-Bituminous | 3
Lignite
| What is the estimated actual annual fuel consumption? | 569114000 | lbs/year | [12 empty] | Coal blend
[5 empty] | For units burning coal blends: | [10 empty] | Not Applicable
[6 empty] | Note: The table below is pre-populated with default values for HHV and %S. Please enter the actual values for these parameters in the table below. If the actual value for any parameter is not known, you may use the default values provided. | [8 empty] | Coal
| Enter the net plant heat input rate (NPHR) | 11.833 | MMBtu/MW | [10 empty] | 2 | Fuel Oil
[8 empty] | Fraction in Coal Blend | %S | HHV (Btu/lb) |  |  |  |  | Natural Gas
| If the NPHR is not known, use the default NPHR value: | Fuel Type | Default NPHR |  |  | Bituminous |  | 0 | 2.35 | 11814
|  | Coal | 10 MMBtu/MW |  |  | Sub-Bituminous |  | 1 | 0.2 | 7560
|  | Fuel Oil | 11 MMBtu/MW |  |  | Lignite |  | 0 | 0.91 | 6534
|  | Natural Gas | 8.2 MMBtu/MW
Please click the calculate button to calculate weighted values based on the data in the table above.
| Plant Elevation | 450 | Feet above sea level
For coal-fired boilers, you may use either Method 1 or Method 2 to calculate the catalyst replacement cost. The equations for both methods are shown on rows 85 and 86 on the Cost Estimate tab. Please select your preferred method:
1
Enter the following design parameters for the proposed SCR:
| Number of days the SCR operates (tSCR) | 365 | days |  |  |  | Number of SCR reactor chambers (nscr) |  |  | 1
| Number of days the boiler operates (tplant) | 365 | days |  |  |  | Number of catalyst layers (Rlayer) |  |  | 3
| Inlet NOx Emissions (NOxin) to SCR | 0.402 | lb/MMBtu |  |  |  | Number of empty catalyst layers (Rempty) |  |  | 1
| NOx Removal Efficiency (EF) provided by vendor | 90 | percent |  |  |  | Ammonia Slip (Slip) provided by vendor |  |  | 10 | ppm
| Stoichiometric Ratio Factor (SRF) | 0.525 |  |  |  |  | Volume of the catalyst layers (Volcatalyst) (Enter "UNK" if value is not known) |  |  | UNK | Cubic feet
| *The SRF value of 0.525 is a default value. User should enter actual value, if known. | [5 empty] | Flue gas flow rate (Qfluegas) (Enter "UNK" if value is not known) |  |  | 162098.5 | acfm
| Estimated operating life of the catalyst (Hcatalyst) | 24000 | hours
| Estimated SCR equipment life | 20 | Years* |  |  |  | Gas temperature at the SCR inlet (T) |  |  | 310 | oF
| * For industrial boilers, the typical equipment life is between 20 and 25 years. | [5 empty] | Base case fuel gas volumetric flow rate factor (Qfuel) |  |  | 516 | ft3/min-MMBtu/hour
| Concentration of reagent as stored (Cstored) | 50 | percent* | *The reagent concentration of 50% and density of 71 lbs/cft are default values for urea reagent. User should enter actual values for reagent, if different from the default values provided.
| Density of reagent as stored (ρstored) | 71 | lb/cubic feet*
| Number of days reagent is stored (tstorage) | 30 | days | [5 empty] | Densities of typical SCR reagents:
[9 empty] | 50% urea solution |  | 71 | lbs/ft3
[9 empty] | 29.4% aqueous NH3 |  | 56 | lbs/ft3 |  |  | Ammonia
[9 empty] | 19% aqueous NH3 |  | 58 | lbs/ft3 |  | 2 | Urea
Select the reagent used
Enter the cost data for the proposed SCR:
| Desired dollar-year | 2016
| CEPCI for 2016 | 536.4 | Enter the CEPCI value for 2016 |  | 584.6 | 2012 CEPCI |  | CEPCI = Chemical Engineering Plant Cost Index
| Annual Interest Rate (i) | 5 | Percent
| Reagent (Costreag) | 1.62 | $/gallon for a 50 percent solution of urea
| Electricity (Costelect) | 0.21 | $/kWh
| Catalyst cost (CC replace) | 160 | $/cubic foot (includes removal and disposal/regeneration of existing catalyst and installation of new catalyst* |  |  |  |  | * $160/cf is a default value for the catalyst cost. User should enter actual value, if known.
| Operator Labor Rate | 60 | $/hour (including benefits)* |  |  |  |  | * $60/hour is a default value for the operator labor rate. User should enter actual value, if known.
| Operator Hours/Day | 4 | hours/day* |  |  |  |  | * 4 hours/day is a default value for the operator labor. User should enter actual value, if known.
Note: The use of CEPCI in this spreadsheet is not an endorsement of the index, but is there merely to allow for availability of a well-known cost index to spreadsheet users. Use of other well-known cost indexes (e.g., M&S) is acceptable.
Maintenance and Administrative Charges Cost Factors:
0.015
| Maintenance Cost Factor (MCF) = | 0.005
| Administrative Charges Factor (ACF) = | 0.03
Data Sources for Default Values Used in Calculations:
| Data Element | Default Value | Sources for Default Value | [5 empty] | If you used your own site-specific values, please enter the value used and the reference source . . . |  |  |  | Recommended data sources for site-specific information
| Reagent Cost ($/gallon) | 1.62 | Based on the average of vendor quotes from 2011 - 2013. | [9 empty] | Check with reagent vendors for current prices.
| Electricity Cost ($/kWh) | 0.039 | Average annual electricity cost for utilities is based on 2014 electricity production cost data for fossil-fuel plants compiled by the U.S. Energy Information (EIA). Available at http://www.eia.gov/tools/faqs/faq.cfm?id=19&t=3. | [5 empty] | $0.210/kWh GVEA rates. http://www.gvea.com/rates/rates |  |  |  | Plant's utility bill or use U.S. Energy Information Administration (EIA) data for most recent year. Available at http://www.eia.gov/electricity/data.cfm#sales.
| Percent sulfur content for Coal (% weight) | 0.31 | Average sulfur content based on U.S. coal data for 2014 compiled by the U.S. Energy Information Administration (EIA) from data reported on EIA Form EIA-923, Power Plant Operations Report. Available at http://www.eia.gov/electricity/data/eia923/. | [5 empty] | 0.20 percent (Typical Gross As Received). Coal data sheet at http://www.usibelli.com/Coal_data.php |  |  |  | Check with fuel supplier or use U.S. Energy Information Administration (EIA) data for most recent year." Available at http://www.eia.gov/electricity/data/eia923/.
| Higher Heating Value (HHV) (Btu/lb) | 8730 | 2014 coal data compiled by the Office of Oil, Gas, and Coal Supply Statistics, U.S. Energy Information Administration (EIA) from data reported on EIA Form EIA-923, Power Plant Operations Report. Available at http://www.eia.gov/electricity/data/eia923/. | [5 empty] | 7,560 Btu/lb (Typical Gross As Received). Coal data sheet at http://www.usibelli.com/Coal_data.php |  |  |  | Fuel supplier or use U.S. Energy Information Administration (EIA) data for most recent year." Available at http://www.eia.gov/electricity/data/eia923/.
| Catalyst Cost ($/cubic foot) | 160 | Cichanowicz, J.E. "Current Capital Cost and Cost-Effectiveness of Power Plant Emissions Control Technologies", July 2013. | [9 empty] | Check with vendors for current prices.
Reset Form
Calculate
Method 1
Method 2
Not applicable
Note on D7: Simpson, Aaron: No basis was provided to justify a retrofit factor reflecting greater than average difficulty for installation of selective catalytic reduction on the boilers. High retrofit cost factors may be justified in unusual circumstances (e.g., long and unique ductwork and piping, site preparation, tight fits, helicopter or crane installation, additional engineering, and asbestos abatement).
Note on C12: Simpson, Aaron: Typical Gross As Received. http://www.usibelli.com/coal/data-sheet
Note on I12: Simpson, Aaron: SIP Limit
Note on C33: Simpson, Aaron: Emission rate is average from two most recent NOx source tests accepted by the Department which occurred on November 19, 2011 and July 12, 2019.
Note on C34: Simpson, Aaron: EPA's Air Pollution Control Technology Fact Sheet indicating 70 - 90 percent control. https://www3.epa.gov/ttncatc1/dir1/fscr.pdf
Note on K36: Simpson, Aaron: April 7, 2016 Source Test
Note on K39: Simpson, Aaron: April 7, 2016 Source Test
Note on C56: Simpson, Aaron: GVEA rates. http://www.gvea.com/rates/rates

## SCR Design Parameters
SCR Design Parameters
The following design parameters for the SCR were calculated based on the values entered on the Data Inputs tab. These values were used to prepare the costs shown on the Cost Estimate tab.
Parameter | Equation | Calculated Value | Units
Maximum Annual Heat Input Rate (QB) = | HHV x Max. Fuel Rate = | 495 | MMBtu/hour
Maximum Annual fuel consumption (mfuel) = | (QB x 1.0E6 x 8760)/HHV = | 573571428.5714 | lbs/year
Actual Annual fuel consumption (Mactual) = |  | 569114000 | lbs/year
Heat Rate Factor (HRF) = | NPHR/10 = | 1.1833
Total System Capacity Factor (CFtotal) = | (Mactual/Mfuel) x (tscr/tplant) = | 0.99223 | fraction
Total operating time for the SCR (top) = | CFtotal x 8760 = | 8691.9229 | hours
NOx Removal Efficiency (EF) = | (NOxin- NOxout)/NOxin = | 90 | percent
NOx removed per hour = | NOxin x EF x QB = | 179.091 | lb/hour
Total NOx removed per year = | (NOxin x EF x QB x top)/2000 = | 778.3226 | tons/year
NOx removal factor (NRF) = | EF/80 | 1.125
Volumetric flue gas flow rate (qflue gas) = | Qfuel x QB x (460 + T)/(460 + 700)nscr | 162098.5 | acfm
Space velocity (Vspace) = | qflue gas/Volcatalyst | 24.5489 | /hour
Residence Time | 1/Vspace | 0.040735 | hour
Coal Factor (CoalF) = | 1 for oil and natural gas; 1 for bituminous; 1.05 for sub-bituminous; 1.07 for lignite (weighted average is used for coal blends) | 1.05 |  |  |  | 1.05 | CoalF for blended fuel
SO2 Emission rate = | (%S/100)x(64/32)*1E6)/HHV = | < 3 | lbs/MMBtu
Elevation Factor (ELEVF) = | 14.7 psia/P = |  |  | Not applicable; elevation factor does not apply to plants located at elevations below 500 feet.
Atmospheric pressure at sea level (P) = | 2116x[(59-(0.00356xh)+459.7)/518.6]5.256 x (1/144)* = | 14.4721 | psia
| SNCR Retrofit | 1.19
Retrofit Factor (RF) | Retrofit to existing boiler | 1.5
* Equation is from the National Aeronautics and Space Administration (NASA), Earth Atmosphere Model. Available at https://spaceflightsystems.grc.nasa.gov/education/rocket/atmos.html.
Catalyst Data:
Parameter | Equation | Calculated Value | Units |  |  | 1.2391 | EF adj
Future worth factor (FWF) = | (interest rate)(1/((1+ interest rate)Y -1) , where Y = Hcatalyts/(tSCR x 24 hours) rounded to the nearest integer | 0.31721 | Fraction |  |  | 0.7165 | Slipadj | 3
Catalyst volume (Volcatalyst) = | 2.81 x QB x EF adj x Slipadj x Noxadj x Sadj x (Tadj/Nscr) | 6603.0898 | Cubic feet |  |  | 0.98136 | Noxadj
Cross sectional area of the catalyst (Acatalyst) = | qflue gas /(16ft/sec x 60 sec/min) | 168.8526 | ft2 |  |  | 0.97498 | Sadj
Height of each catalyst layer (Hlayer) = | (Volcatalyst/(Rlayer x Acatalyst)) + 1 | 14.0352 | feet
[6 empty] | 5.5884 | Tadj
SCR Reactor Data:
Parameter | Equation | Calculated Value | Units
Cross sectional area of the reactor (ASCR) = | 1.15 x Acatalyst | 194.1805 | ft2
Reactor length and width dimentions for a square reactor = | (ASCR)0.5 | 13.9349 | feet
Reactor height = | (Rlayer + Rempty) x (7ft + hlayer) + 9ft | 93.1409 | feet
Reagent Data:
Type of reagent used | Urea | Molecular Weight of Reagent (MW) = |  | 60.06 | g/mole | 2 | 56
|  |  | Density = | 71 | lb/ft3
Parameter | Equation | Calculated Value | Units
Reagent consumption rate (mreagent) = | (NOxin x QB x EF x SFR x MWR)/MWNOx = | 122.7344 | lb/hour
Reagent Usage Rate (msol) = | mreagent/Csol = | 245.4687 | lb/hour
| (msol x 7.4805)/Reagent Density | 25.8624 | gal/hour
Estimated tank volume for reagent storage = | (msol x 7.4805 x tstorage x 24)/Reagent Density = | 18620.9112 | gallons (storage needed to store a 30 day reagent supply)
Capital Recovery Factor:
Parameter | Equation | Calculated Value
Capital Recovery Factor (CRF) = | i (1+ i)n/(1+ i)n - 1 = | 0.080243
Where n = Equipment Life and i= Interest Rate
Other parameters | Equation | Calculated Value | Units
Electricity Usage:
Electricity Consumption (P) = | A x 1,000 x 0.0056 x (CoalF x HRF)0.43 = | 304.3234 | kW
where A = (0.1 x QB) for industrial boilers.

## Cost Estimate
Cost Estimate
Total Capital Investment (TCI) |  |  |  |  | 1 | ELEVF
TCI for Oil and Natural Gas Boilers
For Oil and Natural Gas-Fired Utility Boilers between 25MW and 500 MW: |  |  |  |  | New | Retrofit
TCI = 80,000 x (200/BMW )0.35 x BMW x ELEVF x RF |  |  |  |  | 0 | 0
For Oil and Natural Gas-Fired Utility Boilers >500 MW:
TCI = 60,670 x BMW x ELEVF x RF |  |  |  |  | 0 | 0
For Oil-Fired Industrial Boilers between 275 and 5,500 MMBTU/hour :
TCI = 7,270 x (2,200/QB )0.35 x QB x ELEVF x RF |  |  |  |  | 0 | 0
For Natural Gas-Fired Industrial Boilers between 205 and 4,100 MMBTU/hour :
TCI = 9,760 x (1,640/QB )0.35 x QB x ELEVF x RF |  |  |  |  | 0 | 0
For Oil-Fired Industrial Boilers >5,500 MMBtu/hour:
TCI = 5,275 x QB x ELEVF x RF |  |  |  |  | 0 | 0
For Natural Gas-Fired Industrial Boilers >4,100 MMBtu/hour:
TCI = 7,082 x QB x ELEVF x RF |  |  |  |  | 0 | 0
Total Capital Investment (TCI) = | 0 |  | in 2016 dollars |  | 0 | 0
TCI for Coal-Fired Boilers
For Coal-Fired Boilers:
TCI = 1.3 x (SCRcost + RPC + APHC + BPC)
Capital costs for the SCR (SCRcost) = | 14416054.7833 |  | in 2016 dollars
Reagent Preparation Cost (RPC) = | 2467094.2302 |  | in 2016 dollars
Air Pre-Heater Costs (APHC)* = | 0 |  | in 2016 dollars
Balance of Plant Costs (BPC) = | 3327459.1925 |  | in 2016 dollars
Total Capital Investment (TCI) = | 26273790.6679 |  | in 2016 dollars
* Not applicable - This factor applies only to coal-fired boilers that burn bituminous coal and emits equal to or greater than 3lb/MMBtu of sulfur dioxide.
SCR Capital Costs (SCRcost)
For Coal-Fired Utility Boilers >25 MW:
SCRcost = 270,000 x (NRF)0.2 x (BMW x HRF x CoalF)0.92 x ELEVF x RF |  |  |  |  | 0 | 0
For Coal-Fired Industrial Boilers >250 MMBtu/hour:
SCRcost = 270,000 x (NRF)0.2 x (0.1 x QB x CoalF)0.92 x ELEVF x RF |  |  |  |  | 0 | 15711457.1706
[5 empty] | 0 | 15711457.1706
SCR Capital Costs (SCRcost) = |  |  | 14416054.7833 | in 2016 dollars
Reagent Preparation Costs (RPC)
For Coal-Fired Utility Boilers >25 MW:
RPC = 490,000 x (NOxin x BMW x NPHR x EF)0.25 x RF |  |  |  |  | 0 | 0
For Coal-Fired Industrial Boilers >250 MMBtu/hour:
RPC = 490,000 x (NOxin x QB x EF)0.25 x RF |  |  |  |  | 0 | 2688783.1599
Reagent Preparation Costs (RPC) = |  |  | 2467094.2302 | in 2016 dollars | 0 | 2688783.1599
Air Pre-Heater Costs (APHC)*
For Coal-Fired Utility Boilers >25MW:
APHC = 69,000 x (BMW x HRF x CoalF)0.78 x AHF x RF |  |  |  |  | 0 | 0
For Coal-Fired Industrial Boilers >250 MMBtu/hour:
APHC = 69,000 x (0.1 x QB x CoalF)0.78 x AHF x RF |  |  |  |  | 0 | 0
Air Pre-Heater Costs (APHcost) = |  |  | 0 | in 2016 dollars | 0 | 0
* Not applicable - This factor applies only to coal-fired boilers that burn bituminous coal and emit equal to or greater than 3lb/MMBtu of sulfur dioxide.
Balance of Plant Costs (BPC)
For Coal-Fired Utility Boilers >25MW:
BPC = 460,000 x (BMW x HRFx CoalF)0.42 x ELEVF x RF |  |  |  |  | 0 | 0
For Coal-Fired Industrial Boilers >250 MMBtu/hour:
BPC = 460,000 x (0.1 x QB x CoalF)0.42 ELEVF x RF |  |  |  |  | 0 | 3626459.0678
Balance of Plant Costs (BOPcost) = |  |  | 3327459.1925 | in 2016 dollars | 0 | 3626459.0678
Annual Costs
Total Annual Cost (TAC)
TAC = Direct Annual Costs + Indirect Annual Costs
Direct Annual Costs (DAC) = |  | 1162727.3219 | in 2016 dollars
Indirect Annual Costs (IDAC) = |  | 2112481.3659 | in 2016 dollars
Total annual costs (TAC) = DAC + IDAC |  | 3275208.6878 | in 2016 dollars
Direct Annual Costs (DAC)
DAC = (Annual Maintenance Cost) + (Annual Reagent Cost) + (Annual Electricity Cost) + (Annual Catalyst Cost)
Annual Maintenance Cost = | 0.005 x TCI = |  | 131368.9533 | in 2016 dollars
Annual Reagent Cost = | qsol x Costreag x top = |  | 364165.9314 | in 2016 dollars
Annual Electricity Cost = | P x Costelect x top = |  | 555482.7499 | in 2016 dollars
Annual Catalyst Replacement Cost = |  |  | 111709.6872 | in 2016 dollars
1
For coal-fired boilers, the following methods may be used to calcuate the catalyst replacement cost.
Method 1 (for all fuel types): | nscr x Volcat x (CCreplace/Rlayer) x FWF |  | * Calculation Method 1 selected. |  | Method 1 | 111709.6872
Method 2 (for coal-fired utility boilers): | BMW x 0.4 x (CoalF)2.9 x (NRF)0.71 x (CCreplace) x 35.3 |  |  |  | Method 2 (utility) | 3501604.9313
Method 2 (for coal-fired industrial boilers): | (QB/NPHR) x 0.4 x (CoalF)2.9 x (NRF)0.71 x (CCreplace) x 35.3 |  |  |  | Method 2 (industrial) | 295918.6116
Direct Annual Cost = |  |  | 1162727.3219 | in 2016 dollars |  | 295918.6116
Indirect Annual Cost (IDAC)
IDAC = Administrative Charges + Capital Recovery Costs
Administrative Charges (AC) = | 0.03 x (Operator Cost + 0.4 x Annual Maintenance Cost) = |  | 4204.4274 | in 2016 dollars
Capital Recovery Costs (CR)= | CRF x TCI = |  | 2108276.9385 | in 2016 dollars
Indirect Annual Cost (IDAC) = | AC + CR = |  | 2112481.3659 | in 2016 dollars
Cost Effectiveness
Cost Effectiveness = Total Annual Cost/ NOx Removed/year
Total Annual Cost (TAC) = |  | 3275208.6878 | per year in 2016 dollars
NOx Removed = |  | 778.3226 | tons/year
Cost Effectiveness = |  | 4208.035 | per ton of NOx removed in 2016 dollars

## ESRI_MAPINFO_SHEET (hidden)
DO NOT EDIT
For Esri use only