## 1a PTE Summary Base Case
Table 1a Emissions Summary - Base Case
Doyon Utilities and Fort Wainwright Garrison
Emission Unit Type | Regulated Air Pollutant Emissions (tons per year) 1,2
| NOX | CO | PM10 | PM2.5 3 | VOC | SO2 | HAP | GHG (CO2e) 4
Doyon Utilities
Coal Fired Boilers | 1478.4 |  |  | 131.376 |  | 1646.4
Emergency Engines and Generators | 53.9856 |  |  | 2.6311 |  | 2.8042
Coal Handling | 0 |  |  | 0.34151 |  | 0
Ash Handling | 0.42468 |  |  | 2.8312 |  | 0
Coal Pile | 0 |  |  | 3.2246 |  | 0
Facility Total | 1532.8103 | 0 | 0 | 140.4044 | 0 | 1649.2042
Fort Wainwright Garrison
Fuel Oil Boilers (EU 8,9,10,40) | 2.459 |  |  | 0.13278 |  | 7.5478
Emergency Engines | 14.7127 |  |  | 0.9889 |  | 1.0399
Emergency Generators | 10.6633 |  |  | 0.20928 |  | 3.9424
Waste Oil Boiler | 0.4161 |  |  | <0.01 |  | 6.4386
Facility Total | 28.2511 |  |  | 1.331 |  | 18.9687
Total | 1561.0614 | #REF! | #REF! | 141.7354 | #REF! | 1668.1728 | #REF! | #REF!
Notes:
1 Emissions are potential to emit as limited by the facility's Permit and EPA Guidance.
2 Regulated air pollutant calculations based on AP-42 emission factors, manufacturer data, source tests, and mass balances as shown in accompanying spreadsheets.
3 PM2.5 emissions are assumed to be equal to PM10 emissions except as noted on Tables 4-7.
5 Emission Units 1 through 6, 7a, 7b, 7c, 51a, and 51b at Fort Wainwright (Privatized Emission Units) have emission control devices.
EU 1 through 6, EU 51a, and 51b have baghouses. EU 7a through 7c have dust collectors.
Additionally, the insignificant emission unit "fly and bottom ash bin vent filter" has a dust collector.

## 1b PTE Summary BACT Proposed
Table 1b Emission Summary - As Proposed
Doyon Utilities and Fort Wainwright Garrison
Emission Unit Type | Regulated Air Pollutant Emissions (tons per year) 1,2
| NOX | CO | PM10 | PM2.5 3 | VOC | SO2 | HAP | GHG (CO2e) 4
Doyon Utilities
Coal Fired Boilers | 990 |  |  | 69 |  | 1050
Emergency Engines and Generators | 32.403 |  |  | 1.664 |  | 0.22294
Coal Handling | 0 |  |  | 0.051227 |  | 0
Ash Handling | 0 |  |  | 0.42468 |  | 0
Coal Pile |  |  |  | 3.22
Facility Total | 1022.403 | 0 | 0 | 74.3599 | 0 | 1050.2229
Fort Wainwright Garrison
Fuel Oil Boilers (EU 8,9,10,40) | 2.459 |  |  | 0.13278 |  | 7.5478
Emergency Engines | 14.7127 |  |  | 0.9889 |  | 1.0399
Emergency Generators | 10.6633 |  |  | 0.20928 |  | 3.9424
Waste Oil Boiler | 0.4161 |  |  | <0.01 |  | 6.4386
Facility Total | 28.2511 |  |  | 1.331 |  | 18.9687
Total | 1050.6541 | #REF! | #REF! | 75.6909 | #REF! | 1069.1916 | #REF! | #REF!
Notes:
1 Emissions are potential to emit as limited by the facility's Permit and EPA Guidance.
2 Regulated air pollutant calculations based on AP-42 emission factors, manufacturer data, source tests, and mass balances as shown in accompanying spreadsheets.
3 PM2.5 emissions are assumed to be equal to PM10 emissions except as noted on Tables XXX
5 Emission Units 1 through 6, 7a, 7b, 7c, 51a, and 51b at Fort Wainwright (Privatized Emission Units) have emission control devices.
EU 1 through 6, EU 51a, and 51b have baghouses. EU 7a through 7c have dust collectors.
Additionally, the insignificant emission unit "fly and bottom ash bin vent filter" has a dust collector.

## 3.1 Army AQ0236TVP03 Rev 2
Permit AQ0236TVP03 Emission Units
EU ID | Emission Unit Name | Description | Size | Rating | Installation or Construction Date
8 | Backup Diesel‐Fired Boiler 1 | Bassett Hospital | 19 | MMBtu/hr | Est 2003‐2004
9 | Backup Diesel‐Fired Boiler 2 | Bassett Hospital | 19 | MMBtu/hr | Est 2003‐2005
10 | Backup Diesel‐Fired Boiler 3 | Bassett Hospital | 19 | MMBtu/hr | Est 2003‐2006
40 | Boiler Building 5007 | Weil‐McLainBL‐988‐SW | 2.6 | MMBtu/hr | 1985
11 | Backup Diesel‐Electric Generator 1 | Bassett Hospital | 900 | kW | Est 2003‐2004
12 | Backup Diesel‐Electric Generator 2 | Bassett Hospital | 900 | kW | Est 2003‐2005
13 | Backup Diesel‐Electric Generator 3 | Bassett Hospital | 900 | kW | Est 2003‐2006
26 | Emergency Generator Bldg. 2132 | Cummins QSB7‐G5 NR3 | 324 | hp | 2012
27 | Emergency Generator Bldg. 1580 | John Deere 402HF285B | 67 | hp | 2009
28 | Emergency Generator Bldg. 3406 | Caterpillar C9 Genset | 398 | hp | 2007
29 | Emergency Generator Bldg. 3567 | SDMO TM30UCM | 47 | hp | 2005
30 | Fire Pump Building 2089 | John Deere 6081AF001 | 275 | hp | 2007
31 | Fire Pump #1 Building 1572 | Clarke DDFP‐04AT | 235 | hp | 1994
32 | Fire Pump #2 Building 1572 | Clarke DDFP‐04AT | 235 | hp | 1994
33 | Fire Pump #3 Building 1572 | Clarke DDFP‐04AT | 235 | hp | 1994
34 | Fire Pump #4 Building 1572 | Clarke DDFP‐04AT | 235 | hp | 1994
35 | Fire Pump #1 Building 2080 | Cummins N‐885‐F | 240 | hp | 1977
36 | Fire Pump #2 Building 2080 | Cummins N‐885‐F | 240 | hp | 1977
37 | Fire Pump Building 3498 | Clarke, JU4H‐UF40 | 105 | kW | 2005
38 | Fire Pump #1 Building 5009 | Clarke, PDFP‐06YT | 120 | hp | 1996
39 | Fire Pump #2 Building 5009 | Clarke, PDFP‐06YT | 120 | hp | 1996
22 | VOC Extraction and Combustion | Restoration Activities | N/A | - | 1993
23 | FWA Landfill | Landfill | 1.97 | million cubic meters | 1962
24 | Aerospace Activities | Painting and Degreasing | N/A | N/A | 1950's
- | Paved Roads | - | 8376750 | vehicle miles/yr | Various
- | Unpaved Roads | - | 23506 | vehicle miles/yr | Various

## Army VOC Sources (hidden)
Permit AQ0236TVP03 Emission Units | [9 empty] | Potential To Emit Calculations | [19 empty] | 201X Actual Emission Calculations
Permit | EU ID | Emission Unit Name | Description | Size | Rating | Installation or Construction Date | 201X Hours/Year | PTE Hours/Year | NOX Emission Control Device (if present) | NOX Emission Control Efficiency (%) | NOX Emission Control Efficiency Basis | NOX emission factor | NOX emission factor units | NOX emission factor basis | NOX emissions (TPY) | SO2 Emission Control Device (if present) | SO2 Emission Control Efficiency (%) | SO2 Emission Control Efficiency Basis | SO2 emission factor | SO2 emission factor units | SO2 emission factor basis | SO2 emissions (TPY) | PM2.5 Emission Control Device (If present) | PM2.5 Emission Control Efficiency (%) | PM2.5 Emission Control Efficiency Basis | PM2.5 emission factor | PM2.5 emission factor units | PM2.5 emission factor basis | PM2.5 emissions (TPY) | NOX Emission Control Efficiency (%) | NOX Emission Control Efficiency Basis | NOX emission factor | NOX emission factor units | NOX emission factor basis | NOX emissions (TPY) | SO2 Emission Control Device (if present) | SO2 Emission Control Efficiency (%) | SO2 Emission Control Efficiency Basis | SO2 emission factor | SO2 emission factor units | SO2 emission factor basis | SO2 emissions (TPY) | PM2.5 Emission Control Device (If present) | PM2.5 Emission Control Efficiency (%) | PM2.5 Emission Control Efficiency Basis | PM2.5 emission factor | PM2.5 emission factor units | PM2.5 emission factor basis | PM2.5 emissions (TPY)
AQ0236TVP03 | 22 | VOC Extraction and Combustion | Restoration Activities | N/A | - | 1993
AQ0236TVP03 | 23 | FWA Landfill | Landfill | 1.97 | million cubic meters | 1962
AQ0236TVP03 | 24 | Aerospace Activities | Painting and Degreasing | N/A | N/A | 1950's

## Army Boilers (hidden)
Permit AQ0236TVP03 Emission Units | [9 empty] | Potential To Emit Calculations | [19 empty] | 201X Actual Emission Calculations
Permit | EU ID | Emission Unit Name | Description | Size | Rating | Installation or Construction Date | 201X Hours/Year | PTE Hours/Year | NOX Emission Control Device (if present) | NOX Emission Control Efficiency (%) | NOX Emission Control Efficiency Basis | NOX emission factor | NOX emission factor units | NOX emission factor basis | NOX emissions (TPY) | SO2 Emission Control Device (if present) | SO2 Emission Control Efficiency (%) | SO2 Emission Control Efficiency Basis | SO2 emission factor | SO2 emission factor units | SO2 emission factor basis | SO2 emissions (TPY) | PM2.5 Emission Control Device (If present) | PM2.5 Emission Control Efficiency (%) | PM2.5 Emission Control Efficiency Basis | PM2.5 emission factor | PM2.5 emission factor units | PM2.5 emission factor basis | PM2.5 emissions (TPY) | NOX Emission Control Efficiency (%) | NOX Emission Control Efficiency Basis | NOX emission factor | NOX emission factor units | NOX emission factor basis | NOX emissions (TPY) | SO2 Emission Control Device (if present) | SO2 Emission Control Efficiency (%) | SO2 Emission Control Efficiency Basis | SO2 emission factor | SO2 emission factor units | SO2 emission factor basis | SO2 emissions (TPY) | PM2.5 Emission Control Device (If present) | PM2.5 Emission Control Efficiency (%) | PM2.5 Emission Control Efficiency Basis | PM2.5 emission factor | PM2.5 emission factor units | PM2.5 emission factor basis | PM2.5 emissions (TPY)
AQ0236TVP03 | 8 | Backup Diesel‐Fired Boiler 1 | Bassett Hospital | 19 | MMBtu/hr | Est 2003‐2004
AQ0236TVP03 | 9 | Backup Diesel‐Fired Boiler 2 | Bassett Hospital | 19 | MMBtu/hr | Est 2003‐2005
AQ0236TVP03 | 10 | Backup Diesel‐Fired Boiler 3 | Bassett Hospital | 19 | MMBtu/hr | Est 2003‐2006
AQ0236TVP03 | 40 | Boiler Building 5007 | Weil‐McLainBL‐988‐SW | 2.6 | MMBtu/hr | 1985

## 8 Fuel Oil Boiler FWA
A. BACKGROUND INFORMATION |  |  | Source: Forms D1 and D2 Rev 080913 (Ft. Wainwright)
| Fuel Type: |  | No. 1 Fuel Oil
| Calculation Method: |  | Emission Factors
| Fuel Oil Sulfur Content (%S): |  | 0.5
Source Classification Code (SCC):
SCC
| Commercial/Institutional Boilers (<10 MMBtu/hr) (Distillate Fuel Oil) |  |  |  | 1-03-005-03
| References: | 1. AP-42, 5th Edition, Compilation of Air Pollutant Emission Factors, Volume I: Stationary Point and Area Sources, May 2010
2. Alaska Department of Environmental Conservation Air Quality Permit AQ0236TVP02, 5 December 2008
| Notes: | Fuel oil sulfur content from Reference 2, Section 3, Requirement 13.1 (assumes all fuel oil burned by Fort Wainwright meets the same specification).
PTE for each of the 4076 back-up boilers is based on 200 hours of operation (or a third of the 600 hour ORL); heating value used is 137,000 Btu/gal.
B. EMISSION CALCULATION METHOD
| Boiler Size |  |  | Emission Factor (lbs/1,000 gal)1
|  |  |  | NOx | SO22 | CO | NMTOC | PM10 | CO2 | CH4 | N2O
| Distillate Oil-Fired Boilers (<10 MMBTU/hr) |  |  | 20 | 71 | 5 | 0.34 | 1.08 | 21500 | 0.216 | 0.26
1 Reference 1, Tables 1.3-1, 1.3-3, 1.3-6, 1.3-12 [No. 1 (kerosene)]
2 SO2 emissions factor = 142S, where S = weight % sulfur and assumed at 0.5% for all boilers except the building 4076 boilers at the hospital, which are permit-limited to 0.3%.
Emission Calculation:
Emissions (lbs/yr) = Fuel Use (gal/yr) x Emission Factor (lbs/1,000 gal)
C. EMISSION SUMMARY
EU | Building Number | Boiler Capacity (MMBtu/hr) | Potential Fuel Use1 (gal/yr) | Emissions (lbs/yr)
|  |  |  | NOx | SO2 | CO | NMTOC | PM10 | CO2 | CH4 | N2O
8 | 4076 | 19 | 27737.2263 | 554.7445 | 1181.6058 | 138.6861 | 9.4307 | 29.9562 | 269057.1429 | 2.7031 | 3.2537
9 | 4076 | 19 | 27737.2263 | 554.7445 | 1181.6058 | 138.6861 | 9.4307 | 29.9562 | 1210757.1429 | 12.1639 | 14.6417
10 | 4076 | 19 | 27737.2263 | 554.7445 | 1181.6058 | 138.6861 | 9.4307 | 29.9562 | 269057.1429 | 2.7031 | 3.2537
40 | 5007 | 2.6 | 162685.7143 | 3253.7143 | 11550.6857 | 813.4286 | 55.3131 | 175.7006 | 1748871.4286 | 17.5701 | 21.1491
|  |  | Significant Units Total (TPY) | 2.459 | 7.5478 | 0.61474 | 0.041803 | 0.13278
Emergency Boilers - assume 500 hours/year - Informational Only - These are Insignificant Sources within the Title V Permit.
| 5113 | 0.1 | 357.1429 | 7.1429 | 25.3571 | 1.7857 | 0.12143 | 0.38571 | 1748871.4286 | 17.5701 | 21.1491
| 5119 | 0.1 | 357.1429 | 7.1429 | 25.3571 | 1.7857 | 0.12143 | 0.38571 | 269057.1429 | 2.7031 | 3.2537
| 5175 | 0.1 | 357.1429 | 7.1429 | 25.3571 | 1.7857 | 0.12143 | 0.38571 | 538114.2857 | 5.4062 | 6.5074
| KDR | 0.1 | 357.1429 | 7.1429 | 25.3571 | 1.7857 | 0.12143 | 0.38571 | 538114.2857 | 5.4062 | 6.5074
| 1171 | 0.2 | 714.2857 | 14.2857 | 50.7143 | 3.5714 | 0.24286 | 0.77143 | 1076228.5714 | 10.8123 | 13.0149
| 1172 | 0.2 | 714.2857 | 14.2857 | 50.7143 | 3.5714 | 0.24286 | 0.77143 | 1076228.5714 | 10.8123 | 13.0149
| 1191 | 0.2 | 714.2857 | 14.2857 | 50.7143 | 3.5714 | 0.24286 | 0.77143 | 403585.7143 | 4.0546 | 4.8806
| 5009 | 0.2 | 714.2857 | 14.2857 | 50.7143 | 3.5714 | 0.24286 | 0.77143 | 596350.365 | 5.9912 | 7.2117
| 5109 | 0.2 | 714.2857 | 14.2857 | 50.7143 | 3.5714 | 0.24286 | 0.77143 | 596350.365 | 5.9912 | 7.2117
| 5110 | 0.2 | 714.2857 | 14.2857 | 50.7143 | 3.5714 | 0.24286 | 0.77143 | 596350.365 | 5.9912 | 7.2117
| 2400 | 0.3 | 1071.4286 | 21.4286 | 76.0714 | 5.3571 | 0.36429 | 1.1571 | 403585.7143 | 4.0546 | 4.8806
| 4321 | 0.3 | 1071.4286 | 21.4286 | 76.0714 | 5.3571 | 0.36429 | 1.1571 | 403585.7143 | 4.0546 | 4.8806
| 4322 | 0.3 | 1071.4286 | 21.4286 | 76.0714 | 5.3571 | 0.36429 | 1.1571 | 403585.7143 | 4.0546 | 4.8806
| 5003 | 0.3 | 1071.4286 | 21.4286 | 76.0714 | 5.3571 | 0.36429 | 1.1571 | 3363214.2857 | 33.7886 | 40.6714
| 2092 | 0.4 | 1428.5714 | 28.5714 | 101.4286 | 7.1429 | 0.48571 | 1.5429 | 538114.2857 | 5.4062 | 6.5074
| 2092 | 0.4 | 1428.5714 | 28.5714 | 101.4286 | 7.1429 | 0.48571 | 1.5429 | 269057.1429 | 2.7031 | 3.2537
| 5008 | 0.4 | 1428.5714 | 28.5714 | 101.4286 | 7.1429 | 0.48571 | 1.5429 | 1210757.1429 | 12.1639 | 14.6417
| 2096 | 0.8 | 2857.1429 | 57.1429 | 202.8571 | 14.2857 | 0.97143 | 3.0857 | 269057.1429 | 2.7031 | 3.2537
| 2096 | 0.8 | 2857.1429 | 57.1429 | 202.8571 | 14.2857 | 0.97143 | 3.0857 | 269057.1429 | 2.7031 | 3.2537
| 1172 | 0.9 | 3214.2857 | 64.2857 | 228.2143 | 16.0714 | 1.0929 | 3.4714 | 134528.5714 | 1.3515 | 1.6269
| 5010 | 0.9 | 3214.2857 | 64.2857 | 228.2143 | 16.0714 | 1.0929 | 3.4714 | 134528.5714 | 1.3515 | 1.6269
| 1185 | 1.3 | 4642.8571 | 92.8571 | 329.6429 | 23.2143 | 1.5786 | 5.0143 | 134528.5714 | 1.3515 | 1.6269
| 1185 | 1.3 | 4642.8571 | 92.8571 | 329.6429 | 23.2143 | 1.5786 | 5.0143 | 134528.5714 | 1.3515 | 1.6269
|  |  | Insignficant Unit Totals (TPY) | 0.35714 | 1.2679 | 0.089286 | 0.0060714 | 0.019286
| TOTAL EMISSIONS (TPY) |  |  | 2.8161 | 8.8156 | 0.70403 | 0.047874 | 0.15207 | 9302.5613 | 0.093458 | 0.1125
| TOTAL EMISSIONS (lbs/yr (NMTOC - VOCHAP)) | [5 empty] | 227.7
| TOTAL EMISSIONS (TPY (NMTOC - VOCHAP)) | [5 empty] | 0.11385
1 Potential Fuel Use is derived from boiler heat input rating as Boiler Rating BTU/hr X 8760 hr/140000 BTU/gal.
Potential fuel use for 4076 back-up boilers was calculated as 600 hr cumulative limit x 19 MMBTU/hour per boiler/ 137000 BTU/gallon/3 boilers = 27,737 gallons per boiler
Source: From D1 and D2 Revised 080913.xls provided 3/20/13
Note on C35: Deanne Hughes: Permit shows this as 2.6 MMBTU, Weil McLain BL-988-SW

## 9 Engines FWA PTE
A. | BACKGROUND INFORMATION |  |  | Source: Forms D1 and D2 Revised 080913 (Ft. Wainwright)
| Calculation Method: |  | Emission Factors
| Fuel Used: |  | #1 Fuel Oil
Source Classification Code (SCC):
| Internal Combustion Engines |  |  |  | SCC
| Diesel Internal Combustion Engines < 447 kW (600 hp) |  |  |  | 2-03-001-01
| References: | AP-42, 5th Edition, Compilation of Air Pollutant Emission Factors, Volume I: Stationary Point and Area Sources, October 1996
| Notes: | Potential to emit is based on 500 hour limit in USEPA Memorandum, September 6, 1995, "Calculating Potential to Emit (PTE) for Emergency Generators"
Building 2089 - John Deere Engine - Manufacturer information used
B. | EMISSION CALCULATION METHOD
Emission Factors for Uncontrolled Diesel Industrial Engines [Power Output (lb/hp-hr)]1
[7 empty] | NOx | SO2 | CO | VOC | PM10 | CO2
| John Deere 2089 Engine (g/hp-hr) | [5 empty] | 7.4 |  |  |  | 0.16
| Internal Combustion Engines < or = 447 kW (600 hp) | [5 empty] | 0.031 | 0.00205 | 0.00668 | 0.0025141 | 0.0022 | 1.15
1Reference, Table 3.3-1
Emission Calculation:
Emissions (lbs/yr) = Engine Rating (hp) x Operating Hours (hr/yr) x Emission Factor (lb/hp-hr)
C. EMISSION SUMMARY
EU | Building Number | Manufacturer | Manufacturer Year | Model Number | Engine Rating (hp) | Operating Hours (hr/yr) | Emissions (lbs/yr)
[7 empty] | NOx | SO2 | CO | VOC | PM10 a | CO2
31 | 1572 | Clarke | 1994 | DDFP-04AT | 235 | 500 | 3642.5 | 240.875 | 784.9 | 295.4067 | 258.5 | 135125
32 | 1572 | Clarke | 1994 | DDFP-04AT | 235 | 500 | 3642.5 | 240.875 | 784.9 | 295.4067 | 258.5 | 135125
33 | 1572 | Clarke | 1994 | DDFP-04AT | 235 | 500 | 3642.5 | 240.875 | 784.9 | 295.4067 | 258.5 | 135125
34 | 1572 | Clarke | 1994 | DDFP-04AT | 235 | 500 | 3642.5 | 240.875 | 784.9 | 295.4067 | 258.5 | 135125
35 | 2080 | Cummins | 1977 | N-855-F | 240 | 500 | 3720 | 246 | 801.6 | 301.692 | 264 | 138000
36 | 2080 | Cummins | 1977 | N-855-F | 240 | 500 | 3720 | 246 | 801.6 | 301.692 | 264 | 138000
30 | 2089 | John Deere | 2007 | JW64-UF30 | 275 | 500 | 2238.5 | 281.875 | 918.5 | 345.6888 | 48.4 | 158125
37 | 3498 | Clarke | 2005 | JU4H-UF40 | 94 | 500 | 1457 | 96.35 | 313.96 | 118.1627 | 103.4 | 54050
38 | 5009 | Clarke | 1996 | PDFP-06YT | 120 | 500 | 1860 | 123 | 400.8 | 150.846 | 132 | 69000
39 | 5009 | Clarke | 1996 | PDFP-06YT | 120 | 500 | 1860 | 123 | 400.8 | 150.846 | 132 | 69000
| TOTAL EMISSIONS (lbs/yr) | [5 empty] | 29425.5 | 2079.725 | 6776.86 | 2550.5544 | 1977.8 | 1718675
| TOTAL EMISSIONS (TPY) | [5 empty] | 14.7127 | 1.0399 | 3.3884 | 1.2753 | 0.9889 | 859.3375
a PM 2.5 is assumed to equal PM10.
Source: From D1 and D2 Revised 080913.xls provided 3/20/13

## 10 Emer Gen FWA PTE
A. | BACKGROUND INFORMATION
| Emission Year: |  | 2012
| Calculation Method: |  | Emission Factors | Source: Forms D1 and D2 Revised 080913
| Fuel Used: |  | #1 Fuel Oil
Source Classification Code (SCC):
| Internal Combustion Engines |  |  |  | SCC
| Diesel Internal Combustion Engines > 447 kW (600 hp) |  |  |  | 2-03-001-01
| Diesel Internal Combustion Engines < 447 kW (600 hp) |  |  |  | 2-03-001-01
| Notes: | Potential to emit hours were derived from the following:(a) 500 hour limit in USEPA Memorandum, September 6, 1995, "Calculating Potential to Emit (PTE) for Emergency Generators", and (b) 600 hour limit in current operating permit AQ0236TVP02 for Emission Units 11, 12, and 13 combined -- assumed 200 hours each.
B. | EMISSION CALCULATION METHOD
| Non Certified Engines (Emission factors in g/hp-hr) | [5 empty] | NOx | SO2 | CO | VOC | PM
| Cat 3512 - | [5 empty] | 9.4129 |  | 0.00668 | 0.0025141 | 0.1438
|  |  | (Emission factors in g/kW-hr, NOX is conservative as emission factor is Nox+NMHC) |  |  |  | Nox+HC | SO2 | CO | VOC | PM
| John Deere 4024HF285B, Tier 3 | [5 empty] | 4.7 |  |  |  | 0.4
| Cummins QSB7-G3 NR3 - Certified Engine (g/hp-hr) | [5 empty] | 4 |  | 0.0055 | 0.000705 | 0.02
| Cat C9, Tier 3 | [5 empty] | 4 |  |  |  | 0.2
| Conversion from hp to Kw |  |  | 1 horsepower | 0.7457 | kW
Emission Factors for Uncontrolled Diesel Industrial Engines [Power Output (lb/hp-hr)]1
[7 empty] | NOx | SO2 | CO | VOC | PM10 | CO2
| Internal Combustion Engines > 447 kW (600 hp) | [5 empty] | 0.024 | 0.00809 | 0.0055 | 0.000705 | 0.0004 | 1.16
| Internal Combustion Engines < or = 447 kW (600 hp) | [5 empty] | 0.031 | 0.00205 | 0.00668 | 0.0025141 | 0.0022 | 1.15
1Reference 1, Tables 3.3-1, 3.4-1 and 3.4-2.
| References: | AP-42, 5th Edition, Compilation of Air Pollutant Emission Factors, Volume I: Stationary Point and Area Sources, October 1996
Emission Calculation:
Emissions (lbs/yr) = Engine Rating (hp) x Operating Hours (hr/yr) x Emission Factor (g/hp/hr) x (kg/1000 g) * (2.2 lb/kg)
Emissions (lbs/yr) = Engine Rating (hp) x Operating Hours (hr/yr) x Emission Factor (g/kw-hr) X (0.7457 kw/hp) * (kg/1000 g) * (2.2 lb/kg)
Emissions (lbs/yr) = Engine Rating (hp) x Operating Hours (hr/yr) x Emission Factor (lb/hp-hr)
C. EMISSION SUMMARY
EU ID | Building Number | Manufacturer | Manufacturer Year | Model Number | Engine Rating (hp) | Operating Hours (hr/yr) | Emissions (lbs/yr)
[7 empty] | NOx | SO2 | CO | VOC | PM10 a | CO2
26 | Hangar | Cummins | 2012 | QSB7-G3 NR3 | 295 | 500 | 967.9186 | 302.375 | 985.3 | 370.8297 | 3.5893 | 169625
27 | 1580 | John Deere | 2009 | 4024HF285B | 67 | 500 | 258.303 | 68.675 | 223.78 | 84.2224 | 21.9832 | 38525
28 | 3406 | Caterpillar | 2007 | CAT C9 GENSET | 398 | 500 | 1305.8698 | 407.95 | 1329.32 | 500.3059 | 65.2935 | 228850
29 | 3567 | SDMO | ND | TM30UCM | 47 | 500 | 728.5 | 48.175 | 156.98 | 59.0814 | 51.7 | 27025
11 | 4076, Bassett Hospital | Caterpillar | 2003 | 3512 | 1454 | 200 | 6022 | 2352.572 | 1599.4 | 205.014 | 92 | 337328
12 | 4076, Bassett Hospital | Caterpillar | 2003 | 3512 | 1454 | 200 | 6022 | 2352.572 | 1599.4 | 205.014 | 92 | 337328
13 | 4076, Bassett Hospital | Caterpillar | 2003 | 3512 | 1454 | 200 | 6022 | 2352.572 | 1599.4 | 205.014 | 92 | 337328
| TOTAL EMISSIONS (lbs/yr) | [5 empty] | 21326.5915 | 7884.891 | 7493.58 | 1629.4814 | 418.5661 | 1476009
| TOTAL EMISSIONS (TPY) | [5 empty] | 10.6633 | 3.9424 | 3.7468 | 0.81474 | 0.20928 | 738.0045
a PM 2.5 is assumed to equal PM10.
Source: From D1 and D2 Revised 080913.xls provided 3/20/13
Note on C12: Deanne Hughes: different assumption that Fort made -- it used 600 hours for each source
Note on E44: Deanne Hughes: Potential emissions revised for the first three engines to match certified status.
Note on F44: Deanne Hughes: Revised from 134 hp based on nameplate provided by Eric 4/18/17.
Note on F46: Changed from 334 to match Mfg. Information

## 11 Waste Oil Boiler-Criteria(P)
A. BACKGROUND INFORMATION |  |  |  | Document Source: Forms D1 and D2 revised 080913
| Calculation Method: |  | Emission Factors
| Fuel Used: |  | Waste oils
Source Classification Code (SCC)
SCC
| External Combustion, Waste Oil, Small Boiler |  |  | 1-03-013-02
| Reference: | 1. AP-42, 5th Edition, Compilation of Air Pollutant Emission Factors, Volume I: Stationary Point and Area Sources, October 1996
2. PI-02F Instructions, "Process Information: Combustion - Instructions", Indiana Department of Environmental Management, Office of Air Quality, October 2006.
| Notes: | Potential fuel use is calculated by nameplate fuel use rating (2.5 gal/hr) X 8760 hours per year X 2 units = 43,800 gal/year combined use.
B. EMISSION CALCULATION METHOD
Emission factors for waste oil combustors (lbs/1000 gal)1
[5 empty] | NOx | SOX2,4 | CO | TOC | PM103,4 | CO2
| Waste oil combustors, Small boilers |  |  |  | 19 | 294 | 5 | 1 | 15.3 | 22000
1 Reference 1, Tables 1.11-1, 1.11-2, 1.11-3
2 SOx emissions factor = 147S, where S = weight % sulfur: 147 X 2.0 = 294
3 PM10 emissions factor = 51A, where A = weight % ash: 51 X 0.3 = 15.3
4 Reference 2, Part C. Default value for S = 2.0 and for A = 0.3
Emission Calculation:
Emissions (lbs/yr) = Emission Factor (lbs/1,000 gal) x Fuel Used (gal/yr)
C. EMISSION SUMMARY
| Unit |  |  | Fuel Used (gals/yr) | NOx | SOx | CO | TOC | PM10 a | CO2
| Waste Oil Combustor, Small Boilers, Building 3476 |  |  | 43800 | 832.2 | 12877.2 | 219 | 43.8 |  | 963600
| TOTAL EMISSIONS (lbs/yr) |  |  |  | 832.2 | 12877.2 | 219 | 43.8 | 0 | 963600
| TOTAL EMISSIONS (TPY) |  |  |  | 0.4161 | 6.4386 | 0.1095 | 0.0219 | <0.01 | 481.8
a PM 2.5 is assumed to equal PM10.
Source: From D1 and D2 Revised 080913.xls provided 3/20/13

## Unpaved_RoadsREV (hidden)
FORT WAINWRIGHT - FAIRBANKS, AK
TITLE V RENEWAL APPLICATION - EMISSIONS CALCULATIONS
Document Source: Forms D1 and D2 revised 080913
Source ID(s):
Unpaved roads
Emission Calculation Basis:
a. The quantity of PM emissions from vehicles traveling on publicly accessible unpaved roads, dominated by light duty vehicles,
may be estimated using the equations in AP-42 Section 13.2.2 (November 2006).
| E | = | {[k(s/12)a x (S/30)d / (M/0.5)c] - C} x ((365-P)/365)
where: | E | = | annual average emission factor (lb/vehicle mile traveled (VMT))
| s | = | surface material silt content (%)
| M | = | surface material moisture content (%)
| S | = | mean vehicle speed (mph)
| C | = | emission factor for 1980's vehicle fleet exhaust, brake wear, and tire wear (lb/VMT)
| P | = | number of days with at least 0.01 in of precipitation during the averaging period
b. From AP-42 Table 13.2.2-2 (November, 2006) - Constants for Equations 1a and 1b (for Public Roads):
|  |  | PM2.5 | PM10 | PM
| k (lb/VMT) | = | 0.18 | 1.8 | 6
| a | = | 1 | 1 | 1
| c | = | 0.2 | 0.2 | 0.3
| d | = | 0.5 | 0.5 | 0.3
c. Silt content for the Fairbanks area is: |  |  | s | = | 11 | %
d. The surface material moisture content is: |  |  | M | = | 0.2 | %
(under dry, uncontrolled conditions)
e. The mean vehicle speed is: |  |  | S | = | 20 | mph
f. From AP-42 Table 13.2.2-4 (November, 2006) - Emission Factor for 1980's Vehicle Fleet Exhaust, Brake Wear, and Tire Wear:
|  |  | PM2.5 | PM10 | PM
| C (lb/VMT) | = | 0.00036 | 0.00047 | 0.00047
g. Assume that 7 months out of the year have snow packed on the roads. Add to those seven months (212 days), the mean
number of days with 0.01 inches of precipitation in the other 5 months (53 days from May through September).
Data from NOAA's Comparative Climatic Data for the U.S. through 2005 (http://www1.ncdc.noaa.gov/pub/data/ccd-data/CCD_2005.pdf).
| P | = | 265 | days
h. Total VMT/yr at Fort Wainwright:
|  |  | Unpaved roads in Cantonment Area | = | 32.2 | miles/day-vehicle
|  |  | Actual trips per day over cantonment unpaved roads | = | 1 | trip/day
|  |  | Potential trips per day over cantonment unpaved roads | = | 2 | trip/day
|  |  | Actual total VMT/yr | = | 11753
|  |  | Potential total VMT/yr | = | 23506
Emission Calculation Equations:
a. Emission factor for PM2.5 (lb/VMT) |  |  | = | {[k(s/12)a x (S/30)d / (M/0.5)c] - C} x ((365-P)/365)
|  |  | = | {[0.18(11/12)1 x (20/30)0.5 / (0.2/0.5)0.2 - 0.00036]} x ((365 - 106)/365)
|  |  | = | 0.044235
b. Emission factor for PM10 (lb/VMT) |  |  | = | {[k(s/12)a x (S/30)d / (M/0.5)c] - C} x ((365-P)/365)
|  |  | = | {[1.8(11/12)1 x (20/30)0.5 / (0.2/0.5)0.2 - 0.00047]} x ((365 - 106)/365)
|  |  | = | 0.44321
c. Emission factor for PM (lb/VMT) |  |  | = | {[k(s/12)a x (S/30)d / (M/0.5)c] - C} x ((365-P)/365)
|  |  | = | {[6(11/12)1 x (20/30)0.3 / (0.2/0.5)0.3 - 0.00047]} x ((365 - 106)/365)
|  |  | = | 1.7563
d. Emissions (ton/yr) |  |  | = | (pollutant emission factor, lb/VMT) x (VMT/yr) / (2,000 lb/ton)
Emission Summary:
Pollutant | Actual | Potential
| (ton/yr) | (ton/yr)
PM | 10.3208 | 20.6415
PM10 | 2.6045 | 5.209
PM2.5 | 0.25995 | 0.51989

## Paved_RoadsREV (hidden)
FORT WAINWRIGHT - FAIRBANKS, AK
TITLE V RENEWAL APPLICATION - EMISSIONS CALCULATIONS
Document Source: Forms D1 and D2 revised 080913
Source ID(s):
Paved roads
Emission Calculation Basis:
a. The quantity of PM emissions from resuspension of loose material on the road surface due to vehicle travel on a dry paved
road may be estimated using the equations in AP-42 Section 13.2.1 (November 2006).
| E | = | [k(sL/2)0.65 x (W/3)1.5 - C] x (1 - (P/4N))
where: | E | = | Annual average PM emission factor (lb/vehicle mile traveled (VMT))
| k | = | particle size multiplier for particle size range (lb/VMT)
| sL | = | road surface silt loading (g/m2)
| W | = | average weight (ton) of the vehicles traveling the road
| C | = | emission factor for 1980's vehicle fleet exhaust, brake wear, and tire wear (lb/VMT)
| P | = | number of days with at least 0.01 in of precipitation during the averaging period
| N | = | 365 days in the averaging period
b. From AP-42 Table 13.2.1-1 (November, 2006) - Particle Size Multipliers (k) for Paved Road Equation:
|  |  | PM2.5 | PM10 | PM
| k (lb/VMT) | = | 0.0024 | 0.016 | 0.082
c. Silt loading is estimated using the method in AP-42 Table 13.2.1-3 (November, 2006) - Ubiquitous Silt Loading Default Values with
Hot Spot Contributions from Anti-Skid Abrasives. Fairbanks, Alaska experiences 7 months out of the year in which the mean
temperature is below freezing.
| sL | = | (0.2 x 3 x (7/12)) + (0.2 x (5/12))
|  | = | 0.43333 | g/m2
d. The average weight of the Light Truck Fleet was obtained from www.nhtsa.gov/cars/rules/CAFÉ/LightTruckFleet.htm.
| W | = | 2.4 | ton
e. From AP-42 Table 13.2.1-2 (November, 2006) - Emission Factor for 1980's Vehicle Fleet Exhaust, Brake Wear, and Tire Wear:
|  |  | PM2.5 | PM10 | PM
| C (lb/VMT) | = | 0.00036 | 0.00047 | 0.00047
f. Assume that 7 months out of the year have snow packed on the roads. Add to those seven months (212 days), the mean number
of days with 0.01 inches of precipitation in the other 5 months (53 days from May through September).
Data from NOAA's Comparative Climatic Data for the U.S. through 2005 (http://www1.ncdc.noaa.gov/pub/data/ccd-data/CCD_2005.pdf).
| P | = | 265 | days
g. Total VMT/yr at Fort Wainwright:
|  | Number of registered vehicles at post | = | 10200 | vehicles
|  | Actual daily vehicles driving at post | = | 2550 | vehicles | (est. as 25% of registered vehicles)
|  | Potential daily vehicles driving at post | = | 5100 | vehicles | (est. as 50% of registered vehicles)
|  | Daily miles traveled by each vehicle | = | 4.5 | miles/day-vehicle
|  | Actual total VMT/yr | = | 4188375
|  | Potential total VMT/yr | = | 8376750
Emission Calculation Equations:
a. Emission factor for PM2.5 (lb/VMT) |  |  | = | [k(sL/2)0.65 x (W/3)1.5 - C] x (1 - (P/4N))
|  |  | = | [0.0024(1.32/2)0.65 x (2.4/3)1.5 - 0.00036] x (1 - (106/(4x365)))
|  |  | = | 0.00022549
b. Emission factor for PM10 (lb/VMT) |  |  | = | [k(sL/2)0.65 x (W/3)1.5 - C] x (1 - (P/4N))
|  |  | = | [0.016(1.32/2)0.65 x (2.4/3)1.5 - 0.00047] x (1 - (106/(4x365)))
|  |  | = | 0.003083
c. Emission factor for PM (lb/VMT) |  |  | = | [k(sL/2)0.65 x (W/3)1.5 - C] x (1 - (P/4N))
|  |  | = | [0.082(1.32/2)0.65 x (2.4/3)1.5 - 0.00047] x (1 - (106/(4x365)))
|  |  | = | 0.017387
d. Emissions (ton/yr) |  |  | = | (pollutant emission factor, lb/VMT) x (VMT/yr) / (2,000 lb/ton)
Emission Summary:
Pollutant | Actual | Potential
| (ton/yr) | (ton/yr)
PM | 36.4116 | 72.8233
PM10 | 6.4563 | 12.9126
PM2.5 | 0.47222 | 0.94443

## Army Engines (hidden)
Unit | What | Where | Size | Units | Date | Hours/Year for calculation of PTE |  |  |  | NOX | NOX |  |  | PM | PM |  | SO2 | SO2
[7 empty] | Subpart IIII? | NOX+NMHC |  | lb/hr | TPY | PM |  | lb/hr | TPY | SO2 | lb/hr | TPY
[8 empty] | g/hp-hr, unless noted |  |  |  | g/hp-hr, unless noted |  |  |  | g/hp-hr, unless noted
35 | Fire Pump #1 Building 2080 | Cummins N‐885‐F | 240 | hp | 1977 | 500
36 | Fire Pump #2 Building 2080 | Cummins N‐885‐F | 240 | hp | 1977 | 500
31 | Fire Pump #1 Building 1572 | Clarke DDFP‐04AT | 235 | hp | 1994 | 500
32 | Fire Pump #2 Building 1572 | Clarke DDFP‐04AT | 235 | hp | 1994 | 500
33 | Fire Pump #3 Building 1572 | Clarke DDFP‐04AT | 235 | hp | 1994 | 500
34 | Fire Pump #4 Building 1572 | Clarke DDFP‐04AT | 235 | hp | 1994 | 500
38 | Fire Pump #1 Building 5009 | Clarke, PDFP‐06YT | 120 | hp | 1996 | 500
39 | Fire Pump #2 Building 5009 | Clarke, PDFP‐06YT | 120 | hp | 1996 | 500
29 | Emergency Generator Bldg. 3567 | SDMO TM30UCM | 47 | hp | 2005 | 500
37 | Fire Pump Building 3498 | Clarke, JU4H‐UF40 | 105 | kW | 2005 | 500 | maybe | 7.8 | g/hp-hr |  |  | 0.6 | g/hp-hr
30 | Fire Pump Building 2089 | John Deere 6081AF001 | 275 | hp | 2007 | 500 |  | 7.8 | g/hp-hr |  |  | 0.4 | g/hp-hr
28 | Emergency Generator Bldg. 3406 | Caterpillar C9 Genset | 398 | hp | 2007 | 500 |  | 4 | g/kw-hr |  |  | 0.2 | g/kw-hr
27 | Emergency Generator Bldg. 1580 | John Deere 402HF285B | 67 | hp | 2009 | 500 |  | 4.7 | g/kw-hr |  |  | 0.4 | g/kw-hr
26 | Emergency Generator Bldg. 2132 | Cummins QSB7‐G5 NR3 | 324 | hp | 2012 | 500 |  | 4 | g/kw-hr |  |  | 0.2 | g/kw-hr
11 | Backup Diesel‐Electric Generator 1 | Bassett Hospital | 1207 | hp | Est 2003‐2004 | 200
12 | Backup Diesel‐Electric Generator 2 | Bassett Hospital | 1207 | hp | Est 2003‐2005 | 200 | maybe | 6.4 | g/kw-hr |  |  | 0.2 | g/kw-hr
13 | Backup Diesel‐Electric Generator 3 | Bassett Hospital | 1207 | hp | Est 2003‐2006 | 200 | maybe | 6.4 | g/kw-hr |  |  | 0.2 | g/kw-hr
Notes: Backup diesel electric generators 1 through 3 are limited to 600 hours/12 mo period as a group.
Fire Pumps and Emergency engines not otherwise limited in the Title V permit are assumed to have potential to emit based on 500 hours/year per EPA Memo

## Army Material Handling (hidden)
Permit AQ0236TVP03 Emission Units | [9 empty] | Potential To Emit Calculations | [19 empty] | 201X Actual Emission Calculations
Permit | EU ID | Emission Unit Name | Description | Size | Rating | Installation or Construction Date | 201X Hours/Year | PTE Hours/Year | NOX Emission Control Device (if present) | NOX Emission Control Efficiency (%) | NOX Emission Control Efficiency Basis | NOX emission factor | NOX emission factor units | NOX emission factor basis | NOX emissions (TPY) | SO2 Emission Control Device (if present) | SO2 Emission Control Efficiency (%) | SO2 Emission Control Efficiency Basis | SO2 emission factor | SO2 emission factor units | SO2 emission factor basis | SO2 emissions (TPY) | PM2.5 Emission Control Device (If present) | PM2.5 Emission Control Efficiency (%) | PM2.5 Emission Control Efficiency Basis | PM2.5 emission factor | PM2.5 emission factor units | PM2.5 emission factor basis | PM2.5 emissions (TPY) | NOX Emission Control Efficiency (%) | NOX Emission Control Efficiency Basis | NOX emission factor | NOX emission factor units | NOX emission factor basis | NOX emissions (TPY) | SO2 Emission Control Device (if present) | SO2 Emission Control Efficiency (%) | SO2 Emission Control Efficiency Basis | SO2 emission factor | SO2 emission factor units | SO2 emission factor basis | SO2 emissions (TPY) | PM2.5 Emission Control Device (If present) | PM2.5 Emission Control Efficiency (%) | PM2.5 Emission Control Efficiency Basis | PM2.5 emission factor | PM2.5 emission factor units | PM2.5 emission factor basis | PM2.5 emissions (TPY)
AQ0236TVP03 | - | Paved Roads | - | 8376750 | vehicle miles/yr | Various
AQ0236TVP03 | - | Unpaved Roads | - | 23506 | vehicle miles/yr | Various

## DU Permit AQ1121TVP02 Rev 2 (hidden)
[8 empty] | DOW |  |  |  | DOW | Dow | [7 empty] | DOW | Dow | [7 empty] | Dow | Dow
Permit AQ1121TVP02 Emission Units | [9 empty] | Potential To Emit Calculations | [25 empty] | 201X Actual Emission Calculations
Permit | EU ID | Emission Unit Name | Description | Size | Rating | Installation or Construction Date | Applicable ZZZZ requirement for area source | 201X Hours/Year | PTE Hours/Year | NOX Emission Control Efficiency (%) | NOX Emission Control Efficiency Basis | Source Test NOX Emission Factor | Source Test Reference | NOX emission factor | NOX emission factor units | NOX emission factor basis | NOX emissions (TPY) | SO2 Emission Control Device (if present) | SO2 Emission Control Efficiency (%) | SO2 Emission Control Efficiency Basis | Source Test SO2 Emission Factor | Source Test Reference | SO2 emission factor | SO2 emission factor units | SO2 emission factor basis | SO2 emissions (TPY) | PM2.5 Emission Control Device (If present) | PM2.5 Emission Control Efficiency (%) | PM2.5 Emission Control Efficiency Basis | Source Test PM2.5 Emission Factor | Source Test Reference | PM2.5 emission factor | PM2.5 emission factor units | PM2.5 emission factor basis | PM2.5 emissions (TPY) | NOX Emission Control Efficiency (%) | NOX Emission Control Efficiency Basis | NOX emission factor | NOX emission factor units | NOX emission factor basis | NOX emissions (TPY) | SO2 Emission Control Device (if present) | SO2 Emission Control Efficiency (%) | SO2 Emission Control Efficiency Basis | SO2 emission factor | SO2 emission factor units | SO2 emission factor basis | SO2 emissions (TPY) | PM2.5 Emission Control Device (If present) | PM2.5 Emission Control Efficiency (%) | PM2.5 Emission Control Efficiency Basis | PM2.5 emission factor | PM2.5 emission factor units | PM2.5 emission factor basis | PM2.5 emissions (TPY)
Coal Fired Boilers
AQ1121TVP02 | 1 | Coal‐Fired Boiler 3 | Central Heating & Power Plant | 230 | MMBtu/hr | 1953
AQ1121TVP02 | 2 | Coal‐Fired Boiler 4 | Central Heating & Power Plant | 230 | MMBtu/hr | 1953
AQ1121TVP02 | 3 | Coal‐Fired Boiler 5 | Central Heating & Power Plant | 230 | MMBtu/hr | 1953
AQ1121TVP02 | 4 | Coal‐Fired Boiler 6 | Central Heating & Power Plant | 230 | MMBtu/hr | 1953
AQ1121TVP02 | 5 | Coal‐Fired Boiler 7 | Central Heating & Power Plant | 230 | MMBtu/hr | 1953
AQ1121TVP02 | 6 | Coal‐Fired Boiler 8 | Central Heating & Power Plant | 230 | MMBtu/hr | 1953
Material Handling
AQ1121TVP02 | 7a | DC-01 | South Coal Handling Dust Collector | 13150 | acfm | 2001
AQ1121TVP02 | 7b | DC-02 | South Under‐bunker Dust Collector | 884 | acfm | 2005
AQ1121TVP02 | 7c | NDC-1 | North Coal Handling Dust Collector | 9250 | acfm | 2004
Emergency/Black Start Generators
AQ1121TVP02 | 8 | Black Start Generator Engine | Central Heating & Power Plant | 2937 | hp | 2009
AQ1121TVP02 | 9 | Emergency Generator Engine | Building 1032 | 353 | hp | 1988
AQ1121TVP02 | 10 | Emergency Generator Engine | Building 1060 | 762 | hp | 2010
AQ1121TVP02 | 11 | Emergency Generator Engine | Building 1060 | 762 | hp | 2010
AQ1121TVP02 | 12 | Emergency Generator Engine | Building 1193 | 82 | hp | 2002
AQ1121TVP02 | 13 | Emergency Generator Engine | Building 1555 | 587 | hp | 2008
AQ1121TVP02 | 14 | Emergency Generator Engine | Building 1563 | 320 | hp | 2008
AQ1121TVP02 | 15 | Emergency Generator Engine | Building 2117 | 1059 | hp | 2005
AQ1121TVP02 | 16 | Emergency Generator Engine | Building 2117 | 212 | hp | 2005
AQ1121TVP02 | 17 | Emergency Generator Engine | Building 2088 | 176 | hp | 2007
AQ1121TVP02 | 18 | Emergency Generator Engine | Building 2296 | 212 | hp | 2005
AQ1121TVP02 | 19 | Emergency Generator Engine | Building 3004 | 71 | hp | 2007
AQ1121TVP02 | 20 | Emergency Generator Engine | Building 3028 | 35 | hp | 1976
AQ1121TVP02 | 21 | Emergency Generator Engine | Building 3407 | 95 | hp | 2001
AQ1121TVP02 | 22 | Emergency Generator Engine | Building 3565 | 35 | hp | 1989
AQ1121TVP02 | 23 | Emergency Generator Engine | Building 3587 | 155 | hp | 2003
AQ1121TVP02 | 24 | Emergency Generator Engine | Building 3703 | 50 | hp | 1993
AQ1121TVP02 | 25 | Emergency Generator Engine | Building 5108 | 18 | hp | 2011
AQ1121TVP02 | 26 | Emergency Generator Engine | Building 1620 | 68 | hp | 2003
AQ1121TVP02 | 27 | Emergency Generator Engine | Building 1054 | 274 | hp | 2010
AQ1121TVP02 | 28 | Emergency Generator Engine | Building 4390 | 274 | hp | 2010
AQ1121TVP02 | 35 | Emergency Pump Engine | Building 4023 | 55 | hp | 2009
AQ1121TVP02 | 29 | Emergency Pump Engine | Building 1056 | 75 | hp | 1988
AQ1121TVP02 | 30 | Emergency Pump Engine | Building 3403 | 75 | hp | 1952
AQ1121TVP02 | 31 | Emergency Pump Engine | Building 3724 | 75 | hp | 1952
AQ1121TVP02 | 32 | Emergency Pump Engine | Building 4162 | 75 | hp | 1955
AQ1121TVP02 | 33 | Emergency Pump Engine | Building 1002 | 75 | hp | 1994
AQ1121TVP02 | 34 | Emergency Pump Engine | Building 3405 | 220 | hp | 1995
AQ1121TVP02 | 36 | Emergency Pump Engine | Building 3563 | 220 | hp | 1995
AQ1121TVP02 | 51a | DC-1 | Fly Ash Dust Collector | 3620 | acfm | 1993
AQ1121TVP02 | 51b | DC-2 | Bottom Ash Dust Collector | 3620 | acfm | 1994
AQ1121TVP02 | 52 | Coal Storage Pile | Central Heating & Power Plant | N/A | N/A | unknown
Table notes:
1. EU ID 13 was installed in 2008, but the engine build date is February 17, 1999.

## 3.2 DU Emission Units
Significant Emission Unit Parameters - Base Case
Doyon Utilities - Fort Wainwright (Privatized Emission Units)
Emission Unit |  |  | Fuel | Electrical Output Rating |  | Rating |  | Federally-Enforceable Limits or PTE Limits g
ID | Name | Description | Type
Significant Emission Units
1 | Coal-Fired Boiler 3 | Central Heat and Power Plant (CHPP) | Coal | N/A |  | 230 | MMBtu/hr | 336000 | ton coal/year combined d
2 | Coal-Fired Boiler 4 | CHPP | Coal | N/A |  | 230 | MMBtu/hr
3 | Coal-Fired Boiler 5 | CHPP | Coal | N/A |  | 230 | MMBtu/hr
4 | Coal-Fired Boiler 6 | CHPP | Coal | N/A |  | 230 | MMBtu/hr
5 | Coal-Fired Boiler 7 | CHPP | Coal | N/A |  | 230 | MMBtu/hr
6 | Coal-Fired Boiler 8 | CHPP | Coal | N/A |  | 230 | MMBtu/hr
7a | South Coal Handling Dust Collector (DC-01) | Airlanco 169-AST-8 | N/A | N/A |  | 13150 | acfma | 8584.8 | hr/yr g
7b | South Underbunker Dust Collector (DC-02) | Airlanco 16-AST | N/A | N/A |  | 884 | acfma | 8760 | hr/yr g
7c | North Coal Handling Dust Collector (NDC-1) | Dustex C67-10-547 | N/A | N/A |  | 9250 | acfma | 175.2 | hr/yr g
8 | Backup Generator Engine | Caterpillar 3516C | Distillate | 2000 | kW | 2937 | hpb | 500 | hr/yr e
9 | Generator Engine | Detroit 6V92 | Distillate | 250 | kW | 352.8947 | hpc | 500 | hr/yr f
10 | Generator Engine | Caterpillar C15 | Distillate | 500 | kW | 762 | hpb | 500 | hr/yr f
11 | Generator Engine | Caterpillar C15 | Distillate | 500 | kW | 762 | hpb | 500 | hr/yr f
12 | Generator Engine | Cummins B3.3 | Distillate | 50 | kW | 82 | hpb | 500 | hr/yr f
13 | Generator Engine | Caterpillar 3406C TA | Distillate | 400 | kW | 587 | hpb | 500 | hr/yr f
14 | Generator Engine | Cummins QSL-G2 NR3 | Distillate | 200 | kW | 320 | hpb | 500 | hr/yr f
15 | Generator Engine | Detroit R1237M36 | Distillate | 750 | kW | 1058.6842 | hpc | 500 | hr/yr f
16 | Generator Engine | John Deere 6068TF250 | Distillate | 150 | kW | 211.7368 | hpc | 500 | hr/yr f
17 | Generator Engine | John Deere 6068TF250 | Distillate | 125 | kW | 176.4474 | hpc | 500 | hr/yr f
18 | Generator Engine | John Deere 6068HF150 | Distillate | 150 | kW | 211.7368 | hpc | 500 | hr/yr f
19 | Generator Engine | John Deere 4045TF270 | Distillate | 50 | kW | 70.5789 | hpc | 500 | hr/yr f
20 | Generator Engine | John Deere 4239D | Distillate | 25 | kW | 35.2895 | hpc | 500 | hr/yr f
21 | Generator Engine | Perkins 2046/1800 | Distillate | 60 | kW | 95 | hpb | 500 | hr/yr f
22 | Generator Engine | Cummins | Distillate | 25 | kW | 35.2895 | hpc | 500 | hr/yr f
23 | Generator Engine | John Deere 6068HF150 | Distillate | 110 | kW | 155.2737 | hpc | 500 | hr/yr f
24 | Generator Engine | Cummins L634D-I/10386E | Distillate | 25 | kW | 50 | hpb | 500 | hr/yr f
25 | Generator Engine | Caterpillar C1.5 | Distillate | 13 | kW | 18.3505 | hpc | 500 | hr/yr f
26 | Generator Engine | Cummins 4B3.9-G2 | Distillate | 35 | kW | 68 | hpb | 500 | hr/yr f
27 | Generator Engine | Caterpillar C6.6 | Distillate | 175 | kW | 274 | hpb | 500 | hr/yr f
28 | Generator Engine | Caterpillar C6.6 | Distillate | 125 | kW | 274 | hpb | 500 | hr/yr f
29a | Lift Pump Engine | John Deere 4045TF290 | Distillate | N/A |  | 74 | hp | 500 | hr/yr f
30 | Lift Pump Engine | Detroit Diesel 10245100 | Distillate | N/A |  | 75 | hp | 500 | hr/yr f
31a | Lift Pump Engine | John Deere 4045TF290 | Distillate | N/A |  | 74 | hp | 500 | hr/yr f
32 | Lift Pump Engine | Perkins | Distillate | N/A |  | 75 | hp | 500 | hr/yr f
33 | Lift Pump Engine | Perkins | Distillate | N/A |  | 75 | hp | 500 | hr/yr f
34 | Well Pump Engine | Detroit Diesel 10447000 | Distillate | N/A |  | 220 | hp | 500 | hr/yr f
35 | Well Pump Engine | John Deere 4045DF120 | Distillate | N/A |  | 55 | hpb | 500 | hr/yr f
36 | Well Pump Engine | Detroit Diesel 4031-C | Distillate | N/A |  | 220 | hp | 500 | hr/yr f
51a | Fly Ash Dust Collector (DC-1) | United Conveyor Corp. 32242 | N/A | N/A |  | 3620 | acfma | 4380 | hr/yr h
51b | Bottom Ash Dust Collector (DC-2) | United Conveyor Corp. 32242 | N/A | N/A |  | 3620 | acfma | 4380 | hr/yr h
52 | Coal Storage Pile | CHPP | N/A | N/A |  | N/A |  | 82049 | tpy j
Insignificant Emission Units
N/A | Fly and Bottom Ash Bin Vent Filter | United Conveyor Corp 96TB-BVT-25:S6 | N/A | N/A |  | 1460 | acfma | 4380 | hr/yr h
N/A | Ash Loadout to Truck | N/A | N/A | N/A |  | N/A |  | 28560 | tpyf
N/A | Aboveground Storage Tanks | N/Ad | Diesel | N/A |  | N/A |  | N/A
N/A | Underground Storage Tanks | N/Ad | Diesel | N/A |  | N/A |  | N/A
Notes:
a Rating for dust collectors and vent filters is the manufacturer's design inlet gas flow rate in cubic feet per minute
b Engine rating from vendor data
c Engine rating in hp calculated from electrical output assuming 95% efficiency (hp=kW*1.341/.95).
d Maximum annual coal consumption, combined for Emissions Units 1 through 6, per AQ1121TVP01 Revision 3 Condition 11.1.
e Maximum annual operation for Emission Unit 8, per AQ1121TVP01 Revision 3 Condition 13.
f Annual operating hours for potential emissions are based on historical operating hours for emergency engines, EU IDs 9 through 37. Please refer to Table D-4.
g As calculated in Table D-1.7a
h As calculated in Table D-1.7b
i Multiple tanks, see Table D-1.3 for details
j As calculated in Table D-1.7c
Conversion factors:
| Engine horsepower | 1.341 | hp/kw
| Engine drive shaft efficiency | 95% | Per Alan Schuler at ADEC

## 2a DU NOx Base Case
Table XX -- Oxides of Nitrogen (NOX) Emissions - Base Case
Doyon Utilities - Fort Wainwright (Privatized Emission Units)
Emission Unit |  | Fuel | Factor | NOX Emission |  | Emission Unit |  | Allowable Annual |  | Potential
ID | Description | Type | Reference | Factor |  | Rating/Capacity |  | Operation |  | NOX Emissions
Significant Emission Units
1 | Coal-Fired Boiler 3 | Coal | AP-42, Table 1.1-3 | 8.8 | lb/ton | 230 | MMBtu/hr | 336000 | tpy | 1478.4 | tpy
2 | Coal-Fired Boiler 4 | Coal | AP-42, Table 1.1-3 | 8.8 | lb/ton | 230 | MMBtu/hr
3 | Coal-Fired Boiler 5 | Coal | AP-42, Table 1.1-3 | 8.8 | lb/ton | 230 | MMBtu/hr
4 | Coal-Fired Boiler 6 | Coal | AP-42, Table 1.1-3 | 8.8 | lb/ton | 230 | MMBtu/hr
5 | Coal-Fired Boiler 7 | Coal | AP-42, Table 1.1-3 | 8.8 | lb/ton | 230 | MMBtu/hr
6 | Coal-Fired Boiler 8 | Coal | AP-42, Table 1.1-3 | 8.8 | lb/ton | 230 | MMBtu/hr
7a | South Coal Handling Dust Collector (DC-01) | N/A | N/A | N | /A | 13150 | acfm | 2195.2 | hr/yr | 0 | tpy
7b | South Underbunker Dust Collector (DC-02) | N/A | N/A | N | /A | 884 | acfm | 100 | hr/yr | 0 | tpy
7c | North Coal Handling Dust Collector (NDC-1) | N/A | N/A | N | /A | 9250 | acfm | 44.8 | hr/yr | 0 | tpy
8 | Backup Generator Engine | Distillate | Vendor | 5.39 | g/hp-hr | 2937 | hp | 500 | hr/yr | 8.7249 | tpy
9 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 352.8947 | hp | 500 | hr/yr | 2.7349 | tpy
10 | Generator Engine | Distillate | AP-42, Table 3.4-1 | 0.024 | lb/hp-hr | 762 | hp | 500 | hr/yr | 4.572 | tpy
11 | Generator Engine | Distillate | AP-42, Table 3.4-1 | 0.024 | lb/hp-hr | 762 | hp | 500 | hr/yr | 4.572 | tpy
12 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 82 | hp | 500 | hr/yr | 0.6355 | tpy
13 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 587 | hp | 500 | hr/yr | 4.5492 | tpy
14 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 320 | hp | 500 | hr/yr | 2.48 | tpy
15 | Generator Engine | Distillate | AP-42, Table 3.4-1 | 0.024 | lb/hp-hr | 1058.6842 | hp | 500 | hr/yr | 6.3521 | tpy
16 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 211.7368 | hp | 500 | hr/yr | 1.641 | tpy
17 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 176.4474 | hp | 500 | hr/yr | 1.3675 | tpy
18 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 211.7368 | hp | 500 | hr/yr | 1.641 | tpy
19 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 70.5789 | hp | 500 | hr/yr | 0.54699 | tpy
20 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 35.2895 | hp | 500 | hr/yr | 0.27349 | tpy
21 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 95 | hp | 500 | hr/yr | 0.73625 | tpy
22 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 35.2895 | hp | 500 | hr/yr | 0.27349 | tpy
23 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 155.2737 | hp | 500 | hr/yr | 1.2034 | tpy
24 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 50 | hp | 500 | hr/yr | 0.3875 | tpy
25 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 18.3505 | hp | 500 | hr/yr | 0.14222 | tpy
26 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 68 | hp | 500 | hr/yr | 0.527 | tpy
27 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 274 | hp | 500 | hr/yr | 2.1235 | tpy
28 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 274 | hp | 500 | hr/yr | 2.1235 | tpy
29a | Lift Pump Engine | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 74 | hp | 500 | hr/yr | 0.5735 | tpy
30 | Lift Pump Engine | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 75 | hp | 500 | hr/yr | 0.58125 | tpy
31a | Lift Pump Engine | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 74 | hp | 500 | hr/yr | 0.5735 | tpy
32 | Lift Pump Engine | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 75 | hp | 200 | hr/yr | 0.2325 | tpy
33 | Lift Pump Engine | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 75 | hp | 500 | hr/yr | 0.58125 | tpy
34 | Well Pump Engine | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 220 | hp | 500 | hr/yr | 1.705 | tpy
35 | Well Pump Engine | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 55 | hp | 500 | hr/yr | 0.42625 | tpy
36 | Well Pump Engine | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 220 | hp | 500 | hr/yr | 1.705 | tpy
51a | Fly Ash Dust Collector (DC-1) | N/A | N/A | N/A |  | 3620 | acfm | 4380 | hr/yr | 0 | tpy
51b | Bottom Ash Dust Collector (DC-2) | N/A | N/A | N/A |  | 3620 | acfm | 4380 | hr/yr | 0 | tpy
52 | Coal Storage Pile | N/A | N/A | N/A |  | N/A |  | 82049 | tpy | 0 | tpy
Significant Emission Units Total Assessable Potential to Emit - NOX | [9 empty] | 1532.3856 | tpy
Insignificant Emission Units
N/A | Fly and Bottom Ash Bin Vent Filter | N/A | N/A | N/A |  | 1460 | acfm | 4380 | hr/yr | 0 | tpy
N/A | Ash Loadout to Truck | N/A | N/A | N/A |  | N/A |  | 28560 | tpy | 0 | tpy
N/A | Aboveground Storage Tanks | Diesel | N/A | N/A |  | N/A |  | N/A |  | 0 | tpy
N/A | Underground Storage Tanks | Diesel | N/A | N/A |  | N/A |  | N/A |  | 0 | tpy
Insignificant Emission Units Total Assessable Potential to Emit - NOX | [9 empty] | 0 | tpy
Total Assessable Potential to Emit - NOX | [9 empty] | 1532.3856 | tpy
Conversion factors:
| Weight | 453.6 | g/lb
| Weight | 2000 | lb/ton
Source: Doyon Title V Renewal Permit Application, D-1.5, May 2013

## 2b DU NOx Proposed
TableXXX. Revised Oxides of Nitrogen (NOX) Emissions - Proposed
Doyon Utilities - Fort Wainwright (Privatized Emission Units)
Emission Unit |  |  |  | Fuel | Factor | NOX Emission |  | Emission Unit |  | Allowable Annual |  | Potential
ID | Description | Type of Service | Installation Date | Type | Reference | Factor |  | Max Rating/Capacity |  | Operation |  | NOX Emissions
Significant Emission Units
1 | Coal-Fired Boiler 3 |  | 1953 | Coal | AP-42 Table 1.1.3 with 25% control assumed by OFA and OT per table 1.1.2 (9/98). | 6.6 | lb/ton | 230 | MMBtu/hr | 300000 | ton/year | 990 | tpy
2 | Coal-Fired Boiler 4 |  | 1953 | Coal |  | 6.6 | lb/ton | 230 | MMBtu/hr
3 | Coal-Fired Boiler 5 |  | 1953 | Coal |  | 6.6 | lb/ton | 230 | MMBtu/hr
4 | Coal-Fired Boiler 6 |  | 1953 | Coal |  | 6.6 | lb/ton | 230 | MMBtu/hr
5 | Coal-Fired Boiler 7 |  | 1953 | Coal |  | 6.6 | lb/ton | 230 | MMBtu/hr
6 | Coal-Fired Boiler 8 |  | 1953 | Coal |  | 6.6 | lb/ton | 230 | MMBtu/hr
7a | South Coal Handling Dust Collector (DC-01) |  | 2001 | N/A | N/A | N | /A | 13150 | acfm | 2195 | hr/yr | 0 | tpy
7b | South Underbunker Dust Collector (DC-02) |  | 2005 | N/A | N/A | N | /A | 884 | acfm | 100 | hr/yr | 0 | tpy
7c | North Coal Handling Dust Collector (NDC-1) |  | 2004 | N/A | N/A | N | /A | 9250 | acfm | 45 | hr/yr | 0 | tpy
8 | Caterpillar 3516C | Backup Generator Engine | 2009 | Distillate | Vendor | 5.39 | g/kw-hr | 2937 | hp | 500 | hr/yr | 8.7249 | tpy
9 | Detroit 6V92 | Generator Engine | 1988 | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 353 | hp | 500 | hr/yr | 0.0060312 | tpy
10 | Caterpillar C15 | Generator Engine | 2010 | Distillate | Certified Engine | 6.4 | g/kw-hr | 762 | hp | 500 | hr/yr | 2.0001 | tpy
11 | Caterpillar C15 | Generator Engine | 2010 | Distillate | Certified Engine | 6.4 | g/kw-hr | 762 | hp | 500 | hr/yr | 2.0001 | tpy
12 | Cummins B3.3; SN 68011380 | Generator Engine | 2002 | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 82 | hp | 500 | hr/yr | 0.6355 | tpy
13 | Caterpillar 3406C TA; SN 4ZR04910 | Generator Engine | 2008 | Distillate | Certified Engine | 4 | g/kw-hr | 587 | hp | 500 | hr/yr | 0.963 | tpy
14 | Cummins QSL-G2 NR3 | Generator Engine | 2008 | Distillate | Certified Engine | 4 | g/kw-hr | 320 | hp | 500 | hr/yr | 0.52497 | tpy
15 | Detroit R1237M36; SN 5352004032 | Generator Engine | 2005 | Distillate | Mfg Information | 5.75 | g/hp-hr | 1058.6842 | hp | 500 | hr/yr | 3.3481 | tpy
16 | John Deere 6068TF250; SN PE6068T440136 | Generator Engine | 2005 | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 211.7368 | hp | 500 | hr/yr | 1.641 | tpy
17 | John Deere 6068TF250 | Generator Engine | 2007 | Distillate | Permit condition 23.1c | 6.9 | g/hp-hr | 176.4474 | hp | 500 | hr/yr | 0.66962 | tpy
18 | John Deere 6068HF150; SN PE6068H46179 | Generator Engine | 2005 | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 211.7368 | hp | 500 | hr/yr | 1.641 | tpy
19 | John Deere 4045TF270 | Generator Engine | 2007 | Distillate | Certified Engine | 7.5 | g/kw-hr | 70.5789 | hp | 500 | hr/yr | 0.2171 | tpy
20 | John Deere 4239D; SN T04239D226632 | Generator Engine | 1976 | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 35.2895 | hp | 500 | hr/yr | 0.27349 | tpy
21 | Perkins 2046/1800; SN AK50724 | Generator Engine | 2001 | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 95 | hp | 500 | hr/yr | 0.73625 | tpy
22 | Cummins | Generator Engine | 1989 | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 35.2895 | hp | 500 | hr/yr | 0.27349 | tpy
23 | John Deere 6068HF150; SN PE6068H221858 | Generator Engine | 2003 | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 155.2737 | hp | 500 | hr/yr | 1.2034 | tpy
24 | Cummins L634D-I/10386E; SN 53112605 | Generator Engine | 1993 | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 50 | hp | 500 | hr/yr | 0.3875 | tpy
25 | Caterpillar C1.5 | Generator Engine | 2011 | Distillate | Certified Engine | 7.5 | g/kw-hr | 18.3505 | hp | 500 | hr/yr | 0.056446 | tpy
26 | Cummins 4B3.9-G2: SN 46319490 | Generator Engine | 2003 | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 68 | hp | 500 | hr/yr | 0.527 | tpy
27 | Caterpillar C6.6 | Generator Engine | 2010 | Distillate | Certified Engine | 4 | g/kw-hr | 274 | hp | 500 | hr/yr | 0.44951 | tpy
28 | Caterpillar C6.6 | Generator Engine | 2010 | Distillate | Certified Engine | 4 | g/kw-hr | 274 | hp | 500 | hr/yr | 0.44951 | tpy
29a | John Deere 4045TF290 | Lift Pump Engine | 2014 | Distillate | Certified Engine | 4.7 | g/kW-hr | 74 | hp | 500 | hr/yr | 0.14264 | tpy
30 | Detroit Diesel 10245100 | Lift Pump Engine | 1952 | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 75 | hp | 500 | hr/yr | 0.58125 | tpy
31a | John Deere 4045TF290 | Lift Pump Engine | 2014 | Distillate | Certified Engine | 4.7 | g/kW-hr | 74 | hp | 500 | hr/yr | 0.14264 | tpy
32 | Perkins | Lift Pump Engine | 1955 | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 75 | hp | 500 | hr/yr | 0.58125 | tpy
33 | Perkins | Lift Pump Engine | 1994 | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 75 | hp | 500 | hr/yr | 0.58125 | tpy
34 | Detroit Diesel 10447000 | Well Pump Engine | 1995 | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 220 | hp | 500 | hr/yr | 1.705 | tpy
35 | John Deere 4045DF120 | Well Pump Engine | 2009 | Distillate | Certified Engine | 7.8 | g/hp-hr | 55 | hp | 500 | hr/yr | 0.23595 | tpy
36 | Detroit Diesel 4031-C | Well Pump Engine | 1995 | Distillate | AP-42, Table 3.3-1 | 0.031 | lb/hp-hr | 220 | hp | 500 | hr/yr | 1.705 | tpy
51a | Fly Ash Dust Collector (DC-1) |  | 1993 | N/A | N/A | N/A |  | 3620 | acfm | 4380 | hr/yr | 0 | tpy
51b | Bottom Ash Dust Collector (DC-2) |  | 1994 | N/A | N/A | N/A |  | 3620 | acfm | 4380 | hr/yr | 0 | tpy
52 | Coal Storage Pile |  | UNK | N/A | N/A | N/A |  | N/A |  | 82049 | tpy | 0 | tpy
Significant Emission Units Potential to Emit - NOX | [11 empty] | 1022.403 | tpy
Insignificant Emission Units
52 | Fly and Bottom Ash Bin Vent Filter |  |  | N/A | N/A | N/A |  | 1460 | acfm | 4380 | hr/yr | 0 | tpy
52 | Ash Loadout to Truck |  |  | N/A | N/A | N/A |  | N/A |  | 28560 | tpy | 0 | tpy
52 | Aboveground Storage Tanks |  |  | Diesel | N/A | N/A |  | N/A |  | N/A |  | 0 | tpy
52 | Underground Storage Tanks |  |  | Diesel | N/A | N/A |  | N/A |  | N/A |  | 0 | tpy
Insignificant Emission Units Potential to Emit - NOX | [11 empty] | 0 | tpy
Total Potential to Emit - NOX | [11 empty] | 1022.403 | tpy
Conversion factors: | 1 hp | Conversion factors: |  | 0.7457 | kW
| Weight |  |  | 453.6 | g/lb
| Weight |  |  | 2000 | lb/ton
| Coal Heating Value |  |  | 15.12 | MMBtu/ton | From www.usibelli.com/Coal_data.php
Source: Doyon Title V Renewal Permit Application, D-1.5

## 15 Proposed BACT Engines NOX
Location | EU | Make | Description | Year | Status |  |  | Size (hp) | Annual Operating Limits (non-Emergency) | Proposed BACT
FWA | 11 | Caterpillar | 3512 | 2003 |  |  |  | 1454 | 200 | Current Owner Requested Limit of 600 hours/12-month period cumulative for these three engines.
FWA | 12 | Caterpillar | 3512 | 2003 |  |  |  | 1454 | 200
FWA | 13 | Caterpillar | 3512 | 2003 |  |  |  | 1454 | 200
FWA | 26 | Cummins | QSB7-G3 NR3 | 2012 | Certified Engine |  |  | 295 | 500 | Comply with 40 CFR 60 Subpart IIII
FWA | 27 | John Deere | 4024HF285B | 2009 | Certified Engine |  |  | 67 | 500 | Comply with 40 CFR 60 Subpart IIII
FWA | 28 | Caterpillar | CAT C9 GENSET | 2007 | Certified Engine |  |  | 398 | 500 | Comply with 40 CFR 60 Subpart IIII
FWA | 29 | SDMO | TM30UCM | ND |  |  |  | 47 | 500 | Good Combustion Practices
FWA | 30 | John Deere | JW64-UF30 | 2007 | Certified Engine |  |  | 275 | 500 | Comply with 40 CFR 60 Subpart IIII
FWA | 31 | Clarke | DDFP-04AT | 1994 |  |  |  | 235 | 500 | Good Combustion Practices
FWA | 32 | Clarke | DDFP-04AT | 1994 |  |  |  | 235 | 500 | Good Combustion Practices
FWA | 33 | Clarke | DDFP-04AT | 1994 |  |  |  | 235 | 500 | Good Combustion Practices
FWA | 34 | Clarke | DDFP-04AT | 1994 |  |  |  | 235 | 500 | Good Combustion Practices
FWA | 35 | Cummins | N-855-F | 1977 |  |  |  | 240 | 500 | Good Combustion Practices
FWA | 36 | Cummins | N-855-F | 1977 |  |  |  | 240 | 500 | Good Combustion Practices
FWA | 37 | Clarke | JU4H-UF40 | 2005 |  |  |  | 94 | 500 | Good Combustion Practices
FWA | 38 | Clarke | PDFP-06YT | 1996 |  |  |  | 120 | 500 | Good Combustion Practices
FWA | 39 | Clarke | PDFP-06YT | 1996 |  |  |  | 120 | 500 | Good Combustion Practices
DU | 8 | Caterpillar 3516C | Backup Generator Engine | 2009 | Certified Engine | 6.4 | g/kw-hr | 2937 | 500 | Comply with 40 CFR 60 Subpart IIII
DU | 9 | Detroit 6V92 | Generator Engine | 1988 |  | 0.031 | lb/hp-hr | 352.8947 | 500 | Good Housekeeping Practices
DU | 10 | Caterpillar C15 | Generator Engine | 2010 | Certified Engine | 6.4 | g/kw-hr | 762 | 500 | Comply with 40 CFR 60 Subpart IIII
DU | 11 | Caterpillar C15 | Generator Engine | 2010 | Certified Engine | 6.4 | g/kw-hr | 762 | 500 | Comply with 40 CFR 60 Subpart IIII
DU | 12 | Cummins B3.3 | Generator Engine | 2002 |  | 0.031 | lb/hp-hr | 82 | 500 | Good Combustion Practices
DU | 13 | Caterpillar 3406C TA | Generator Engine | 2008 | Certified Engine | 4 | g/kw-hr | 587 | 500 | Comply with 40 CFR 60 Subpart IIII
DU | 14 | Cummins QSL-G2 NR3 | Generator Engine | 2008 | Certified Engine | 4 | g/kw-hr | 320 | 500 | Comply with 40 CFR 60 Subpart IIII
DU | 15 | Detroit R1237M36 | Generator Engine | 2005 | Mfg Information | 5.75 | g/hp-hr | 1058.6842 | 500 | Good Housekeeping Practices
DU | 16 | John Deere 6068TF250 | Generator Engine | 2005 |  | 0.031 | lb/hp-hr | 211.7368 | 500 | Good Combustion Practices
DU | 17 | John Deere 6068TF250 | Generator Engine | 2007 | Permit condition 23.1c | 6.9 | g/hp-hr | 176.4474 | 500 | Good Combustion Practices
DU | 18 | John Deere 6068HF150 | Generator Engine | 2005 |  | 0.031 | lb/hp-hr | 211.7368 | 500 | Good Combustion Practices
DU | 19 | John Deere 4045TF270 | Generator Engine | 2007 | Certified Engine | 7.5 | g/kw-hr | 70.5789 | 500 | Comply with 40 CFR 60 Subpart IIII
DU | 20 | John Deere 4239D | Generator Engine | 1976 |  | 0.031 | lb/hp-hr | 35.2895 | 500 | Good Combustion Practices
DU | 21 | Perkins 2046/1800 | Generator Engine | 2001 |  | 0.031 | lb/hp-hr | 95 | 500 | Good Combustion Practices
DU | 22 | Cummins | Generator Engine | 1989 |  | 0.031 | lb/hp-hr | 35.2895 | 500 | Good Combustion Practices
DU | 23 | John Deere 6068HF150 | Generator Engine | 2003 |  | 0.031 | lb/hp-hr | 155.2737 | 500 | Good Combustion Practices
DU | 24 | Cummins L634D-I/10386E | Generator Engine | 1993 |  | 0.031 | lb/hp-hr | 50 | 500 | Good Combustion Practices
DU | 25 | Caterpillar C1.5 | Generator Engine | 2011 | Certified Engine | 7.5 | g/kw-hr | 18.3505 | 500 | Comply with 40 CFR 60 Subpart IIII
DU | 26 | Cummins 4B3.9-G2 | Generator Engine | 2003 |  | 0.031 | lb/hp-hr | 68 | 500 | Good Combustion Practices
DU | 27 | Caterpillar C6.6 | Generator Engine | 2010 | Certified Engine | 4 | g/kw-hr | 274 | 500 | Comply with 40 CFR 60 Subpart IIII
DU | 28 | Caterpillar C6.6 | Generator Engine | 2010 | Certified Engine | 4 | g/kw-hr | 274 | 500 | Comply with 40 CFR 60 Subpart IIII
DU | 30 | Detroit Diesel 10245100 | Lift Pump Engine | 1952 |  | 0.031 | lb/hp-hr | 75 | 500 | Good Combustion Practices
DU | 32 | Perkins | Lift Pump Engine | 1955 |  | 0.031 | lb/hp-hr | 75 | 500 | Good Combustion Practices
DU | 33 | Perkins | Lift Pump Engine | 1994 |  | 0.031 | lb/hp-hr | 75 | 500 | Good Combustion Practices
DU | 34 | Detroit Diesel 10447000 | Well Pump Engine | 1995 |  | 0.031 | lb/hp-hr | 220 | 500 | Good Combustion Practices
DU | 35 | John Deere 4045DF120 | Well Pump Engine | 2009 | Certified Engine | 7.8 | g/hp-hr | 55 | 500 | Comply with 40 CFR 60 Subpart IIII
DU | 36 | Detroit Diesel 4031-C | Well Pump Engine | 1995 |  | 0.031 | lb/hp-hr | 220 | 500 | Good Combustion Practices
DU | 29a | John Deere 4045TF290 | Lift Pump Engine | 2014 | Certified Engine | 4.7 | g/kW-hr | 74 | 500 | Comply with 40 CFR 60 Subpart IIII
DU | 31a | John Deere 4045TF290 | Lift Pump Engine | 2014 | Certified Engine | 4.7 | g/kW-hr | 74 | 500 | Comply with 40 CFR 60 Subpart IIII
Note on I5: Deanne Hughes: Revised from 134 hp based on nameplate provided by Eric 4/18/17.
Note on I7: Changed from 334 to match Mfg. Information

## D-2.7 PM10 (hidden)
Table D-2.7. Unlimited Potential to Emit Calculations - Particulate Matter Less Than 10 Microns (PM10) Emissions
Doyon Utilities - Fort Wainwright (Privatized Emission Units)
Emission Unit |  | Fuel | Factor | PM10 Emission |  | Emission Unit |  | Allowable Annual |  | Potential
ID | Name | Type | Reference | Factor |  | Rating/Capacity |  | Operation |  | PM10 Emissions
Significant Emission Units
1 | Coal-Fired Boiler 3 | Coal | AP-42, Tables 1.1-5 and 1.1-9 | 13.8048 | lb/ton | 230 | MMBtu/hr | 8760 | hr/yr | 919.7722 | tpy
2 | Coal-Fired Boiler 4 | Coal | AP-42, Tables 1.1-5 and 1.1-9 | 13.8048 | lb/ton | 230 | MMBtu/hr | 8760 | hr/yr | 919.7722 | tpy
3 | Coal-Fired Boiler 5 | Coal | AP-42, Tables 1.1-5 and 1.1-9 | 13.8048 | lb/ton | 230 | MMBtu/hr | 8760 | hr/yr | 919.7722 | tpy
4 | Coal-Fired Boiler 6 | Coal | AP-42, Tables 1.1-5 and 1.1-9 | 13.8048 | lb/ton | 230 | MMBtu/hr | 8760 | hr/yr | 919.7722 | tpy
5 | Coal-Fired Boiler 7 | Coal | AP-42, Tables 1.1-5 and 1.1-9 | 13.8048 | lb/ton | 230 | MMBtu/hr | 8760 | hr/yr | 919.7722 | tpy
6 | Coal-Fired Boiler 8 | Coal | AP-42, Tables 1.1-5 and 1.1-9 | 13.8048 | lb/ton | 230 | MMBtu/hr | 8760 | hr/yr | 919.7722 | tpy
7a | South Coal Handling Dust Collector (DC-01) | N/A | See detailed calculations in Table D-2.7a |  |  | 13150 | acfm | 8760 | hr/yr | 0.29961 | tpy
7b | South Underbunker Dust Collector (DC-02) | N/A | See detailed calculations in Table D-2.7a |  |  | 884 | acfm | 8760 | hr/yr | 0.0073406 | tpy
7c | North Coal Handling Dust Collector (NDC-1) | N/A | See detailed calculations in Table D-2.7a |  |  | 9250 | acfm | 8760 | hr/yr | 0.034565 | tpy
8 | Black Start Generator Engine | Distillate | Vendor | 0.026 | g/hp-hr | 2937 | hp | 8760 | hr/yr | 0.73736 | tpy
9 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 352.8947 | hp | 8760 | hr/yr | 3.4005 | tpy
10 | Generator Engine | Distillate | AP-42, Table 3.4-1 | 0.0007 | lb/hp-hr | 762 | hp | 8760 | hr/yr | 2.3363 | tpy
11 | Generator Engine | Distillate | AP-42, Table 3.4-1 | 0.0007 | lb/hp-hr | 762 | hp | 8760 | hr/yr | 2.3363 | tpy
12 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 82 | hp | 8760 | hr/yr | 0.79015 | tpy
13 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 587 | hp | 8760 | hr/yr | 5.6563 | tpy
14 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 320 | hp | 8760 | hr/yr | 3.0835 | tpy
15 | Generator Engine | Distillate | AP-42, Table 3.4-1 | 0.0007 | lb/hp-hr | 1058.6842 | hp | 8760 | hr/yr | 3.2459 | tpy
16 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 211.7368 | hp | 8760 | hr/yr | 2.0403 | tpy
17 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 176.4474 | hp | 8760 | hr/yr | 1.7002 | tpy
18 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 211.7368 | hp | 8760 | hr/yr | 2.0403 | tpy
19 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 70.5789 | hp | 8760 | hr/yr | 0.6801 | tpy
20 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 35.2895 | hp | 8760 | hr/yr | 0.34005 | tpy
21 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 95 | hp | 8760 | hr/yr | 0.91542 | tpy
22 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 35.2895 | hp | 8760 | hr/yr | 0.34005 | tpy
23 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 155.2737 | hp | 8760 | hr/yr | 1.4962 | tpy
24 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 50 | hp | 8760 | hr/yr | 0.4818 | tpy
25 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 18.3505 | hp | 8760 | hr/yr | 0.17683 | tpy
26 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 68 | hp | 8760 | hr/yr | 0.65525 | tpy
27 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 274 | hp | 8760 | hr/yr | 2.6403 | tpy
28 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 274 | hp | 8760 | hr/yr | 2.6403 | tpy
29 | Lift Pump Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 75 | hp | 8760 | hr/yr | 0.7227 | tpy
30 | Lift Pump Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 75 | hp | 8760 | hr/yr | 0.7227 | tpy
31 | Lift Pump Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 75 | hp | 8760 | hr/yr | 0.7227 | tpy
32 | Lift Pump Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 75 | hp | 8760 | hr/yr | 0.7227 | tpy
33 | Lift Pump Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 75 | hp | 8760 | hr/yr | 0.7227 | tpy
34 | Well Pump Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 220 | hp | 8760 | hr/yr | 2.1199 | tpy
35 | Well Pump Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 85 | hp | 8760 | hr/yr | 0.81906 | tpy
36 | Well Pump Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 220 | hp | 8760 | hr/yr | 2.1199 | tpy
51a | Fly Ash Dust Collector (DC-1) | N/A | See detailed calculations in Table D-2.7b |  |  | 3620 | acfm | 8760 | hr/yr | 1.1763 | tpy
51b | Bottom Ash Dust Collector (DC-2) | N/A | See detailed calculations in Table D-2.7b |  |  | 3620 | acfm | 8760 | hr/yr | 1.1763 | tpy
52 | Coal Storage Pile | N/A | See detailed calculations in Table D-2.7c |  |  | N/A |  | 180643.5 | tpy | 3.2246 | tpy
Significant Emission Units Total Unlimited Potential to Emit - PM10 | [9 empty] | 5570.9576 | tpy
Insignificant Emission Units
N/A | Fly and Bottom Ash Bin Vent Filter | N/A | See detailed calculations in Table D-2.7b |  |  | 1460 | acfm | 8760 | hr/yr | 0.4744 | tpy
N/A | Ash Loadout to Truck | N/A | See detailed calculations in Table D-2.7b |  |  | N/A |  | 67959.5238 | tpy | 0.004284 | tpy
N/A | Aboveground Storage Tanks | Diesel | N/A | N/A |  | N/A |  | N/A |  | 0 | tpy
N/A | Underground Storage Tanks | Diesel | N/A | N/A |  | N/A |  | N/A |  | 0 | tpy
Insignificant Emission Units Total Unlimited Potential to Emit - PM10 | [9 empty] | 0.47869 | tpy
Total Unlimited Potential to Emit - PM10 | [9 empty] | 5571.4363 | tpy
Conversion factors:
| Weight | 453.6 | g/lb
| Weight | 2000 | lb/ton
| Coal Heating Value | 15.12 | MMBtu/ton | From www.usibelli.com/Coal_data.php

## 4a PM25 Base Case
Table XXX. Particulate Matter Less Than 2.5 Microns (PM2.5) Emissions - Base Case for BACT analysis
Doyon Utilities - Fort Wainwright (Privatized Emission Units)
Emission Unit |  | Fuel | Factor | PM2.5 Emission |  | Emission Unit |  | Allowable Annual |  | Potential
ID | Name | Type | Reference | Factor a |  | Rating/Capacity |  | Operation |  | PM2.5 Emissions
Significant Emission Units
1 | Coal-Fired Boiler 3 | Coal | AP-42, Tables 1.1-5 and 1.1-6 | 0.782 | lb/ton | 230 | mmbtu/hr | 336000 | ton/year | 131.376 | tpy
2 | Coal-Fired Boiler 4 | Coal
3 | Coal-Fired Boiler 5 | Coal
4 | Coal-Fired Boiler 6 | Coal
5 | Coal-Fired Boiler 7 | Coal
6 | Coal-Fired Boiler 8 | Coal
7a | South Coal Handling Dust Collector (DC-01) | N/A | See detailed calculations in Table D-1.7a in the Title V Renewal Permit Application |  |  | 13150 | acfm | 2195.2 | hr/yr | 0.29963 | tpy
7b | South Underbunker Dust Collector (DC-02) | N/A |  |  |  | 884 | acfm | 100 | hr/yr | 0.0073406 | tpy
7c | North Coal Handling Dust Collector (NDC-1) | N/A |  |  |  | 9250 | acfm | 44.8 | hr/yr | 0.034411 | tpy
8 | Backup Generator Engine | Distillate | Vendor | 0.026 | g/hp-hr | 2937 | hp | 500 | hr/yr | 0.042087 | tpy
9 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 352.8947 | hp | 500 | hr/yr | 0.19409 | tpy
10 | Generator Engine | Distillate | AP-42, Table 3.4-1 | 0.0007 | lb/hp-hr | 762 | hp | 500 | hr/yr | 0.13335 | tpy
11 | Generator Engine | Distillate | AP-42, Table 3.4-1 | 0.0007 | lb/hp-hr | 762 | hp | 500 | hr/yr | 0.13335 | tpy
12 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 82 | hp | 500 | hr/yr | 0.0451 | tpy
13 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 587 | hp | 500 | hr/yr | 0.32285 | tpy
14 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 320 | hp | 500 | hr/yr | 0.176 | tpy
15 | Generator Engine | Distillate | AP-42, Table 3.4-1 | 0.0007 | lb/hp-hr | 1058.6842 | hp | 500 | hr/yr | 0.18527 | tpy
16 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 211.7368 | hp | 500 | hr/yr | 0.11646 | tpy
17 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 176.4474 | hp | 500 | hr/yr | 0.097046 | tpy
18 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 211.7368 | hp | 500 | hr/yr | 0.11646 | tpy
19 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 70.5789 | hp | 500 | hr/yr | 0.038818 | tpy
20 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 35.2895 | hp | 500 | hr/yr | 0.019409 | tpy
21 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 95 | hp | 500 | hr/yr | 0.05225 | tpy
22 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 35.2895 | hp | 500 | hr/yr | 0.019409 | tpy
23 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 155.2737 | hp | 500 | hr/yr | 0.085401 | tpy
24 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 50 | hp | 500 | hr/yr | 0.0275 | tpy
25 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 18.3505 | hp | 500 | hr/yr | 0.010093 | tpy
26 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 68 | hp | 500 | hr/yr | 0.0374 | tpy
27 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 274 | hp | 500 | hr/yr | 0.1507 | tpy
28 | Generator Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 274 | hp | 500 | hr/yr | 0.1507 | tpy
29a | Lift Pump Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 74 | hp | 500 | hr/yr | 0.0407 | tpy
30 | Lift Pump Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 75 | hp | 500 | hr/yr | 0.04125 | tpy
31a | Lift Pump Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 74 | hp | 500 | hr/yr | 0.0407 | tpy
32 | Lift Pump Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 75 | hp | 500 | hr/yr | 0.04125 | tpy
33 | Lift Pump Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 75 | hp | 500 | hr/yr | 0.04125 | tpy
34 | Well Pump Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 220 | hp | 500 | hr/yr | 0.121 | tpy
35 | Well Pump Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 55 | hp | 500 | hr/yr | 0.03025 | tpy
36 | Well Pump Engine | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 220 | hp | 500 | hr/yr | 0.121 | tpy
51a | Fly Ash Dust Collector (DC-1) | N/A | See detailed calculations in Table D-1.7b of Title V Renewal Permit Application |  |  | 3620 | acfm | 4380 | hr/yr | 1.1763 | tpy
51b | Bottom Ash Dust Collector (DC-2) | N/A |  |  |  | 3620 | acfm | 4380 | hr/yr | 1.1763 | tpy
52 | Coal Storage Pile | N/A | See detailed calculations in Table D-1.7c of Title V Renewal Permit Application |  |  | N/A |  | 82049 | tpy | 3.22 | tpy
Significant Emission Units Total Assessable Potential to Emit - PM2.5 | [9 empty] | 139.921 | tpy
Insignificant Emission Units
N/A | Fly and Bottom Ash Bin Vent Filter | N/A | See detailed calculations in Table D-1.7b of Title V Renewal Permit Application |  |  | 1460 | acfm | 4380 | hr/yr | 0.4744 | tpy
N/A | Ash Loadout to Truck | N/A |  |  |  | N/A |  | 28560 | tpy | 0.00046231 | tpy
N/A | Aboveground Storage Tanks | Diesel | N/A | N/A |  | N/A |  | N/A |  | 0 | tpy
N/A | Underground Storage Tanks | Diesel | N/A | N/A |  | N/A |  | N/A |  | 0 | tpy
Insignificant Emission Units Total Assessable Potential to Emit - PM2.5 | [9 empty] | 0.47487 | tpy
Total Assessable Potential to Emit - PM2.5 | [9 empty] | 140.3959 | tpy2
Notes:
a PM2.5 potential to emit calculations for all emission units (other than 1 through 6, 7a through 7c, 51a and 51b) conservatively assume that PM2.5 emissions are equal to PM10 emissions.
Conversion factors:
| Weight | 453.6 | g/lb
| Weight | 2000 | lb/ton
Original Source: Table D-1.8 from Title V Renewal Permit Application, May 2013; this table reflects greater emissions of PM2.5 than was included in the Title V Renewal Permit Application as a result of using 500 hours/year for emergency engines rather than 100 hours/year.
Note on I16: Deanne D. Hughes: I have changed all the engines to 500 hours/year per Courtney's request -- but calculations in table D-1 for assessable emissions, 100 hr/year is used instead.

## 4b DU PM25 Proposed
Table xxx Revised Particulate Matter Less Than 2.5 Microns (PM2.5) Emissions - Proposed
Doyon Utilities - Fort Wainwright (Privatized Emission Units)
Emission Unit |  |  | Installation Date | Fuel | Factor | PM2.5 Emission |  | Emission Unit |  | Allowable Annual |  | Potential
ID | Name |  |  | Type | Reference | Factor |  | Rating/Capacity |  | Operation |  | PM2.5 Emissions
Significant Emission Units
1 | Coal-Fired Boiler 3 |  | 1953 | Coal | MACT 2016 testing and MACTEC guidance on CPM emissions (to Mid Atlantic Regional Air Management Association) August 2008; See Excel Sheet "CPM and PM25 for CHPP Boilers" | 0.46 | lb/ton | 230 | mmbtu/hr | 300000 | ton/year | 69 | tpy
2 | Coal-Fired Boiler 4 |  | 1953 | Coal |  | 0.46 | lb/ton | 230 | mmbtu/hr
3 | Coal-Fired Boiler 5 |  | 1953 | Coal |  | 0.46 | lb/ton | 230 | mmbtu/hr
4 | Coal-Fired Boiler 6 |  | 1953 | Coal |  | 0.46 | lb/ton | 230 | mmbtu/hr
5 | Coal-Fired Boiler 7 |  | 1953 | Coal |  | 0.46 | lb/ton | 230 | mmbtu/hr
6 | Coal-Fired Boiler 8 |  | 1953 | Coal |  | 0.46 | lb/ton | 230 | mmbtu/hr
7a | South Coal Handling Dust Collector (DC-01) |  | 2001 | N/A | See detailed calculations in Table Coal Prep 7a 7b 7c |  |  | 13150 | acfm | 2195 | hr/yr | 0.044941 | tpy
7b | South Underbunker Dust Collector (DC-02) |  | 2005 | N/A |  |  |  | 884 | acfm | 100 | hr/yr | 0.0011011 | tpy
7c | North Coal Handling Dust Collector (NDC-1) |  | 2004 | N/A |  |  |  | 9250 | acfm | 45 | hr/yr | 0.0051847 | tpy
8 | Caterpillar 3516C | Backup Generator Engine | 2009 | Distillate | Certified Engine | 0.2 | g/kW-hr | 2937 | hp | 500 | hr/yr | 0.24091 | tpy
9 | Detroit 6V92 | Generator Engine | 1988 | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 352.8947 | hp | 500 | hr/yr | 0.19409 | tpy
10 | Caterpillar C15 | Generator Engine | 2010 | Distillate | Certified Engine | 0.2 | g/kW-hr | 762 | hp | 500 | hr/yr | 0.062505 | tpy
11 | Caterpillar C15 | Generator Engine | 2010 | Distillate | Certified Engine | 0.2 | g/kW-hr | 762 | hp | 500 | hr/yr | 0.062505 | tpy
12 | Cummins B3.3 | Generator Engine | 2002 | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 82 | hp | 500 | hr/yr | 0.0451 | tpy
13 | Caterpillar 3406C TA | Generator Engine | 2008 | Distillate | Certified Engine | 0.2 | g/kW-hr | 587 | hp | 500 | hr/yr | 0.04815 | tpy
14 | Cummins QSL-G2 NR3 | Generator Engine | 2008 | Distillate | Certified Engine | 0.2 | g/kW-hr | 320 | hp | 500 | hr/yr | 0.026249 | tpy
15 | Detroit R1237M36 | Generator Engine | 2005 | Distillate | Mfg Information | 0.09 | g/hp-hr | 1058.6842 | hp | 500 | hr/yr | 0.052405 | tpy
16 | John Deere 6068TF250 | Generator Engine | 2005 | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 211.7368 | hp | 500 | hr/yr | 0.11646 | tpy
17 | John Deere 6068TF250 | Generator Engine | 2007 | Distillate | Certified Engine | 0.3 | g/kW-hr | 176.4474 | hp | 500 | hr/yr | 0.02171 | tpy
18 | John Deere 6068HF150 | Generator Engine | 2005 | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 211.7368 | hp | 500 | hr/yr | 0.11646 | tpy
19 | John Deere 4045TF270 | Generator Engine | 2007 | Distillate | Certified Engine | 0.4 | g/kW-hr | 70.5789 | hp | 500 | hr/yr | 0.011579 | tpy
20 | John Deere 4239D | Generator Engine | 1976 | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 35.2895 | hp | 500 | hr/yr | 0.019409 | tpy
21 | Perkins 2046/1800 | Generator Engine | 2001 | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 95 | hp | 500 | hr/yr | 0.05225 | tpy
22 | Cummins | Generator Engine | 1989 | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 35.2895 | hp | 500 | hr/yr | 0.019409 | tpy
23 | John Deere 6068HF150 | Generator Engine | 2003 | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 155.2737 | hp | 500 | hr/yr | 0.085401 | tpy
24 | Cummins L634D-I/10386E | Generator Engine | 1993 | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 50 | hp | 500 | hr/yr | 0.0275 | tpy
25 | Caterpillar C1.5 | Generator Engine | 2011 | Distillate | Certified Engine | 0.4 | g/kW-hr | 18.3505 | hp | 500 | hr/yr | 0.0030105 | tpy
26 | Cummins 4B3.9-G2 | Generator Engine | 2003 | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 68 | hp | 500 | hr/yr | 0.0374 | tpy
27 | Caterpillar C6.6 | Generator Engine | 2010 | Distillate | Certified Engine | 0.2 | g/kW-hr | 274 | hp | 500 | hr/yr | 0.022475 | tpy
28 | Caterpillar C6.6 | Generator Engine | 2010 | Distillate | Certified Engine | 0.2 | g/kW-hr | 274 | hp | 500 | hr/yr | 0.022475 | tpy
29a | John Deere 4045TF290 | Lift Pump Engine | 2014 | Distillate | Certified Engine | 0.03 | g/kW-hr | 74 | hp | 500 | hr/yr | 0.0009105 | tpy
30 | Detroit Diesel 10245100 | Lift Pump Engine | 1952 | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 75 | hp | 500 | hr/yr | 0.04125 | tpy
31a | John Deere 4045TF290 | Lift Pump Engine | 2014 | Distillate | Certified Engine | 0.03 | g/kW-hr | 74 | hp | 500 | hr/yr | 0.0009105 | tpy
32 | Perkins | Lift Pump Engine | 1955 | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 75 | hp | 500 | hr/yr | 0.04125 | tpy
33 | Perkins | Lift Pump Engine | 1994 | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 75 | hp | 500 | hr/yr | 0.04125 | tpy
34 | Detroit Diesel 10447000 | Well Pump Engine | 1995 | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 220 | hp | 500 | hr/yr | 0.121 | tpy
35 | John Deere 4045DF120 | Well Pump Engine | 2009 | Distillate | Certified Engine | 0.4 | g/kW-hr | 55 | hp | 500 | hr/yr | 0.009023 | tpy
36 | Detroit Diesel 4031-C | Well Pump Engine | 1995 | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 220 | hp | 500 | hr/yr | 0.121 | tpy
51a | Fly Ash Dust Collector (DC-1) |  | 1993 | N/A | See detailed calculations in Table DU Ash Handling |  |  | 3620 | acfm | 4380 | hr/yr | 0.17644 | tpy
51b | Bottom Ash Dust Collector (DC-2) |  | 1994 | N/A | See detailed calculations in Table DU Ash Handling |  |  | 3620 | acfm | 4380 | hr/yr | 0.17644 | tpy
52 | Coal Storage Pile |  | UNK | N/A | See detailed calculations in Table DU Coal Pile |  |  | N/A |  | 82049 | tpy | 3.22 | tpy
Significant Emission Units Total Potential to Emit - PM2.5 | [11 empty] | 74.2881 | tpy
Insignificant Emission Units
N/A | Fly and Bottom Ash Bin Vent Filter |  |  | N/A | See detailed calculations in Table DU Ash Handling |  |  | 1460 | acfm | 4380 | hr/yr | 0.071161 | tpy
N/A | Ash Loadout to Truck |  |  | N/A | See detailed calculations in Table DU Ash Handling |  |  | N/A |  | 28560 | tpy | 0.0006426 | tpy
N/A | Aboveground Storage Tanks |  |  | Diesel | N/A | N/A |  | N/A |  | N/A |  | 0 | tpy
N/A | Underground Storage Tanks |  |  | Diesel | N/A | N/A |  | N/A |  | N/A |  | 0 | tpy
Insignificant Emission Units Total Potential to Emit - PM2.5 | [11 empty] | 0.071803 | tpy
Total Unlimited Potential to Emit - PM2.5 | [11 empty] | 74.3599 | tpy2
Notes:
a PM2.5 potential to emit calculations for all emission units other than 1 through 6, 7a through 7c, 51a, 51b, and 52 conservatively assume that PM2.5 emissions are equal to PM10 emissions.
For certified engines, PM2.5 is conservatively estimated as the PM Emission Standard applicable to that engine.
Conversion factors:
| 1 hp | 0.7457 | kW
| Weight | 453.6 | g/lb
| Weight | 2000 | lb/ton
| Coal Heating Value | 15.12 | MMBtu/ton | From www.usibelli.com/Coal_data.php
Source: Underlying data from Title V Renewal Permit Application. Modifications to the calculations for the boilers is detailed in the BACT Submittal.
Note on B16: Deanne Hughes: Title V Renewal Application indicated this generator has a 5.39 vendor guarantee.

## 18 PM2.5 Controls for Engines
Table xxx BACT Cost Estimates for Particulate Matter Less Than 2.5 Microns (PM2.5) Emissions from Engines
Doyon Utilities - Fort Wainwright (Privatized Emission Units)
Emission Unit |  |  | Installation Date | Fuel | Factor | PM2.5 Emission |  | Emission Unit |  | Allowable Annual |  | Potential |  | DPF Cost (CARB basis) | PM Reduced (tpy) | Cost/Ton Reduced | DPF Cost (ODEQ basis) | PM Reduced (tpy) | Cost/Ton Reduced | DOC Cost (ODEQ basis) | PM Reduced (tpy) | Cost/Ton Reduced
ID | Name |  |  | Type | Reference | Factor |  | Rating/Capacity |  | Operation |  | PM2.5 Emissions
Significant Emission Units
1 | Coal-Fired Boiler 3 |  | 1953 | Coal | AP-42, 1.1-9 using baghouse, 500% safety factor applied for "E" rating | 0.16 | lb/ton | 230 | MMBtu/hr | 336000 | ton/year | 4.48 | tpy
2 | Coal-Fired Boiler 4 |  | 1953 | Coal |  |  |  | 230 | MMBtu/hr |  |  | 4.48 | tpy
3 | Coal-Fired Boiler 5 |  | 1953 | Coal |  |  |  | 230 | MMBtu/hr |  |  | 4.48 | tpy
4 | Coal-Fired Boiler 6 |  | 1953 | Coal |  |  |  | 230 | MMBtu/hr |  |  | 4.48 | tpy
5 | Coal-Fired Boiler 7 |  | 1953 | Coal |  |  |  | 230 | MMBtu/hr |  |  | 4.48 | tpy
6 | Coal-Fired Boiler 8 |  | 1953 | Coal |  |  |  | 230 | MMBtu/hr |  |  | 4.48 | tpy
7a | South Coal Handling Dust Collector (DC-01) |  | 2001 | N/A | See detailed calculations in Table D-2.7a |  |  | 13150 | acfm | 8584.8 | hr/yr | 0.044941 | tpy
7b | South Underbunker Dust Collector (DC-02) |  | 2005 | N/A | See detailed calculations in Table D-2.7a |  |  | 884 | acfm | 8760 | hr/yr | 0.0011011 | tpy
7c | North Coal Handling Dust Collector (NDC-1) |  | 2004 | N/A | See detailed calculations in Table D-2.7a |  |  | 9250 | acfm | 175.2 | hr/yr | 0.0051847 | tpy
8 | Caterpillar 3516C | Backup Generator Engine | 2009 | Distillate | Certified Engine | 0.2 | g/kW-hr | 2937 | hp | 500 | hr/yr | 0.24091 | tpy | 111606 | 0.20478 | 545014.2313 | 5750 | 0.21682 | 26519.4529 | 1500 | 0.072274 | 20754.3545
9 | Detroit 6V92 | Generator Engine | 1988 | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 352.8947 | hp | 500 | hr/yr | 0.19409 | tpy | 13410 | 0.16498 | 81283.4225 | 5750 | 0.17468 | 32916.7891 | 1500 | 0.058228 | 25760.9654
10 | Caterpillar C15 | Generator Engine | 2010 | Distillate | Certified Engine | 0.2 | g/kW-hr | 762 | hp | 500 | hr/yr | 0.062505 | tpy | 28956 | 0.053129 | 545014.2313 | 5750 | 0.056254 | 102214.7417 | 1500 | 0.018751 | 79994.1457
11 | Caterpillar C15 | Generator Engine | 2010 | Distillate | Certified Engine | 0.2 | g/kW-hr | 762 | hp | 500 | hr/yr | 0.062505 | tpy | 28956 | 0.053129 | 545014.2313 | 5750 | 0.056254 | 102214.7417 | 1500 | 0.018751 | 79994.1457
12 | Cummins B3.3 | Generator Engine | 2002 | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 82 | hp | 500 | hr/yr | 0.0451 | tpy | 3116 | 0.038335 | 81283.4225 | 5750 | 0.04059 | 141660.5075 | 1500 | 0.01353 | 110864.745
13 | Caterpillar 3406C TA | Generator Engine | 2008 | Distillate | Certified Engine | 0.2 | g/kW-hr | 587 | hp | 500 | hr/yr | 0.04815 | tpy | 22306 | 0.040927 | 545014.2313 | 5750 | 0.043335 | 132687.6205 | 1500 | 0.014445 | 103842.4856
14 | Cummins QSL-G2 NR3 | Generator Engine | 2008 | Distillate | Certified Engine | 0.2 | g/kW-hr | 320 | hp | 500 | hr/yr | 0.026249 | tpy | 12160 | 0.022311 | 545014.2313 | 5750 | 0.023624 | 243398.8538 | 1500 | 0.0078746 | 190486.0595
15 | Detroit R1237M36 | Generator Engine | 2005 | Distillate | Mfg Information | 0.09 | g/hp-hr | 1058.6842 | hp | 500 | hr/yr | 0.052405 | tpy | 40230 | 0.044544 | 903149.1384 | 5750 | 0.047164 | 121914.0336 | 1500 | 0.015721 | 95410.9828
16 | John Deere 6068TF250 | Generator Engine | 2005 | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 211.7368 | hp | 500 | hr/yr | 0.11646 | tpy | 8046 | 0.098987 | 81283.4225 | 5750 | 0.10481 | 54861.3151 | 1500 | 0.034937 | 42934.9423
17 | John Deere 6068TF250 | Generator Engine | 2007 | Distillate | Certified Engine | 0.3 | g/kW-hr | 176.4474 | hp | 500 | hr/yr | 0.02171 | tpy | 6705 | 0.018454 | 363342.8209 | 5750 | 0.019539 | 294280.8911 | 1500 | 0.0065131 | 230306.7843
18 | John Deere 6068HF150 | Generator Engine | 2005 | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 211.7368 | hp | 500 | hr/yr | 0.11646 | tpy | 8046 | 0.098987 | 81283.4225 | 5750 | 0.10481 | 54861.3151 | 1500 | 0.034937 | 42934.9423
19 | John Deere 4045TF270 | Generator Engine | 2007 | Distillate | Certified Engine | 0.4 | g/kW-hr | 70.5789 | hp | 500 | hr/yr | 0.011579 | tpy | 2682 | 0.0098419 | 272507.1157 | 5750 | 0.010421 | 551776.6707 | 1500 | 0.0034736 | 431825.2206
20 | John Deere 4239D | Generator Engine | 1976 | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 35.2895 | hp | 500 | hr/yr | 0.019409 | tpy | 1341 | 0.016498 | 81283.4225 | 5750 | 0.017468 | 329167.8907 | 1500 | 0.0058228 | 257609.6536
21 | Perkins 2046/1800 | Generator Engine | 2001 | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 95 | hp | 500 | hr/yr | 0.05225 | tpy | 3610 | 0.044413 | 81283.4225 | 5750 | 0.047025 | 122275.3854 | 1500 | 0.015675 | 95693.7799
22 | Cummins | Generator Engine | 1989 | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 35.2895 | hp | 500 | hr/yr | 0.019409 | tpy | 1341 | 0.016498 | 81283.4225 | 5750 | 0.017468 | 329167.8907 | 1500 | 0.0058228 | 257609.6536
23 | John Deere 6068HF150 | Generator Engine | 2003 | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 155.2737 | hp | 500 | hr/yr | 0.085401 | tpy | 5900.4 | 0.07259 | 81283.4225 | 5750 | 0.07686 | 74810.8842 | 1500 | 0.02562 | 58547.6485
24 | Cummins L634D-I/10386E | Generator Engine | 1993 | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 50 | hp | 500 | hr/yr | 0.0275 | tpy | 1900 | 0.023375 | 81283.4225 | 5750 | 0.02475 | 232323.2323 | 1500 | 0.00825 | 181818.1818
25 | Caterpillar C1.5 | Generator Engine | 2011 | Distillate | Certified Engine | 0.4 | g/kW-hr | 18.3505 | hp | 500 | hr/yr | 0.0030105 | tpy | 697.32 | 0.0025589 | 272507.1157 | 5750 | 0.0027094 | 2122217.9643 | 1500 | 0.00090314 | 1660866.233
26 | Cummins 4B3.9-G2 | Generator Engine | 2003 | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 68 | hp | 500 | hr/yr | 0.0374 | tpy | 2584 | 0.03179 | 81283.4225 | 5750 | 0.03366 | 170825.9061 | 1500 | 0.01122 | 133689.8396
27 | Caterpillar C6.6 | Generator Engine | 2010 | Distillate | Certified Engine | 0.2 | g/kW-hr | 274 | hp | 500 | hr/yr | 0.022475 | tpy | 10412 | 0.019104 | 545014.2313 | 5750 | 0.020228 | 284261.4351 | 1500 | 0.0067426 | 222465.4709
28 | Caterpillar C6.6 | Generator Engine | 2010 | Distillate | Certified Engine | 0.2 | g/kW-hr | 274 | hp | 500 | hr/yr | 0.022475 | tpy | 10412 | 0.019104 | 545014.2313 | 5750 | 0.020228 | 284261.4351 | 1500 | 0.0067426 | 222465.4709
29a | John Deere 4045TF290 | Lift Pump Engine | 2014 | Distillate | Certified Engine | 0.03 | g/kW-hr | 74 | hp | 500 | hr/yr | 0.0009105 | tpy | 2812 | 0.00077392 | 3633428.2088 | 5750 | 0.00081945 | 7016903.8923 | 1500 | 0.00027315 | 5491490.0027
30 | Detroit Diesel 10245100 | Lift Pump Engine | 1952 | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 75 | hp | 500 | hr/yr | 0.04125 | tpy | 2850 | 0.035063 | 81283.4225 | 5750 | 0.037125 | 154882.1549 | 1500 | 0.012375 | 121212.1212
31a | John Deere 4045TF290 | Lift Pump Engine | 2014 | Distillate | Certified Engine | 0.03 | g/kW-hr | 74 | hp | 500 | hr/yr | 0.0009105 | tpy | 2812 | 0.00077392 | 3633428.2088 | 5750 | 0.00081945 | 7016903.8923 | 1500 | 0.00027315 | 5491490.0027
32 | Perkins | Lift Pump Engine | 1955 | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 75 | hp | 500 | hr/yr | 0.04125 | tpy | 2850 | 0.035063 | 81283.4225 | 5750 | 0.037125 | 154882.1549 | 1500 | 0.012375 | 121212.1212
33 | Perkins | Lift Pump Engine | 1994 | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 75 | hp | 500 | hr/yr | 0.04125 | tpy | 2850 | 0.035063 | 81283.4225 | 5750 | 0.037125 | 154882.1549 | 1500 | 0.012375 | 121212.1212
34 | Detroit Diesel 10447000 | Well Pump Engine | 1995 | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 220 | hp | 500 | hr/yr | 0.121 | tpy | 8360 | 0.10285 | 81283.4225 | 5750 | 0.1089 | 52800.7346 | 1500 | 0.0363 | 41322.314
35 | John Deere 4045DF120 | Well Pump Engine | 2009 | Distillate | Certified Engine | 0.4 | g/kW-hr | 55 | hp | 500 | hr/yr | 0.009023 | tpy | 2090 | 0.0076695 | 272507.1157 | 5750 | 0.0081207 | 708069.3928 | 1500 | 0.0027069 | 554141.2639
36 | Detroit Diesel 4031-C | Well Pump Engine | 1995 | Distillate | AP-42, Table 3.3-1 | 0.0022 | lb/hp-hr | 220 | hp | 500 | hr/yr | 0.121 | tpy | 8360 | 0.10285 | 81283.4225 | 5750 | 0.1089 | 52800.7346 | 1500 | 0.0363 | 41322.314
51a | Fly Ash Dust Collector (DC-1) |  | 1993 | N/A | See detailed calculations in Table D-2.7b |  |  | 3620 | acfm | 500 | hr/yr | 0.17644 | tpy
51b | Bottom Ash Dust Collector (DC-2) |  | 1994 | N/A | See detailed calculations in Table D-2.7b |  |  | 3620 | acfm | 500 | hr/yr | 0.17644 | tpy
52 | Coal Storage Pile |  | UNK | N/A | See detailed calculations in Table D-2.7c |  |  | N/A |  | 180643.5 | tpye | 3.22 | tpy
Significant Emission Units Total Potential to Emit - PM2.5 | [11 empty] | 32.1681 | tpy
Insignificant Emission Units
N/A | Fly and Bottom Ash Bin Vent Filter |  |  | N/A | See detailed calculations in Table D-2.7b |  |  | 1460 | acfm | 8760 | hr/yr | 0.4744 | tpy
N/A | Ash Loadout to Truck |  |  | N/A | See detailed calculations in Table D-2.7b |  |  | N/A |  | 67959.5238 | tpyf | 0.004284 | tpy
N/A | Aboveground Storage Tanks |  |  | Diesel | N/A | N/A |  | N/A |  | N/A |  | 0 | tpy
N/A | Underground Storage Tanks |  |  | Diesel | N/A | N/A |  | N/A |  | N/A |  | 0 | tpy
Insignificant Emission Units Total Potential to Emit - PM2.5 | [11 empty] | 0.47869 | tpy
Total Unlimited Potential to Emit - PM2.5 | [11 empty] | 32.6468 | tpy2
[12 empty] | 1.664 | tpy |  | 0.24961 | tpy |  | 0.1664 | tpy |  | 1.1648 | tpy
Notes:
a PM2.5 potential to emit calculations conservatively assumes that PM2.5 emissions are equal to PM10 emissions. | [14 empty] | max | 3633428.2088 |  |  | 7016903.8923 |  |  | 5491490.0027
For certified engines, PM2.5 is conservatively estimated as the PM Emission Standard applicable to that engine. | [14 empty] | min | 81283.4225 |  |  | 26519.4529 |  |  | 20754.3545
Conversion factors: | [14 empty] | ave | 496042.0924 |  |  | 728301.5196 |  |  | 569975.1023
| 1 hp | 0.7457 | kW
| Weight | 453.6 | g/lb
| Weight | 2000 | lb/ton
| Coal Heating Value | 15.12 | MMBtu/ton | From www.usibelli.com/Coal_data.php
| CARB DPF Costs | 38 | $/hp
| CARB DPF Control | 85% | PM2.5
| ODEQ Costs for DPF | 5750 | $4000-$7500 | ODEQ Clean Diesel Range, use average
| ODEQ DPF Control | 90%
| ODEQ DOC cost | 1500 | $1000-$2000 | ODEQ Clean Diesel Range, use average
| ODEQ DOC Control | 30%
Source: | DU Title V Renewal Permit Application, May 2013

## A. CPM&PM25 for CHPP Boilers
Emission Unit
Filterable PM from "Source Emission Testing Report, Doyon Utilities LLC, June 15-20, 2016, Air Pollution Testing, Inc. |  | 3 | 4 | 5 | 6 | 7 | 8 | Notes
| Flow (dscfm) | 39416 | 38521 | 38793 | 37870 | 39077 | 38555
| Fd (dscf/MMBTU) | 9612 | 9612 | 9612 | 9612 | 9612 | 9612
| O2 (%) | 5.4 | 4.8 | 4.9 | 5 | 5.1 | 4.5
| PM (gr/dscf) | 0.001 | 0.006 | 0.001 | 0.002 | 0.001 | 0.002 | Total filterable PM - not just PM2.5
| PM (lb/MMBTU) | 0.00148 | 0.011 | 0.000997 | 0.00295 | 0.00106 | 0.0039
MACTEC guidance on CPM emissions (to Mid Atlantic Regional Air Management Association) August 2008
| CPM (lb/MMBTU) | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015
| Calculated total CPM+FPM(lb/MMBTU) | 0.01648 | 0.026 | 0.015997 | 0.01795 | 0.01606 | 0.0189
So, to convert back to gr/dscf assuming this CPM loading rate (see calculations from MACT report, page 124)
| Mt/Vmstd | 0.00057676 | 0.00094516 | 0.00057792 | 0.00064442 | 0.00057294 | 0.00069986
| calculated total for CPM+FPM (gr/dscf) | 0.0088994 | 0.014584 | 0.0089172 | 0.0099434 | 0.0088405 | 0.010799 | Includes the confidence interval for CPM; additionally assumes the total FPM represents PM2.5
| CPM+FPM (lb/MMBTU) | 0.01685 | 0.02875 | 0.016246 | 0.018687 | 0.016325 | 0.019875 | Uses confidence interval for the CPM data and 25% safety factor for the FPM testing data; additional safety factor present since testing was total filterable matter.
| CPM+FPM (lb/ton) | 0.2696 | 0.46 | 0.25994 | 0.299 | 0.2612 | 0.318 | Using the highest heat rating from Usibelli data (7200-8000) btu/lb
Assumed:
| Heat Content of Coal | 8000 | BTU/lb
Note on D17: Deanne D. Hughes: Maximum value to be used for calculating emissions for all boilers in the Revised PM2.5

## 5 Coal Prep 7a 7b 7c
Table XXX Coal Handling Systems PM2.5 - Base Case for BACT Analysis
Doyon Utilities - Fort Wainwright (Privatized Emission Units)
Emission Unit |  |  | Factor Reference | PM10 Emission Factor |  | Emission Unit Rating/Capacity |  | Annual Operationa |  | Potential PM10 Emissionb |  | Potential PM2.5 Emissione
Permit ID | Description | Year Installed
7a | South Coal Handling Dust Collector (DC-01) | 2001 | Source Test, 2003 | 0.0025 | gr/dscf | 13150 | acfm | 2195 | hr/yr | 0.29961 | tpy | 0.044941 | tpy
7b | South Underbunker Dust Collector (DC-02) | 2005 | Manufacturer's guaranteec | 0.02 | gr/dscf | 884 | acfm | 100 | hr/yr | 0.0073406 | tpy | 0.0011011 | tpy
7c | North Coal Handling Dust Collector (NDC-1) | 2004 | Typical Value | 0.02 | gr/dscf | 9250 | acfm | 45 | hr/yr | 0.034565 | tpy | 0.0051847 | tpy
Total Emissions | [9 empty] | 0.34151 | tpy | 0.051227 | tpy
Notes:
a Annual operating hours:
| Maximum allowable coal consumption |  | 336000 | tpy
| Conveyor operation rate |  | 150 | tph
| Annual operating hours for coal handling |  | 2240 | hrs/yr
| Average daily coal handling operations |  | 6.137 | hr/day, 365 operating days per year
| Percent of time South coal handling dust collector is in use |  | 98 | percent, primary coal handling system
| Percent of time North coal handling dust collector is in use |  | 2 | percent, North handling system is emergency backup to South handling system
| Underbunker dust collector operating hours |  | 100 | hrs/yr, used only when emptying coal bunker for unscheduled boiler shutdown or bunker fire
b Coal handling dust collection emission calculations:
(exhaust rate, acfm) x (Temp at STP/Temp of exhaust) x (PM10 exhaust concentration, gr/dscf) x (1 lb/ 7,000 gr) x (1 ton/ 2,000 lb) x (60 min/hr) x (operation, hr/yr)
| Temperature at standard conditions = |  | 68 | degrees Fahrenheit |  |  |  | 293.15 | degrees Kelvin
| Exhaust temperature dust collectors = |  | 85 | degrees Fahrenheit |  |  |  | 302.5944 | degrees Kelvin
c Manufacturer's guarantee for particle sizes 2 microns in diameter and larger; PM2.5 estimate is conservative as the 15% ratio identified in note e uses PM10 as the basis.
e Using the "Proposed Revisions to Fine Fraction Ratios Used for AP-42 Fugitive Dust Emission Factors" report authored by Chatten Cowherd, Jr., John Donaldson, and Robert Hegarty Midwest Research Institute, 425 Volker Blvd., Kansas City, MO 64110 ccowherd@mriresearch.org, in 2006, PM2.5 is calculated from these sources as 0.15*PM10.
Original Source: Table D 1.7a of Title V Renewal Permit Application, May 2013

## 7 DU Ash Handling
Table XXX. - Ash Handling System PM2.5 - Base Case for BACT Analaysis
Doyon Utilities - Fort Wainwright (Privatized Emission Units)
Emission Unit |  |  | Factor Reference | PM10 Emission Factord |  | Emission Unit Rating/Capacity |  | Annual Operation |  | Potential PM10 Emissionb |  | Potential PM2.5 Emissione
Permit ID | Description | Year Installed
Significant Sources
51a | Fly Ash Dust Collector (DC-1) | 1993 | Typical Value | 0.02 | gr/dscf | 3620 | acfm | 4380 | hr/yr f | 1.1763 | tpya | 0.17644 | tpy
51b | Bottom Ash Dust Collector (DC-2) | 1994 | Typical Value | 0.02 | gr/dscf | 3620 | acfm | 4380 | hr/yr f | 1.1763 | tpya | 0.17644 | tpy
Insignficant Sources
N/A | Fly and Bottom Ash Bin Vent Filter | 1993 | Manufacturer's guaranteec | 0.02 | gr/scfm | 1460 | acfm | 4380 | hr/yr g | 0.4744 | tpya | 0.071161 | tpy
N/A | Ash Loadout to Truck | Unknown | AP-42 11-19.2-2, truck loading conveyor crushed stone, 200% safety factor for "E" rating | 0.0003 | lb/ton |  |  | 28560 | tpy | 0.004284 | tpyb | 0.0006426 | tpy
Total Emissions | [9 empty] | 2.8312 | tpy | 0.42468 | tpy
Notes:
a Fly and bottom ash dust collector emission calculations:
(exhaust rate, acfm) x (Temp at STP/Temp of exhaust) x (PM10 exhaust concentration, gr/dscf) x (1 lb/ 7,000 gr) x (1 ton/ 2,000 lb) x (60 min/hr) x (operation, hr/yr)
| Temperature at standard conditions = |  |  |  | 68 | degrees Fahrenheit |  | 293.15 | degrees Kelvin
| Exhaust temperature of ash bin vent filter = |  |  |  | 150 | degrees Fahrenheit |  | 338.7056 | degrees Kelvin
| Exhaust temperature of fan duct blower/bag filter = |  |  |  | 150 | degrees Fahrenheit
b Ash loadout emission calculations:
Emission factor from AP-42, Section 13.2.4 based on empirical equation E = k x 0.0032 x (U/5)1.3/(M/2)1.4 lb/ton transferred where:
k = 0.35 for PM10
U = mean wind speed = 5.4 mph in Fairbanks, per National Climactic Data Center (http://lwf.ncdc.noaa.gov/oa/climate/online/ccd/avgwind.html)
M = ash moisture content = 27 percent (AP-42, Table 13.2.4-1)
Ash loadout emissions based on maximum possible coal consumption
| Boiler Rating |  |  |  |  | 230 | MMBtu/hr
| Coal Heating Value |  |  |  |  | 15.12 | MMBtu/ton | From www.usibelli.com/Coal_data.php
| Number of boilers |  |  |  |  | 6
| Maximum possible coal consumption per permit |  |  |  |  | 336000 | tpy
| Ash content of coal per Usibelli Coal Mine website |  |  |  |  | 8.5 | percent
| Operations, ash tons/yr = coal consumption x (0.085 ash content) |  |  |  |  | 28560 | tpy
Ash loadout emissions, tons/yr = (emission factor, lb/ton) x (ash loading, ton/yr) / (2,000 lb/ton)
c Manufacturer's guarantee for particle sizes over 5 microns in diameter
d To estimate uncontrolled emission factor, an estimated of 95% efficiency for dust collection filters was used. Controlled emissions are expected to be significantly less than the potential emission listed.
e Using the "Proposed Revisions to Fine Fraction Ratios Used for AP-42 Fugitive Dust Emission Factors" report authored by Chatten Cowherd, Jr., John Donaldson, and Robert Hegarty Midwest Research Institute, 425 Volker Blvd., Kansas City, MO 64110 ccowherd@mriresearch.org, in 2006, PM2.5 is calculated from these sources as 0.15*PM10.
f Average run time for DC-1 and DC-2 is 12 hours/day per reasonable inquiry of plant operations
g Operation of ash bin vent filter assumed to be the same as the dust collectors
Original Source: Table D-1.7b Ash Handling, Title V Renewal Permit Application, May 2013

## 6 DU Coal Pile
Table XXX. Potential to Emit Calculations - Emergency Coal Storage Pile PM2.5
Doyon Utilities - Fort Wainwright (Privatized Emission Units)
Emission Unit |  |  |  |  | Factor Reference |  | PM10 Emission Factor |  | Annual Operationb |  | Potential PM10 Emission |  | Potential PM2.5 Emissione
Permit ID | Description
| Coal chute to coal pile |  |  |  | AP-42, Section 13.2.4 |  | 0.00036339 | lb/tona | 90321.75 | tpy | 0.016411 | tpy | 0.0024617 | tpy
| Front end loader drop onto stockpile |  |  |  | AP-42, Section 13.2.4 |  | 0.00036339 | lb/tona | 90321.75 | tpy | 0.016411 | tpy | 0.0024617 | tpy
| Front end loader movement - chute to coal pile |  |  |  | AP-42, Section 13.2.2 |  | 2.9247 | lb/VMTc | 760.2841 | VMT | 1.1118 | tpy | 0.16677 | tpy
| Front end loader movement - coal pile to South grizzly |  |  |  | AP-42, Section 13.2.2 |  | 2.9247 | lb/VMTc | 1241.7973 | VMT | 1.816 | tpy | 0.2724 | tpy
| Front end loader movement - coal pile to North grizzly |  |  |  | AP-42, Section 13.2.2 |  | 2.9247 | lb/VMTc | 101.3712 | VMT | 0.14824 | tpy | 0.022236 | tpy
| Stockpile wind erosion |  |  |  | AP-42, Section 13.2.5 |  | 26.738 | g/m2-yrd | 3370 | m2 | 0.099324 | tpy | 0.014899 | tpy
| Front end loader drop into grizzly |  |  |  | AP-42, Section 13.2.4 |  | 0.00036339 | lb/tona | 90321.75 | tpy | 0.016411 | tpy | 0.0024617 | tpy
52 | Coal Storage Pile |  |  |  | Total Emissions | [5 empty] | 3.2246 | tpy | 3.22 | tpy
Notes:
aCoal transfer emission factor from AP-42, Section 13.2.4 based on empirical equation E = k x 0.0032 x (U/5)1.3/(M/2)1.4 lb/ton transferred where:
|  |  |  | k | 0.35 | for PM10
|  |  |  | U = mean wind speed | 5.4 | miles/hr | per http://lwf.ncdc.noaa.gov/oa/climate/online/ccd/avgwind.html
|  |  |  | M = coal moisture content | 4.8 | percent
bFor unlimited potential assume entire coal pile is turned over in one year:
|  |  |  | Coal pile volume | 133810 | yd3 | per September 24, 2012 survey
|  |  |  | Density of coal | 50 | lb/ft3
|  |  |  | Coal pile weight | 90321.75 | tons
|  |  |  | Coal moved to coal pile | 90321.75 | tpy
|  |  |  | Coal moved from coal pile | 90321.75 | tpy
cFront end loader movement emission factor from AP-42, Section 13.2.2, Empirical Equation 1a, E = k x (s/12)a x (W/3)b lb/VMT where:
|  |  |  | k | 1.5 | for PM10
|  |  |  | s = surface material silt content (haul road) | 8.4 | percent, from AP-42, Table 13.2.2-1
|  |  |  | W = mean vehicle weight | 27 | tons, estimate
|  |  |  | Size of load bucket | 5 | yd3
|  |  |  | Density of coal | 50 | lb/ft3
|  |  |  | Coal moved per trip | 3.375 | tons (Density of coal x 27 ft3/yd3 x bucket size / 2000 lb/ton)
|  |  |  | a (empirical constant) | 0.9 | from AP-42, Table 13.2.2-2
|  |  |  | b (empirical constant) | 0.45 | from AP-42, Table 13.2.2-2
|  |  |  | Approximate distance from coal chute to coal pile (round trip) | 150 | feet
|  |  |  | Approximate distance from coal pile to South grizzly (round trip) | 250 | feet
|  |  |  | Approximate distance from coal pile to North grizzly (round trip) | 1000 | feet
|  |  |  | Percent of annual coal transferred to South grizzly | 98 | percent, primary coal handling system
|  |  |  | Percent of annual coal transferred to North grizzly | 2 | percent, North handling system is emergency backup to South handling system
|  |  |  | VMT = vehicles miles traveled per year |  | VMT = annual stockpile throughput/coal moved per trip x distanced traveled per round trip in feet / 5280 ft/mi
dFrom AP-42, Section 13.2.5, Industrial Wind Erosion
Coal Pile at FWA CHPP (source: Topographic Map for the Coal Pile South of the Main Power Plant on Fort Wainwright, September 24, 2012, RCH Surveys)
|  |  |  | Average Height = | 40 | ft
|  |  |  | Width at Base = | 205 | ft | The minimum width (south face) of the coal pile is used as a conservative approach
|  |  |  | Height-to-Base Ratio = | 0.19512 |  | < 0.2. FWA CHPP coal pile can therefore be considered a large relatively flat pile with little penetration into the surface wind layer and and a single friction velocity (using Equation (1)) can be used to for the entire surface of the coal pile. Friction velocity is a measure of wind shear stress on the erodible surface.
|  |  |  | Surface Area of Active (north) Face = | 3370 | m2 | Calculated from survey using Computer Aided Design (CAD) software
AP-42 Section 13.2.5, Equation (2)
Emission factor for wind-generated particulate emissions from mixtures of erodible and nonerodible surface material subject to disturbance, EF
N
EF (g/m2-yr) = k ƩPi
i=1
|  |  | where | k = particle size multiplier (0.5 for particle size < 10 microns, per table on page 13.2.5-3)
N = number of disturbances per year
Pi = erosion potential corresponding to the fastest mile of wind for the ith period between disturbances, g/m2
AP-42 Section 13.2.5, Equation (3)
Erosion potential function for a dry exposed surface, P
P = 58 (u* - ut*)2 + 25 (u* - ut*)
P = 0 for u* < ut*
|  |  | where | u* = friction velocity (m/s)
ut = threshold friction velocity (m/s)
AP-42 Section 13.2.5, Equation (1)
Friction velocity, u*
|  |  |  | u* = 0.4 x u(z) / ln(z/zo) |  | when z >zo
|  |  | where | u* = friction velocity (cm/s)
u(z) = wind speed at height z above test surface (cm/s)
z = height above test surface (cm)
zo = roughness height, cm
Data:
|  | u(z) |  | Use maximum wind gust speed recorded at Fairbanks International Airport for each of the previous 12 months (see table below)
|  | z | 10 | meters
|  | N | 215 | disturbances/year for active face, as determined from 2012 records
|  |  | 17.9167 | average disturbances/month
|  |  |  | Uncrusted coal pile2 (Table 13.2.5-2) |  |  |  | Scraper tracks on coal pile (Table 13.2.5-2)
Month-Year | Maximum Wind Speed (u(10))1 |  | Wind Direction | Roughness Height (zo) | Threshold Friction Velocity (ut) | Calculated Friction Velocity (u*) | Erosion potential function, P | Roughness Height (zo) | Threshold Friction Velocity (ut) | Calculated Friction Velocity (u*) |  |  | Erosion potential function, P | P x N | k | Emission Factor, EF
| mph | m/s | deg | cm | m/s | m/s |  | cm | m/s | m/s | [5 empty] | g/m2-yr
2012-03-01 | 23 | 10.2819 | 250 | 0.3 | 1.12 | 0.50702 | 0 | 0.06 | 0.62 | 0.42307 |  |  | 0 | 0
2012-04-01 | 32 | 14.3053 | 320 | 0.3 | 1.12 | 0.70541 | 0 | 0.06 | 0.62 | 0.58862 |  |  | 0 | 0
2012-05-01 | 33 | 14.7523 | 140 | 0.3 | 1.12 | 0.72746 | 0 | 0.06 | 0.62 | 0.60702 |  |  | 0 | 0
2012-06-01 | 39 | 17.4346 | 110 | 0.3 | 1.12 |  | 0 | 0.06 | 0.62 | 0.71739 |  |  | 2.9847 | 53.476
2012-07-01 | 32 | 14.3053 | 320 | 0.3 | 1.12 | 0.70541 | 0 | 0.06 | 0.62 | 0.58862 |  |  | 0 | 0
2012-08-01 | 33 | 14.7523 | 260 | 0.3 | 1.12 | 0.72746 | 0 | 0.06 | 0.62 | 0.60702 |  |  | 0 | 0
2012-09-01 | 31 | 13.8582 | 240 | 0.3 | 1.12 | 0.68337 | 0 | 0.06 | 0.62 | 0.57023 |  |  | 0 | 0
2012-10-01 | 28 | 12.5171 | 60 | 0.3 | 1.12 | 0.61724 | 0 | 0.06 | 0.62 | 0.51505 |  |  | 0 | 0
2012-11-01 | 24 | 10.729 | 30 | 0.3 | 1.12 | 0.52906 | 0 | 0.06 | 0.62 | 0.44147 |  |  | 0 | 0
2012-12-01 | 26 | 11.623 | 270 | 0.3 | 1.12 | 0.57315 | 0 | 0.06 | 0.62 | 0.47826 |  |  | 0 | 0
2013-01-01 | 28 | 12.5171 | 270 | 0.3 | 1.12 | 0.61724 | 0 | 0.06 | 0.62 | 0.51505 |  |  | 0 | 0
2013-02-01 | 19 | 8.4938 | 280 | 0.3 | 1.12 | 0.41884 | 0 | 0.06 | 0.62 | 0.3495 |  |  | 0 | 0
Annual Total | [6 empty] | 0 | [5 empty] | 2.9847 | 53.476 | 0.5 | 26.738
1http://www.nws.noaa.gov/climate/index.php?wfo=pafg. Tower height of 10 meters confirmed by Fairbanks Weather Forecast Office, National Weather Service on 27-March-2013
2The erosion potential factor for the uncrusted coal pile is zero for all months. Therefore, wind erosion of the uncrusted coal pile is not a significant source of PM emissions
e Using the "Proposed Revisions to Fine Fraction Ratios Used for AP-42 Fugitive Dust Emission Factors" report authored by Chatten Cowherd, Jr., John Donaldson, and Robert Hegarty Midwest Research Institute, 425 Volker Blvd., Kansas City, MO 64110 ccowherd@mriresearch.org, in 2006, PM2.5 is calculated from these sources as 0.15*PM10.
Original Source: Title V Renewal Permit Application Table D-1.7c, May 2013

## 3a DU SO2 base case
Table xxx Sulfur Dioxide (SO2) Emissions - Base Case
Doyon Utilities - Fort Wainwright (Privatized Emission Units)
Emission Unit |  |  | Fuel | Fuel Sulfur |  | Factor | SO2 Emission |  | Emission Unit |  | Allowable Annual |  | Potential
ID | Name |  | Type | Content |  | Reference | Factor |  | Rating/Capacity |  | Operation |  | SO2 Emissions
Significant Emission Units
1 | Coal-Fired Boiler 3 |  | Coal | 0.28 | wt. pct.a | AP-42 Table 1.1-3 | 9.8 | lb/ton-coal | 336000 | tons/year | 8760 | hr/yr | 274.4 | tpy
2 | Coal-Fired Boiler 4 |  | Coal |  |  |  | 9.8 | lb/ton-coal |  |  | 8760 | hr/yr | 274.4 | tpy
3 | Coal-Fired Boiler 5 |  | Coal |  |  |  | 9.8 | lb/ton-coal |  |  | 8760 | hr/yr | 274.4 | tpy
4 | Coal-Fired Boiler 6 |  | Coal |  |  |  | 9.8 | lb/ton-coal |  |  | 8760 | hr/yr | 274.4 | tpy
5 | Coal-Fired Boiler 7 |  | Coal |  |  |  | 9.8 | lb/ton-coal |  |  | 8760 | hr/yr | 274.4 | tpy
6 | Coal-Fired Boiler 8 |  | Coal |  |  |  | 9.8 | lb/ton-coal |  |  | 8760 | hr/yr | 274.4 | tpy
7a | South Coal Handling Dust Collector (DC-01) |  | N/A | N/A |  | N/A | N/A |  | 13150 | acfm | 2195 | hr/yr | 0 | tpy
7b | South Underbunker Dust Collector (DC-02) |  | N/A | N/A |  | N/A | N/A |  | 884 | acfm | 100 | hr/yr | 0 | tpy
7c | North Coal Handling Dust Collector (NDC-1) |  | N/A | N/A |  | N/A | N/A |  | 9250 | acfm | 45 | hr/yr | 0 | tpy
8 | Caterpillar 3516C | Back up Generator Engine | Distillate | 0.0015 | wt. pct.b | Mass balance | 0.2115 | lb/1000 gal | 2937 | hp | 500 | hr/yr | 0.0079347 | tpy
9 | Detroit 6V92 | Generator Engine | Distillate | 0.5 | wt. pct. | Mass balance | 70.5 | lb/1000 gal | 352.8947 | hp | 500 | hr/yr | 0.3178 | tpy
10 | Caterpillar C15 | Generator Engine | Distillate | 0.0015 | wt. pct.b | Mass balance | 0.2115 | lb/1000 gal | 762 | hp | 500 | hr/yr | 0.0020587 | tpy
11 | Caterpillar C15 | Generator Engine | Distillate | 0.0015 | wt. pct.b | Mass balance | 0.2115 | lb/1000 gal | 762 | hp | 500 | hr/yr | 0.0020587 | tpy
12 | Cummins B3.3 | Generator Engine | Distillate | 0.5 | wt. pct. | Mass balance | 70.5 | lb/1000 gal | 82 | hp | 500 | hr/yr | 0.073845 | tpy
13 | Caterpillar 3406C TA | Generator Engine | Distillate | 0.0015 | wt. pct.b | Mass balance | 0.2115 | lb/1000 gal | 587 | hp | 500 | hr/yr | 0.0015859 | tpy
14 | Cummins QSL-G2 NR3 | Generator Engine | Distillate | 0.0015 | wt. pct.b | Mass balance | 0.2115 | lb/1000 gal | 320 | hp | 500 | hr/yr | 0.00086453 | tpy
15 | Detroit R1237M36 | Generator Engine | Distillate | 0.5 | wt. pct. | Mass balance | 70.5 | lb/1000 gal | 1058.6842 | hp | 500 | hr/yr | 0.9534 | tpy
16 | John Deere 6068TF250 | Generator Engine | Distillate | 0.5 | wt. pct. | Mass balance | 70.5 | lb/1000 gal | 211.7368 | hp | 500 | hr/yr | 0.19068 | tpy
17 | John Deere 6068TF250 | Generator Engine | Distillate | 0.0015 | wt. pct.b | Mass balance | 0.2115 | lb/1000 gal | 176.4474 | hp | 500 | hr/yr | 0.0004767 | tpy
18 | John Deere 6068HF150 | Generator Engine | Distillate | 0.5 | wt. pct. | Mass balance | 70.5 | lb/1000 gal | 211.7368 | hp | 500 | hr/yr | 0.19068 | tpy
19 | John Deere 4045TF270 | Generator Engine | Distillate | 0.0015 | wt. pct.b | Mass balance | 0.2115 | lb/1000 gal | 70.5789 | hp | 500 | hr/yr | 0.00019068 | tpy
20 | John Deere 4239D | Generator Engine | Distillate | 0.5 | wt. pct. | Mass balance | 70.5 | lb/1000 gal | 35.2895 | hp | 500 | hr/yr | 0.03178 | tpy
21 | Perkins 2046/1800 | Generator Engine | Distillate | 0.5 | wt. pct. | Mass balance | 70.5 | lb/1000 gal | 95 | hp | 500 | hr/yr | 0.085552 | tpy
22 | Cummins | Generator Engine | Distillate | 0.5 | wt. pct. | Mass balance | 70.5 | lb/1000 gal | 35.2895 | hp | 500 | hr/yr | 0.03178 | tpy
23 | John Deere 6068HF150 | Generator Engine | Distillate | 0.5 | wt. pct. | Mass balance | 70.5 | lb/1000 gal | 155.2737 | hp | 500 | hr/yr | 0.13983 | tpy
24 | Cummins L634D-I/10386E | Generator Engine | Distillate | 0.5 | wt. pct. | Mass balance | 70.5 | lb/1000 gal | 50 | hp | 500 | hr/yr | 0.045027 | tpy
25 | Caterpillar C1.5 | Generator Engine | Distillate | 0.0015 | wt. pct.b | Mass balance | 0.2115 | lb/1000 gal | 18.3505 | hp | 500 | hr/yr | 4.9577e-05 | tpy
26 | Cummins 4B3.9-G2 | Generator Engine | Distillate | 0.5 | wt. pct. | Mass balance | 70.5 | lb/1000 gal | 68 | hp | 500 | hr/yr | 0.061237 | tpy
27 | Caterpillar C6.6 | Generator Engine | Distillate | 0.0015 | wt. pct.b | Mass balance | 0.2115 | lb/1000 gal | 274 | hp | 500 | hr/yr | 0.00074025 | tpy
28 | Caterpillar C6.6 | Generator Engine | Distillate | 0.0015 | wt. pct.b | Mass balance | 0.2115 | lb/1000 gal | 274 | hp | 500 | hr/yr | 0.00074025 | tpy
29a | John Deere 4045TF290 | Lift Pump Engine | Distillate | 0.0015 | wt. pct.b | Mass balance | 0.2115 | lb/1000 gal | 74 | hp | 500 | hr/yr | 0.00019992 | tpy
30 | Detroit Diesel 10245100 | Lift Pump Engine | Distillate | 0.5 | wt. pct. | Mass balance | 70.5 | lb/1000 gal | 75 | hp | 500 | hr/yr | 0.067541 | tpy
31a | John Deere 4045TF290 | Lift Pump Engine | Distillate | 0.5 | wt. pct. | Mass balance | 70.5 | lb/1000 gal | 74 | hp | 500 | hr/yr | 0.066641 | tpy
32 | Perkins | Lift Pump Engine | Distillate | 0.5 | wt. pct. | Mass balance | 70.5 | lb/1000 gal | 75 | hp | 500 | hr/yr | 0.067541 | tpy
33 | Perkins | Lift Pump Engine | Distillate | 0.5 | wt. pct. | Mass balance | 70.5 | lb/1000 gal | 75 | hp | 500 | hr/yr | 0.067541 | tpy
34 | Detroit Diesel 10447000 | Well Pump Engine | Distillate | 0.5 | wt. pct. | Mass balance | 70.5 | lb/1000 gal | 220 | hp | 500 | hr/yr | 0.19812 | tpy
35 | John Deere 4045DF120 | Well Pump Engine | Distillate | 0.0015 | wt. pct.b | Mass balance | 0.2115 | lb/1000 gal | 55 | hp | 500 | hr/yr | 0.00014859 | tpy
36 | Detroit Diesel 4031-C | Well Pump Engine | Distillate | 0.5 | wt. pct. | Mass balance | 70.5 | lb/1000 gal | 220 | hp | 500 | hr/yr | 0.19812 | tpy
51a | Fly Ash Dust Collector (DC-1) |  | N/A | N/A |  | N/A | N/A |  | 3620 | acfm | 4380 | hr/yr | 0 | tpy
51b | Bottom Ash Dust Collector (DC-2) |  | N/A | N/A |  | N/A | N/A |  | 3620 | acfm | 4380 | hr/yr | 0 | tpy
52 | Coal Storage Pile |  | N/A | N/A |  | N/A | N/A |  | N/A |  | 82049 | tpy | 0 | tpy
Significant Emission Units Potential to Emit - SO2 | [12 empty] | 1649.2042 | tpy
Insignificant Emission Units
N/A | Fly and Bottom Ash Bin Vent Filter |  | N/A | N/A |  | N/A | N/A |  | 1460 | acfm | 4380 | hr/yr | 0 | tpy
N/A | Ash Loadout to Truck |  | N/A | N/A |  | N/A | N/A |  | N/A |  | 28560 | tpy | 0 | tpy
N/A | Aboveground Storage Tanks |  | Diesel | N/A |  | N/A | N/A |  | N/A |  | N/A |  | 0 | tpy
N/A | Underground Storage Tanks |  | Diesel | N/A |  | N/A | N/A |  | N/A |  | N/A |  | 0 | tpy
Insignificant Emission Units Potential to Emit - SO2 | [12 empty] | 0 | tpy
Total Potential to Emit - SO2 | [12 empty] | 1649.2042 | tpy
Notes:
a Weighted Sulfur content, averaged over 2015-2016=0.13
b For engines subject to 40 CFR 60 Subpart IIII, fuel used must meet the requirements of 40 CFR 80.510(b).
Conversion factors:
| Diesel Heating Value |  | 137000 | Btu/gal | From AP 42, Appendix A, Page A-5
| Density of Diesel |  | 7.05 | lb/gal | From AP 42, Appendix A, Page A-7, density for Distillate Oil
| Engine Heat Rate |  | 7000 | Btu/hp-hr | Average brake-specific fuel consumption (BSFC) from AP 42, Table 3.3-1, footnote a
| Weight |  | 2000 | lb/ton
| Coal Heating Value |  | 15.12 | MMBtu/ton | From www.usibelli.com/Coal_data.php
SO2 emissions from Coal combustion at CHPP
AP-42 emission factor, table 1.1-3 |  | 35*%S by weight
| % S by weight | 0.28 | Usibelli Coal Data sheet indicates range between 0.08 and 0.28% gross as received. http://www.usibelli.com/coal/data-sheet, accessed June 8, 2017
| SO2 emission factor | 9.8 | lb/ton coal
From CHPP data
| coal BTU content | 7572 | Btu/lb | 2016 average
SO2 |  | 0.64712 | lb SO2/MMBTU
Original Source: Title V Renewal Permit Application, Table D-1.10 SO2, May 2013

## 3b DU SO2 Proposed
Table xxx Sulfur Dioxide (SO2) Emissions - Propsed
Doyon Utilities - Fort Wainwright (Privatized Emission Units)
Emission Unit |  |  | Fuel | Fuel Sulfur |  | Factor | SO2 Emission |  | Emission Unit |  | Allowable Annual |  | Potential
ID | Name |  | Type | Content |  | Reference | Factor |  | Rating/Capacity |  | Operation |  | SO2 Emissions
Significant Emission Units
1 | Coal-Fired Boiler 3 |  | Coal | 0.2 | wt. pct.a | AP-42 Table 1.1-3 | 7 | lb/ton-coal | 300000 | tons/year | 8760 | hr/yr | 175 | tpy
2 | Coal-Fired Boiler 4 |  | Coal |  |  |  |  | lb/ton-coal |  |  | 8760 | hr/yr | 175 | tpy
3 | Coal-Fired Boiler 5 |  | Coal |  |  |  |  | lb/ton-coal |  |  | 8760 | hr/yr | 175 | tpy
4 | Coal-Fired Boiler 6 |  | Coal |  |  |  |  | lb/ton-coal |  |  | 8760 | hr/yr | 175 | tpy
5 | Coal-Fired Boiler 7 |  | Coal |  |  |  |  | lb/ton-coal |  |  | 8760 | hr/yr | 175 | tpy
6 | Coal-Fired Boiler 8 |  | Coal |  |  |  |  | lb/ton-coal |  |  | 8760 | hr/yr | 175 | tpy
7a | South Coal Handling Dust Collector (DC-01) |  | N/A | N/A |  | N/A | N/A |  | 13150 | acfm | 2195 | hr/yr | 0 | tpy
7b | South Underbunker Dust Collector (DC-02) |  | N/A | N/A |  | N/A | N/A |  | 884 | acfm | 100 | hr/yr | 0 | tpy
7c | North Coal Handling Dust Collector (NDC-1) |  | N/A | N/A |  | N/A | N/A |  | 9250 | acfm | 45 | hr/yr | 0 | tpy
8 | Caterpillar 3516C | Backup Generator Engine | Distillate | 0.0015 | wt. pct.b | Mass balance | 0.2115 | lb/1000 gal | 2937 | hp | 500 | hr/yr | 0.0079347 | tpy
9 | Detroit 6V92 | Generator Engine | Distillate | 0.0015 | wt. pct. | Mass balance | 0.2115 | lb/1000 gal | 352.8947 | hp | 500 | hr/yr | 0.0009534 | tpy
10 | Caterpillar C15 | Generator Engine | Distillate | 0.0015 | wt. pct.b | Mass balance | 0.2115 | lb/1000 gal | 762 | hp | 500 | hr/yr | 0.0020587 | tpy
11 | Caterpillar C15 | Generator Engine | Distillate | 0.0015 | wt. pct.b | Mass balance | 0.2115 | lb/1000 gal | 762 | hp | 500 | hr/yr | 0.0020587 | tpy
12 | Cummins B3.3 | Generator Engine | Distillate | 0.0015 | wt. pct. | Mass balance | 0.2115 | lb/1000 gal | 82 | hp | 500 | hr/yr | 0.00022153 | tpy
13 | Caterpillar 3406C TA | Generator Engine | Distillate | 0.0015 | wt. pct.b | Mass balance | 0.2115 | lb/1000 gal | 587 | hp | 500 | hr/yr | 0.0015859 | tpy
14 | Cummins QSL-G2 NR3 | Generator Engine | Distillate | 0.0015 | wt. pct.b | Mass balance | 0.2115 | lb/1000 gal | 320 | hp | 500 | hr/yr | 0.00086453 | tpy
15 | Detroit R1237M36 | Generator Engine | Distillate | 0.0015 | wt. pct. | Mass balance | 0.2115 | lb/1000 gal | 1058.6842 | hp | 500 | hr/yr | 0.0028602 | tpy
16 | John Deere 6068TF250 | Generator Engine | Distillate | 0.0015 | wt. pct. | Mass balance | 0.2115 | lb/1000 gal | 211.7368 | hp | 500 | hr/yr | 0.00057204 | tpy
17 | John Deere 6068TF250 | Generator Engine | Distillate | 0.0015 | wt. pct.b | Mass balance | 0.2115 | lb/1000 gal | 176.4474 | hp | 500 | hr/yr | 0.0004767 | tpy
18 | John Deere 6068HF150 | Generator Engine | Distillate | 0.0015 | wt. pct. | Mass balance | 0.2115 | lb/1000 gal | 211.7368 | hp | 500 | hr/yr | 0.00057204 | tpy
19 | John Deere 4045TF270 | Generator Engine | Distillate | 0.0015 | wt. pct.b | Mass balance | 0.2115 | lb/1000 gal | 70.5789 | hp | 500 | hr/yr | 0.00019068 | tpy
20 | John Deere 4239D | Generator Engine | Distillate | 0.0015 | wt. pct. | Mass balance | 0.2115 | lb/1000 gal | 35.2895 | hp | 500 | hr/yr | 9.534e-05 | tpy
21 | Perkins 2046/1800 | Generator Engine | Distillate | 0.0015 | wt. pct. | Mass balance | 0.2115 | lb/1000 gal | 95 | hp | 500 | hr/yr | 0.00025666 | tpy
22 | Cummins | Generator Engine | Distillate | 0.0015 | wt. pct. | Mass balance | 0.2115 | lb/1000 gal | 35.2895 | hp | 500 | hr/yr | 9.534e-05 | tpy
23 | John Deere 6068HF150 | Generator Engine | Distillate | 0.0015 | wt. pct. | Mass balance | 0.2115 | lb/1000 gal | 155.2737 | hp | 500 | hr/yr | 0.00041949 | tpy
24 | Cummins L634D-I/10386E | Generator Engine | Distillate | 0.0015 | wt. pct. | Mass balance | 0.2115 | lb/1000 gal | 50 | hp | 500 | hr/yr | 0.00013508 | tpy
25 | Caterpillar C1.5 | Generator Engine | Distillate | 0.0015 | wt. pct.b | Mass balance | 0.2115 | lb/1000 gal | 18.3505 | hp | 500 | hr/yr | 4.9577e-05 | tpy
26 | Cummins 4B3.9-G2 | Generator Engine | Distillate | 0.0015 | wt. pct. | Mass balance | 0.2115 | lb/1000 gal | 68 | hp | 500 | hr/yr | 0.00018371 | tpy
27 | Caterpillar C6.6 | Generator Engine | Distillate | 0.0015 | wt. pct.b | Mass balance | 0.2115 | lb/1000 gal | 274 | hp | 500 | hr/yr | 0.00074025 | tpy
28 | Caterpillar C6.6 | Generator Engine | Distillate | 0.0015 | wt. pct.b | Mass balance | 0.2115 | lb/1000 gal | 274 | hp | 500 | hr/yr | 0.00074025 | tpy
29a | John Deere 4045TF290 | Lift Pump Engine | Distillate | 0.0015 | wt. pct.b | Mass balance | 0.2115 | lb/1000 gal | 74 | hp | 500 | hr/yr | 0.00019992 | tpy
30 | Detroit Diesel 10245100 | Lift Pump Engine | Distillate | 0.0015 | wt. pct. | Mass balance | 0.2115 | lb/1000 gal | 75 | hp | 500 | hr/yr | 0.00020262 | tpy
31a | John Deere 4045TF290 | Lift Pump Engine | Distillate | 0.0015 | wt. pct. | Mass balance | 0.2115 | lb/1000 gal | 74 | hp | 500 | hr/yr | 0.00019992 | tpy
32 | Perkins | Lift Pump Engine | Distillate | 0.0015 | wt. pct. | Mass balance | 0.2115 | lb/1000 gal | 75 | hp | 500 | hr/yr | 0.00020262 | tpy
33 | Perkins | Lift Pump Engine | Distillate | 0.0015 | wt. pct. | Mass balance | 0.2115 | lb/1000 gal | 75 | hp | 500 | hr/yr | 0.00020262 | tpy
34 | Detroit Diesel 10447000 | Well Pump Engine | Distillate | 0.0015 | wt. pct. | Mass balance | 0.2115 | lb/1000 gal | 220 | hp | 500 | hr/yr | 0.00059436 | tpy
35 | John Deere 4045DF120 | Well Pump Engine | Distillate | 0.0015 | wt. pct.b | Mass balance | 0.2115 | lb/1000 gal | 55 | hp | 500 | hr/yr | 0.00014859 | tpy
36 | Detroit Diesel 4031-C | Well Pump Engine | Distillate | 0.5 | wt. pct. | Mass balance | 70.5 | lb/1000 gal | 220 | hp | 500 | hr/yr | 0.19812 | tpy
51a | Fly Ash Dust Collector (DC-1) |  | N/A | N/A |  | N/A | N/A |  | 3620 | acfm | 4380 | hr/yr | 0 | tpy
51b | Bottom Ash Dust Collector (DC-2) |  | N/A | N/A |  | N/A | N/A |  | 3620 | acfm | 4380 | hr/yr | 0 | tpy
52 | Coal Storage Pile |  | N/A | N/A |  | N/A | N/A |  | N/A |  | 82049 | tpy | 0 | tpy
Significant Emission Units Potential to Emit - SO2 | [12 empty] | 1050.2229 | tpy
Insignificant Emission Units
N/A | Fly and Bottom Ash Bin Vent Filter |  | N/A | N/A |  | N/A | N/A |  | 1460 | acfm | 8760 | hr/yr | 0 | tpy
N/A | Ash Loadout to Truck |  | N/A | N/A |  | N/A | N/A |  | N/A |  | 67959.5238 | tpy | 0 | tpy
N/A | Aboveground Storage Tanks |  | Diesel | N/A |  | N/A | N/A |  | N/A |  | N/A |  | 0 | tpy
N/A | Underground Storage Tanks |  | Diesel | N/A |  | N/A | N/A |  | N/A |  | N/A |  | 0 | tpy
Insignificant Emission Units Potential to Emit - SO2 | [12 empty] | 0 | tpy
Total Potential to Emit - SO2 | [12 empty] | 1050.2229 | tpy
Notes:
a Weighted Sulfur content, averaged over 2015-2016=0.13
b For engines subject to 40 CFR 60 Subpart IIII, fuel used must meet the requirements of 40 CFR 80.510(b).
Conversion factors:
| Diesel Heating Value |  | 137000 | Btu/gal | From AP 42, Appendix A, Page A-5
| Density of Diesel |  | 7.05 | lb/gal | From AP 42, Appendix A, Page A-7, density for Distillate Oil
| Engine Heat Rate |  | 7000 | Btu/hp-hr | Average brake-specific fuel consumption (BSFC) from AP 42, Table 3.3-1, footnote a
| Weight |  | 2000 | lb/ton
| Coal Heating Value |  | 15.12 | MMBtu/ton | From www.usibelli.com/Coal_data.php
SO2 emissions from Coal combustion at CHPP
AP-42 emission factor, table 1.1-3 |  | 35*%S by weight
| % S by weight | 0.2 | Usibelli Coal Data sheet indicates range between 0.08 and 0.28% gross as received. http://www.usibelli.com/coal/data-sheet, accessed June 8, 2017
| SO2 emission factor | 7 | lb/ton coal
From CHPP data
| coal BTU content | 7572 | Btu/lb | 2016 average
SO2 |  | 0.46223 | lb SO2/MMBTU

## 17 Proposed BACT Engines SO2
Location | EU | Make | Description | Year | Status |  |  | Size (hp) | Annual Operating Limits (non-Emergency) | Proposed BACT
DU | 8 | Caterpillar 3516C | Backup Generator Engine | 2009 | Certified Engine | 6.4 | g/kw-hr | 2937 | 500 | Comply with 40 CFR 60 Subpart IIII
DU | 9 | Detroit 6V92 | Generator Engine | 1988 |  | 0.031 | lb/hp-hr | 352.8947 | 500 | Limit fuel to ULSD.
DU | 10 | Caterpillar C15 | Generator Engine | 2010 | Certified Engine | 6.4 | g/kw-hr | 762 | 500 | Comply with 40 CFR 60 Subpart IIII
DU | 11 | Caterpillar C15 | Generator Engine | 2010 | Certified Engine | 6.4 | g/kw-hr | 762 | 500 | Comply with 40 CFR 60 Subpart IIII
DU | 12 | Cummins B3.3 | Generator Engine | 2002 |  | 0.031 | lb/hp-hr | 82 | 500 | Limit fuel to ULSD.
DU | 13 | Caterpillar 3406C TA | Generator Engine | 2008 | Certified Engine | 4 | g/kw-hr | 587 | 500 | Comply with 40 CFR 60 Subpart IIII
DU | 14 | Cummins QSL-G2 NR3 | Generator Engine | 2008 | Certified Engine | 4 | g/kw-hr | 320 | 500 | Comply with 40 CFR 60 Subpart IIII
DU | 15 | Detroit R1237M36 | Generator Engine | 2005 | Mfg Information | 5.75 | g/hp-hr | 1058.6842 | 500 | Limit fuel to ULSD.
DU | 16 | John Deere 6068TF250 | Generator Engine | 2005 |  | 0.031 | lb/hp-hr | 211.7368 | 500 | Limit fuel to ULSD.
DU | 17 | John Deere 6068TF250 | Generator Engine | 2007 | Permit condition 23.1c | 6.9 | g/hp-hr | 176.4474 | 500 | Limit fuel to ULSD.
DU | 18 | John Deere 6068HF150 | Generator Engine | 2005 |  | 0.031 | lb/hp-hr | 211.7368 | 500 | Limit fuel to ULSD.
DU | 19 | John Deere 4045TF270 | Generator Engine | 2007 | Certified Engine | 7.5 | g/kw-hr | 70.5789 | 500 | Comply with 40 CFR 60 Subpart IIII
DU | 20 | John Deere 4239D | Generator Engine | 1976 |  | 0.031 | lb/hp-hr | 35.2895 | 500 | Limit fuel to ULSD.
DU | 21 | Perkins 2046/1800 | Generator Engine | 2001 |  | 0.031 | lb/hp-hr | 95 | 500 | Limit fuel to ULSD.
DU | 22 | Cummins | Generator Engine | 1989 |  | 0.031 | lb/hp-hr | 35.2895 | 500 | Limit fuel to ULSD.
DU | 23 | John Deere 6068HF150 | Generator Engine | 2003 |  | 0.031 | lb/hp-hr | 155.2737 | 500 | Limit fuel to ULSD.
DU | 24 | Cummins L634D-I/10386E | Generator Engine | 1993 |  | 0.031 | lb/hp-hr | 50 | 500 | Limit fuel to ULSD.
DU | 25 | Caterpillar C1.5 | Generator Engine | 2011 | Certified Engine | 7.5 | g/kw-hr | 18.3505 | 500 | Comply with 40 CFR 60 Subpart IIII
DU | 26 | Cummins 4B3.9-G2 | Generator Engine | 2003 |  | 0.031 | lb/hp-hr | 68 | 500 | Limit fuel to ULSD.
DU | 27 | Caterpillar C6.6 | Generator Engine | 2010 | Certified Engine | 4 | g/kw-hr | 274 | 500 | Comply with 40 CFR 60 Subpart IIII
DU | 28 | Caterpillar C6.6 | Generator Engine | 2010 | Certified Engine | 4 | g/kw-hr | 274 | 500 | Comply with 40 CFR 60 Subpart IIII
DU | 30 | Detroit Diesel 10245100 | Lift Pump Engine | 1952 |  | 0.031 | lb/hp-hr | 75 | 500 | Limit fuel to ULSD.
DU | 32 | Perkins | Lift Pump Engine | 1955 |  | 0.031 | lb/hp-hr | 75 | 500 | Limit fuel to ULSD.
DU | 33 | Perkins | Lift Pump Engine | 1994 |  | 0.031 | lb/hp-hr | 75 | 500 | Limit fuel to ULSD.
DU | 34 | Detroit Diesel 10447000 | Well Pump Engine | 1995 |  | 0.031 | lb/hp-hr | 220 | 500 | Limit fuel to ULSD.
DU | 35 | John Deere 4045DF120 | Well Pump Engine | 2009 | Certified Engine | 7.8 | g/hp-hr | 55 | 500 | Comply with 40 CFR 60 Subpart IIII
DU | 36 | Detroit Diesel 4031-C | Well Pump Engine | 1995 |  | 0.031 | lb/hp-hr | 220 | 500 | Limit fuel to ULSD.
DU | 29a | John Deere 4045TF290 | Lift Pump Engine | 2014 | Certified Engine | 4.7 | g/kW-hr | 74 | 500 | Comply with 40 CFR 60 Subpart IIII
DU | 31a | John Deere 4045TF290 | Lift Pump Engine | 2014 | Certified Engine | 4.7 | g/kW-hr | 74 | 500 | Comply with 40 CFR 60 Subpart IIII
FWA | 11 | Caterpillar | 3512 | 2003 |  |  |  | 1454 | 200 | Owner Requested Limit of 600 hours/12-month period cumulative for these three engines.
FWA | 12 | Caterpillar | 3512 | 2003 |  |  |  | 1454 | 200
FWA | 13 | Caterpillar | 3512 | 2003 |  |  |  | 1454 | 200
FWA | 26 | Cummins | QSB7-G3 NR3 | 2012 | Certified Engine |  |  | 295 | 500 | Comply with 40 CFR 60 Subpart IIII
FWA | 27 | John Deere | 4024HF285B | 2009 | Certified Engine |  |  | 67 | 500 | Comply with 40 CFR 60 Subpart IIII
FWA | 28 | Caterpillar | CAT C9 GENSET | 2007 | Certified Engine |  |  | 398 | 500 | Comply with 40 CFR 60 Subpart IIII
FWA | 29 | SDMO | TM30UCM | ND |  |  |  | 47 | 500 | Limit fuel to ULSD.
FWA | 30 | John Deere | JW64-UF30 | 2007 | Certified Engine |  |  | 275 | 500 | Comply with 40 CFR 60 Subpart IIII
FWA | 31 | Clarke | DDFP-04AT | 1994 |  |  |  | 235 | 500 | Limit fuel to ULSD.
FWA | 32 | Clarke | DDFP-04AT | 1994 |  |  |  | 235 | 500 | Limit fuel to ULSD.
FWA | 33 | Clarke | DDFP-04AT | 1994 |  |  |  | 235 | 500 | Limit fuel to ULSD.
FWA | 34 | Clarke | DDFP-04AT | 1994 |  |  |  | 235 | 500 | Limit fuel to ULSD.
FWA | 35 | Cummins | N-855-F | 1977 |  |  |  | 240 | 500 | Limit fuel to ULSD.
FWA | 36 | Cummins | N-855-F | 1977 |  |  |  | 240 | 500 | Limit fuel to ULSD.
FWA | 37 | Clarke | JU4H-UF40 | 2005 |  |  |  | 94 | 500 | Limit fuel to ULSD.
FWA | 38 | Clarke | PDFP-06YT | 1996 |  |  |  | 120 | 500 | Limit fuel to ULSD.
FWA | 39 | Clarke | PDFP-06YT | 1996 |  |  |  | 120 | 500 | Limit fuel to ULSD.
Note on I34: Deanne Hughes: Revised from 134 hp based on nameplate provided by Eric 4/18/17.
Note on I36: Changed from 334 to match Mfg. Information

## SO2 costs for wet and semi dry
Source: Andreas Poullikkas, "Review of Design, Operating, and Financial Considerations in Flue Gas Desulfurization Systems" Energy Technology and Policy, June 2015
Wet Scrubber
191 | $/KW | capital low
316 | $/Kw | capital high
0.78 | cents/kwH | operating low
1.56 | cents/kwH | operating high
1380 | MMBTU/hr | total capacity
11120 | btu/kw | CHPP data report
1 | kWh | equals | 3413 | BTU
8000 | btu/lb | Usibelli Coal data sheet
300000 | ton/yr | coal combustion
124100.7194 | kW
23703237.4101 | $ capital low
39215827.3381 | $ capital high
10969821.2716 | $/year operating expense, low estimate
21939642.5432 | $/year operating expense, high estimate
Base case | 1764 | tpy
Control | 90%
Removed | 1587.6
$/ton | 6909.6884
$/ton | 13819.3768
Semi Dry System
125 | $/KW | capital low
216 | $/Kw | capital high
0.59 | cents/kwH | operating low
0.7 | cents/kwH | operating high
1380 | MMBTU/hr | total capacity
11120 | btu/kw | CHPP data report
1 | kWh | equals | 3413 | BTU
8000 | btu/lb | Usibelli Coal data sheet
300000 | ton/yr | coal combustion
124100.7194 | kW
15512589.9281 | $ capital low
26805755.3957 | $ capital high
8297685.3208 | $/year operating expense, low estimate
9844711.3976 | $/year operating expense, high estimate
Base case | 1764 | tpy
Control | 90%
Removed | 1587.6
$/ton | 5226.5592
$/ton | 6201.0024

## Notes for calcs - DDH (hidden)
Derived PM2.5 from Filterable PM Testing, 2016
AP-42 Emission Factors
Section 1.1, 9/98
Rating
PM 2.5, Stoker | 0.032 | lb/MMBTU | C | Table 1.1.9
PM10 Filterable, Spreader Stoker, uncontrolled | 13.2 | lb/ton | E | Table 1.1.4
PM, Filterable, Spreader Stoker, uncontrolled | 66 | lb/ton | B | Table 1.1.4
PM-Total Condensable, uncontrolled | 0.04 | lb/MMBTU | C | Table 1.1.5
Sub bit heat content | 20 | MMBTU/ton |  | footnote e, table 1.1.5
MACT 2016 Testing, Air Polllution Testing June 2016
| Unit 3 | Unit 4 | Unit 5 | Unit 6 | Unit 7 | Unit 8
Average Filterable PM, lb/mmbtu | 0.00148 | 0.011 | 0.000997 | 0.00295 | 0.00106 | 0.0039
Converting AP-42 data to lb/mmbtu using 20 MMBTU/ton per AP-42 notation
Ours is really 15.1 MMBTU/ton |  |  | @15 mmbtu/ton
PM10 Filterable, Spreader Stoker, uncontrolled | 0.66 | lb/MMBtu | 0.87417 | lb/mmbtu
PM, Filterable, Spreader Stoker, uncontrolled | 3.3 | lb/MMBtu
Volumetric flow rate at MACT testing | 38705.3333 | dscfm
Fd | 9612 | dscf/MMBTU
grain loading | 0.01 | grain/dscf
Conversion | 1 | grain | equals | 0.00014286 | pounds
PM emissions per grain loading guarantee | 0.055293 | lb/min/boiler stack
| 3.3176 | lb/hr/stack
Permit Limit in lb/MMBTU, Filterable PM | 0.04 | lb/mmbtu
Boiler Size, each | 230 | MMBTU/hr
Filterable PM limit, lb/hr | 9.2 | lb/hr
PM2.5 proposed PTE | 0.16 | lb/ton
| 1.0228 | lb/hr, annual average
0.010596
AP-42 CPM Total | 0.04 | lb/mmbtu
AP-42 PM2.5, Bit Coal, Baghouse Controlled | 0.032 | lb/ton
| 0.20457 | lb/hr, annual average
0.0021192

## DU CHPP (hidden)
[7 empty] | DOW |  |  |  | DOW | Dow | [7 empty] | DOW | Dow | [7 empty] | Dow | Dow
Permit AQ1121TVP02 Emission Units | [8 empty] | Potential To Emit Calculations | [25 empty] | 201X Actual Emission Calculations
Permit | EU ID | Emission Unit Name | Description | Size | Rating | Installation or Construction Date | 201X Hours/Year | PTE Hours/Year | NOX Emission Control Efficiency (%) | NOX Emission Control Efficiency Basis | Source Test NOX Emission Factor | Source Test Reference | NOX emission factor | NOX emission factor units | NOX emission factor basis | NOX emissions (TPY) | SO2 Emission Control Device (if present) | SO2 Emission Control Efficiency (%) | SO2 Emission Control Efficiency Basis | Source Test SO2 Emission Factor | Source Test Reference | SO2 emission factor | SO2 emission factor units | SO2 emission factor basis | SO2 emissions (TPY) | PM2.5 Emission Control Device (If present) | PM2.5 Emission Control Efficiency (%) | PM2.5 Emission Control Efficiency Basis | Source Test PM2.5 Emission Factor | Source Test Reference | PM2.5 emission factor | PM2.5 emission factor units | PM2.5 emission factor basis | PM2.5 emissions (TPY) | NOX Emission Control Efficiency (%) | NOX Emission Control Efficiency Basis | NOX emission factor | NOX emission factor units | NOX emission factor basis | NOX emissions (TPY) | SO2 Emission Control Device (if present) | SO2 Emission Control Efficiency (%) | SO2 Emission Control Efficiency Basis | SO2 emission factor | SO2 emission factor units | SO2 emission factor basis | SO2 emissions (TPY) | PM2.5 Emission Control Device (If present) | PM2.5 Emission Control Efficiency (%) | PM2.5 Emission Control Efficiency Basis | PM2.5 emission factor | PM2.5 emission factor units | PM2.5 emission factor basis | PM2.5 emissions (TPY)
Coal Fired Boilers
AQ1121TVP02 | 1 | Coal‐Fired Boiler 3 | Central Heating & Power Plant | 230 | MMBtu/hr | 1953
AQ1121TVP02 | 2 | Coal‐Fired Boiler 4 | Central Heating & Power Plant | 230 | MMBtu/hr | 1953
AQ1121TVP02 | 3 | Coal‐Fired Boiler 5 | Central Heating & Power Plant | 230 | MMBtu/hr | 1953
AQ1121TVP02 | 4 | Coal‐Fired Boiler 6 | Central Heating & Power Plant | 230 | MMBtu/hr | 1953
AQ1121TVP02 | 5 | Coal‐Fired Boiler 7 | Central Heating & Power Plant | 230 | MMBtu/hr | 1953
AQ1121TVP02 | 6 | Coal‐Fired Boiler 8 | Central Heating & Power Plant | 230 | MMBtu/hr | 1953
Table notes:
1. EU ID 13 was installed in 2008, but the engine build date is February 17, 1999.

## DU Material Handling (hidden)
[8 empty] | DOW |  |  |  | DOW | Dow | [7 empty] | DOW | Dow | [7 empty] | Dow | Dow
Permit AQ1121TVP02 Emission Units | [9 empty] | Potential To Emit Calculations | [25 empty] | 201X Actual Emission Calculations
Permit | EU ID | Emission Unit Name | Description | Size | Rating | Installation or Construction Date | Applicable ZZZZ requirement for area source | 201X Hours/Year | PTE Hours/Year | NOX Emission Control Efficiency (%) | NOX Emission Control Efficiency Basis | Source Test NOX Emission Factor | Source Test Reference | NOX emission factor | NOX emission factor units | NOX emission factor basis | NOX emissions (TPY) | SO2 Emission Control Device (if present) | SO2 Emission Control Efficiency (%) | SO2 Emission Control Efficiency Basis | Source Test SO2 Emission Factor | Source Test Reference | SO2 emission factor | SO2 emission factor units | SO2 emission factor basis | SO2 emissions (TPY) | PM2.5 Emission Control Device (If present) | PM2.5 Emission Control Efficiency (%) | PM2.5 Emission Control Efficiency Basis | Source Test PM2.5 Emission Factor | Source Test Reference | PM2.5 emission factor | PM2.5 emission factor units | PM2.5 emission factor basis | PM2.5 emissions (TPY) | NOX Emission Control Efficiency (%) | NOX Emission Control Efficiency Basis | NOX emission factor | NOX emission factor units | NOX emission factor basis | NOX emissions (TPY) | SO2 Emission Control Device (if present) | SO2 Emission Control Efficiency (%) | SO2 Emission Control Efficiency Basis | SO2 emission factor | SO2 emission factor units | SO2 emission factor basis | SO2 emissions (TPY) | PM2.5 Emission Control Device (If present) | PM2.5 Emission Control Efficiency (%) | PM2.5 Emission Control Efficiency Basis | PM2.5 emission factor | PM2.5 emission factor units | PM2.5 emission factor basis | PM2.5 emissions (TPY)
Material Handling
AQ1121TVP02 | 7a | DC-01 | South Coal Handling Dust Collector | 13150 | acfm | 2001
AQ1121TVP02 | 7b | DC-02 | South Under‐bunker Dust Collector | 884 | acfm | 2005
AQ1121TVP02 | 7c | NDC-1 | North Coal Handling Dust Collector | 9250 | acfm | 2004
AQ1121TVP02 | 51a | DC-1 | Fly Ash Dust Collector | 3620 | acfm | 1993
AQ1121TVP02 | 51b | DC-2 | Bottom Ash Dust Collector | 3620 | acfm | 1994
AQ1121TVP02 | 52 | Coal Storage Pile | Central Heating & Power Plant | N/A | N/A | unknown
Table notes:
1. EU ID 13 was installed in 2008, but the engine build date is February 17, 1999.

## DU Engines (hidden)
[10 empty] | NOX | NOX |  |  | PM | PM |  | SO2 | SO2
ID | What | Where | Size | HP | YEAR | Hours/Year for PTE | Subpart IIII? | NOX+NMHC |  | lb/hr | TPY | PM |  | lb/hr | TPY | SO2 | lb/hr | TPY
[8 empty] | g/hp-hr, unless noted |  |  |  | g/hp-hr, unless noted |  |  |  | g/hp-hr, unless noted
30 | Emergency Pump Engine | Building 3403 | 75 | hp | 1952 | 500 | NO
31 | Emergency Pump Engine | Building 3724 | 75 | hp | 1952 | 500 | NO
32 | Emergency Pump Engine | Building 4162 | 75 | hp | 1955 | 500 | NO
20 | Emergency Generator Engine | Building 3028 | 35 | hp | 1976 | 500 | NO
29 | Emergency Pump Engine | Building 1056 | 75 | hp | 1988 | 500 | NO
9 | Emergency Generator Engine | Building 1032 | 353 | hp | 1988 | 500 | NO
22 | Emergency Generator Engine | Building 3565 | 35 | hp | 1989 | 500 | NO
24 | Emergency Generator Engine | Building 3703 | 50 | hp | 1993 | 500 | NO
33 | Emergency Pump Engine | Building 1002 | 75 | hp | 1994 | 500 | NO
34 | Emergency Pump Engine | Building 3405 | 220 | hp | 1995 | 500 | NO
36 | Emergency Pump Engine | Building 3563 | 220 | hp | 1995 | 500 | NO
21 | Emergency Generator Engine | Building 3407 | 95 | hp | 2001 | 500 | NO
12 | Emergency Generator Engine | Building 1193 | 82 | hp | 2002 | 500 | NO
26 | Emergency Generator Engine | Building 1620 | 68 | hp | 2003 | 500 | NO
23 | Emergency Generator Engine | Building 3587 | 155 | hp | 2003 | 500 | NO
16 | Emergency Generator Engine | Building 2117 | 212 | hp | 2005 | 500 | NO
18 | Emergency Generator Engine | Building 2296 | 212 | hp | 2005 | 500 | NO
15 | Emergency Generator Engine | Building 2117 | 1059 | hp | 2005 | 500 | NO
19 | Emergency Generator Engine | Building 3004 | 71 | hp | 2007 | 500 | y | 7.5 | g/KW-hr |  |  | 0.4 | g/KW-hr
17 | Emergency Generator Engine | Building 2088 | 176 | hp | 2007 | 500 | y | 4 | g/KW-hr |  |  | 0.2 | g/KW-hr
14 | Emergency Generator Engine | Building 1563 | 320 | hp | 2008 | 500 | y | 4 | g/KW-hr |  |  | 0.2 | g/KW-hr
13 | Emergency Generator Engine | Building 1555 | 587 | hp | 2008 | 500 | y | 4 | g/KW-hr |  |  | 0.2 | g/KW-hr
35 | Emergency Pump Engine | Building 4023 | 55 | hp | 2009 | 500 | y | 7.8 | g/hp-hr |  |  | 0.6 | g/hp-hr
8 | Black Start Generator Engine | Central Heating & Power Plant | 2937 | hp | 2009 | 500 | y | 6.4 | g/KW-hr |  |  | 0.2 | g/KW-hr
27 | Emergency Generator Engine | Building 1054 | 274 | hp | 2010 | 500 | y | 4 | g/KW-hr |  |  | 0.2 | g/KW-hr
28 | Emergency Generator Engine | Building 4390 | 274 | hp | 2010 | 500 | y | 4 | g/KW-hr |  |  | 0.2 | g/KW-hr
10 | Emergency Generator Engine | Building 1060 | 762 | hp | 2010 | 500 | y | 6.4 | g/KW-hr |  |  | 0.2 | g/KW-hr
11 | Emergency Generator Engine | Building 1060 | 762 | hp | 2010 | 500 | y | 6.4 | g/KW-hr |  |  | 0.2 | g/KW-hr
25 | Emergency Generator Engine | Building 5108 | 18 | hp | 2011 | 500 | y | 7.5 | g/KW-hr |  |  | 0.8 | g/KW-hr
Fire Pumps and Emergency engines not otherwise limited in the Title V permit are assumed to have potential to emit based on 500 hours/year per EPA Memo
Note on I4: Deanne Hughes: use the values highlighted in Table D.3-5 for these - in lb/hr-hr units