## 5-1 Available-SO2
Table 5-1. Summary of Available SO2 Emission Control Technology
Emission Unit |  | Available Emission Control Technology
1, 2 | Simple Cycle Gas Turbine | ULSD
Low Sulfur Fuel
No. 1 HSD
Good Combustion Practices
5, 6 | Combined Cycle Gas Turbine | ULSD
LSR/Naphtha
Limited Operation
Good Combustion Practices
7 | Emergency Generator Engine | ULSD
Low Sulfur Fuel
Limited Operation
Good Combustion Practices
11, 12 | Propane-Fired Boiler | Low Sulfur Fuel
Good Combustion Practices

## 5-2 Feasible-SO2
Table 5-2. Summary of Technically Feasible SO2 Emission Control Technology
Emission Unit |  | Technically Feasible Control Technology
1, 2 | Simple Cycle Gas Turbine | ULSD
Low Sulfur Fuel
No. 1 HSD
Good Combustion Practices
5, 6 | Combined Cycle Gas Turbine | ULSD
Good Combustion Practices and LSR/Naphtha
7 | Emergency Generator Engine | ULSD
Low Sulfur Fuel
Limited Operation
Good Combustion Practices
11, 12 | Propane-Fired Boiler | Low Sulfur Fuel
Good Combustion Practices

## 5-3 Ranking-SO2
Table 5-3. Ranking of Technically Feasible SO2 Emission Control Technology
Emission Unit |  | Emission Control Technology | Control Efficiency (pct.) | SO2 Emissions (tpy) | SO2 Emissions Reduction (tpy)
1 | Simple Cycle Turbine | ULSD (0.0015 wt. pct. S) | 99.7 | 4.4592 | 1481.9408
|  | Low Sulfur Fuel (0.05 wt. pct. S) | 90 | 148.64 | 1337.76
|  | No. 1 HSD (0.100 wt. pct. S) | 80 | 297.28 | 1189.12
|  | Good Combustion Practices (0.50 wt. pct. S) (existing) | 0 | 1486.4 | 0
2 | Simple Cycle Turbine | Limited Operation + ULSD (0.0015 wt. pct. S) | 99.7 | 4.0683 | 1352.0317
|  | Limited Operation + Low Sulfur Fuel (0.05 wt. pct. S) | 90 | 135.61 | 1220.49
|  | Limited Operations + No. 1 HSD (0.100 wt. pct. S) | 80 | 271.22 | 1084.88
|  | Good Combustion Practices (0.50 wt. pct. S) (existing) | 0 | 1356.1 | 0
5, 6 | Combined Cycle Gas Turbines (per turbine) | ULSD (0.0015 wt. pct. S) | 70 | 3.03 | 7.07
|  | LSR/Naphtha (0.0050 wt. pct. S) + Good Combustion Practices (existing) | 0 | 10.1 | 0
7 | Emergency Generator Engine | ULSD (0.0015 wt. pct. S) + Limited Operation | 98.5 | 0.00015 | 0.00985
|  | Low Sulfur Fuel (0.05 wt. pct. S) + Limited Operation | 50 | 0.005 | 0.005
|  | Limited Operation (0.1 wt. pct. S) (existing) | 0 | 0.01 | 0
11, 12 | Propane-Fired Boiler | Low Sulfur Fuel (existing) | 0 | 0.0002 | 0

## 5-4 EU ID 1 ULSD CE
Table 5-4. Annualized Costs for ULSD on
the Diesel-fired Simple Cycle Gas Turbine (EU ID 1)
Shaded cells indicate user inputs
Project: |  | GVEA North Pole - PM2.5 BACT Analysis (EU ID 1 - GE Frame 7 CT) | [5 empty] | Prepared By:
Checked By:
Rev:
Annualized Costs | [9 empty] | Actuals
DIRECT ANNUAL COSTS |  |  | QTY | UNIT |  | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL | 833 | hours
(1) | Operating & Maintenance Costs |  |  | % |  |  | 0 |  | 0 | 4305969.2308 | gallons
(2) | Repair & Replacement Costs |  |  | % |  |  | 0 |  | 0
(3) | Maintenance Materials |  |  | LOT |  | excluded in this estimate
(4) | Utilities
| (a) | ULSD Costs: | 45282461.54 | GAL | 0.424 | 19199763.693 |  |  | 19199763.693 | 1825730.9538
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 19199763.693 | 1825730.9538
INDIRECT ANNUAL COSTS
(5) | Overhead |  |  | % |  | excluded in this estimate | 0 |  | 0
(6) | Administrative Charges, Property Taxes, Insurance |  |  | % of capital |  |  | 0 |  | 0
| Capital Recovery Factor [see inputs below] |  | 0.094393
(7) | Capital Recovery | [6 empty] | CRF * TCI = | 0
Total Indirect Annual Costs (TIAC) (refer to Table 5-10) | [7 empty] | TIAC = | 1461565.9588 | 1011206.6864
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 20661329.6518 | 2836937.6402
Cost Effectiveness Summary
TOTAL TONS SO2 AVOIDED PER YEAR | [7 empty] | = | 1481.9408 | 111.1198
COST EFFECTIVENESS ($ PER TON AVOIDED BASED ON PTE) | [7 empty] | (TAC)/(TPY) = | 13942.0749
COST EFFECTIVENESS ($ PER TON AVOIDED BASED ON ACTUAL HISTORIC RUN TIMES, AVOIDING 111 TONS PER YEAR)1 | [7 empty] | (TAC)/(TPY) = | 25530.4326
COST EFFECTIVENESS ($ PER TON PM AVOIDED BASED ON 6 TONS SO2 AVOIDED = 1 TON PM AVOIDED)2 | [7 empty] | (TAC)/(TPY) = | 153182.5958
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 20 | years
1 | Annual average run hours for EU 1 from 2009-2016 is 833 hours, and the peak in the last four years has been 587 hours. 833 hours equates to 4,305,969 gallons of fuel, a TDAC of $1,791,283, and a TAC of $3,208,769. The capital cost of bulk fuel storage would be less and the TIAC for actuals is shown in Table 5-10. 4,305,969 gallons of .381 wt pct. S replaced with .0015 wt pct. = 111 tons avoided. Monthly testing of No. 2 HSD for 2017 showed 0.381 wt. pct. S. average
2 | Alaska Department of Environmental Conservation, Amendments to State Air Quality Control Plan Vol. III: Appendix III.D.5.7, page 52. In reference to fuel oil emissions, "Ambient sampling and modeling in FNSB indicates that reduction of six tons of SOX emissions result in the same reduction in ambient PM2.5 concentration as the reduction of one ton of directly emitted PM2.5".
Note on E13: Author: Based on unlimited operation. 672 MMBtu/hr @ 8760 hrs/yr and HHV of 0.13 MMBtu/gallon.
Note on G13: Author: Difference in cost for delivery of ULSD compared to #2 fuel oil based on data provided by GVEA. Updated with actuals from January 2017 through October 2018.

## 5-4a EU ID 1 No 1 CE
Table 5-4a. Annualized Costs for No. 1 HSD on
the Diesel-fired Simple Cycle Gas Turbine (EU ID 1)
Shaded cells indicate user inputs
Project: |  | GVEA North Pole - PM2.5 BACT Analysis (EU ID 1 - GE Frame 7 CT) | [5 empty] | Prepared By:
Checked By:
Rev:
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT |  | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating & Maintenance Costs |  |  | % |  |  | 0 |  | 0
(2) | Repair & Replacement Costs |  |  | % |  |  | 0 |  | 0
(3) | Maintenance Materials |  |  | LOT |  | excluded in this estimate
(4) | Utilities |  |  |  | 10% | Estimated time running No. 1
| (a) | ULSD Costs: | 45282461.54 | GAL | 0.05 | 226412.3077 |  |  | 226412.3077
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 226412.3077
INDIRECT ANNUAL COSTS
(5) | Overhead |  |  | % |  | excluded in this estimate | 0 |  | 0
(6) | Administrative Charges, Property Taxes, Insurance |  |  | % of capital |  |  | 0 |  | 0
| Capital Recovery Factor [see inputs below] |  | 0.094393
(7) | Capital Recovery | [6 empty] | CRF * TCI = | 0
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 0
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 226412.3077
Cost Effectiveness Summary
TOTAL TONS SO2 AVOIDED PER YEAR | [7 empty] | = | 118.912
COST EFFECTIVENESS ($ PER TON AVOIDED BASED ON PTE) | [7 empty] | (TAC)/(TPY) = | 1904.0325
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 20 | years
1 | Assuming PTE and running No. 1 HSD 10% of the days. Running No. 1 on curtailment days.
Note on E13: Author: Based on unlimited operation. 672 MMBtu/hr @ 8760 hrs/yr and HHV of 0.13 MMBtu/gallon.
Note on G13: Author: Difference in projected price increase for #1 fuel oil

## 5-5 EU ID 2 ULSD CE
Table 5-5. Annualized Costs for ULSD on
the Diesel-fired Simple Cycle Gas Turbine (EU ID 2)
Shaded cells indicate user inputs
Project: |  | GVEA North Pole - PM2.5 BACT Analysis (EU ID 2 - GE Frame 7 CT) | [5 empty] | Prepared By:
Checked By:
Rev:
Annualized Costs | [9 empty] | Actuals
DIRECT ANNUAL COSTS |  |  | QTY | UNIT |  | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL | 2472 | hours
(1) | Operating & Maintenance Costs |  |  | % |  |  | 0 |  | 0 | 12778338.4615 | gallons
(2) | Repair & Replacement Costs |  |  | % |  |  | 0 |  | 0
(3) | Maintenance Materials |  |  | LOT |  | excluded in this estimate
(4) | Utilities
| (a) | ULSD Costs: | 41312492.31 | GAL | 0.424 | 17516496.7394 |  |  | 17516496.7394 | 5418015.5077
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 17516496.7394 | 5418015.5077
INDIRECT ANNUAL COSTS
(5) | Overhead |  |  | % |  | excluded in this estimate | 0 |  | 0
(6) | Administrative Charges, Property Taxes, Insurance |  |  | % of capital |  |  | 0 |  | 0
| Capital Recovery Factor [see inputs below] |  | 0.094393
(7) | Capital Recovery | [6 empty] | CRF * TCI = | 0
Total Indirect Annual Costs (TIAC) (refer to Table 5-10) | [7 empty] | TIAC = | 1461565.9588 | 1011206.6864
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 18978062.6983 | 6429222.1941
Cost Effectiveness Summary
TOTAL TONS SO2 AVOIDED PER YEAR | [7 empty] | = | 1352.0317 | 329.7578
COST EFFECTIVENESS ($ PER TON AVOIDED BASED ON PTE) | [7 empty] | (TAC)/(TPY) = | 14036.6995
COST EFFECTIVENESS ($ PER TON AVOIDED BASED ON ACTUALS, AVOIDING 330 TONS PER YEAR)1 | [7 empty] | (TAC)/(TPY) = | 19496.8008
COST EFFECTIVENESS ($ PER TON PM AVOIDED BASED ON 6 TONS SO2 AVOIDED = EQUIVALENT TO 1 TON PM AVOIDED)2 | [7 empty] | (TAC)/(TPY) = | 116980.805
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 20 | years
1 | Annual average run hours for EU 2 from 2009-2016 is 2472 hours, and the peak in the last four years has been 2873 hours. 2472 hours equates to 12,778,338 gallons of fuel, a TDAC of $5,315,789 and a TAC of $6,730,274. The capital cost of bulk fuel storage would be less and the TIAC for actuals is shown in Table 5-10. 12,778,338 gallons of .381 wt pct. S replaced with .0015 wt pct. = 330tons avoided. Monthly testing of No. 2 HSD for 2017 showed 0.381 wt. pct. S. average
2 | Alaska Department of Environmental Conservation, Amendments to State Air Quality Control Plan Vol. III: Appendix III.D.5.7, page 52. In reference to fuel oil emissions, "Ambient sampling and modeling in FNSB indicates that reduction of six tons of SOX emissions result in the same reduction in ambient PM2.5 concentration as the reduction of one ton of directly emitted PM2.5".
Note on E13: Author: Based on limited operations. 672 MMBtu/hr @ 7992 hrs/yr and HHV of 0.13 MMBtu/gal
Note on G13: Author: Difference in cost for delivery of ULSD compared to #2 fuel oil based on data provided by GVEA. Updated with actuals from January 2017 through October 2018.

## 5-5a EU ID 2 No 1 CE
Table 5-5a. Annualized Costs for No. 1 HSD on
the Diesel-fired Simple Cycle Gas Turbine (EU ID 2)
Shaded cells indicate user inputs
Project: |  | GVEA North Pole - PM2.5 BACT Analysis (EU ID 2 - GE Frame 7 CT) | [5 empty] | Prepared By:
Checked By:
Rev:
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT |  | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating & Maintenance Costs |  |  | % |  |  | 0 |  | 0
(2) | Repair & Replacement Costs |  |  | % |  |  | 0 |  | 0
(3) | Maintenance Materials |  |  | LOT |  | excluded in this estimate
(4) | Utilities |  |  |  | 10% | Estimated time running No. 1
| (a) | No 1 Costs: | 41312492.31 | GAL | 0.05 | 206562.4616 |  |  | 206562.4616
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 206562.4616
INDIRECT ANNUAL COSTS
(5) | Overhead |  |  | % |  | excluded in this estimate | 0 |  | 0
(6) | Administrative Charges, Property Taxes, Insurance |  |  | % of capital |  |  | 0 |  | 0
| Capital Recovery Factor [see inputs below] |  | 0.094393
(7) | Capital Recovery | [6 empty] | CRF * TCI = | 0
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 0
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 206562.4616
Cost Effectiveness Summary
TOTAL TONS SO2 AVOIDED PER YEAR 1 | [7 empty] | = | 108.488
COST EFFECTIVENESS ($ PER TON AVOIDED BASED ON PTE) | [7 empty] | (TAC)/(TPY) = | 1904.0121
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 20 | years
1 | Assuming PTE and running No. 1 HSD 10% of the days. Running No. 1 on curtailment days.
Note on E13: Author: Based on limited operations. 672 MMBtu/hr @ 7992 hrs/yr and HHV of 0.13 MMBtu/gal
Note on G13: Author: Difference in projected price increase for #1 fuel oil

## 5-6 EU ID 5&6 ULSD CE
Table 5-6. Annualized Costs for ULSD on
the Diesel-fired Combined Cycle Gas Turbines (EU IDs 5 and 6)
Shaded cells indicate user inputs
Project: |  | GVEA North Pole - PM2.5 BACT Analysis (EU IDs 5 and 6 - GE LM6000PC CT) | [5 empty] | Prepared By:
Checked By:
Rev:
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT |  | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating & Maintenance Costs |  |  | % |  |  | 0 |  | 0
(2) | Repair & Replacement Costs |  |  | % |  |  | 0 |  | 0
(3) | Maintenance Materials |  |  | LOT |  | excluded in this estimate
(4) | Utilities
| (a) | ULSD Costs: | 30660000 | GAL | 1.117 | 34247220 |  |  | 34247220
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 34247220
INDIRECT ANNUAL COSTS
(5) | Overhead |  |  | % |  | excluded in this estimate | 0 |  | 0
(6) | Administrative Charges, Property Taxes, Insurance |  |  | % of capital |  |  | 0 |  | 0
| Capital Recovery Factor [see inputs below] |  | 0.094393
(7) | Capital Recovery | [6 empty] | CRF * TCI = | 0
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 0
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 34247220
Cost Effectiveness Summary
TOTAL TONS SO2 AVOIDED PER YEAR | [7 empty] | = | 7.07
COST EFFECTIVENESS ($ PER TON AVOIDED) | [7 empty] | (TAC)/(TPY) = | 4844019.802
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 20 | years
Note on E14: Author: Based on HHV of 0.13 MMBtu/gal and maximum allowed operations of 455 MMBtu/hr for 8,760 hr/yr.
Note on G14: Author: Difference in cost for delivery of ULSD compared to LSR based on data provided by GVEA.

## 5-7 EU ID 7 ULSD CE
Table 5-7. Annualized Costs for ULSD on
the Diesel-fired Emergency Generator Engine (EU ID 7)
Shaded cells indicate user inputs
Project: |  | GVEA North Pole - PM2.5 BACT Analysis (EU ID 7 - Generac Gen Set Engine) | [5 empty] | Prepared By:
Checked By:
Rev:
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT |  | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating & Maintenance Costs |  |  | % |  |  | 0 |  | 0
(2) | Repair & Replacement Costs |  |  | % |  |  | 0 |  | 0
(3) | Maintenance Materials |  |  | LOT |  | excluded in this estimate
(4) | Utilities
| (a) | ULSD Costs: | 1664 | GAL | 0.2668 | 443.9552 |  |  | 443.9552
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 443.9552
INDIRECT ANNUAL COSTS
(5) | Overhead |  |  | % |  | excluded in this estimate | 0 |  | 0
(6) | Administrative Charges, Property Taxes, Insurance |  |  | % of capital |  |  | 0 |  | 0
| Capital Recovery Factor [see inputs below] |  | 0.094393
(7) | Capital Recovery | [6 empty] | CRF * TCI = | 0
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 0
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 443.9552
Cost Effectiveness Summary
TOTAL TONS SO2 AVOIDED PER YEAR | [7 empty] | = | 0.00985
COST EFFECTIVENESS ($ PER TON AVOIDED) | [7 empty] | (TAC)/(TPY) = | 45071.5939
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 20 | years
Note on E13: Author: Based on engine fuel consumption rate of 32 gals/hr and limited operations of 52 hours/yr.
Note on G13: Author: Difference in cost for delivery of ULSD compared to #2 fuel oil based on data provided by GVEA.

## Table 5-8
Table 5-8. GVEA North Pole Facility - SO2 BACT Cost Effectiveness
Summary1 for Each Emission Unit Based on PTE
Control Technology Option | SO2 Emissions (tpy) | Total Installed Capital ($) | Total Annualized Cost ($/year) | Annual O&M Cost ($/year) | Cost Effectiveness ($/ton SO2 removed)
Simple Cycle Gas Turbine (EU ID 1)
ULSD (0.0015 wt. pct. S) | 4.4592 | 10875319.1489 | 20661329.6518 | 19199763.693 | 13942.0749
No. 1 HSD (0.100 wt. pct. S) | 297.28 | ~ | 226412.3077 | 226412.3077 | 1904.0325
Good Combustion Practices (0.50 wt. pct. S) (existing) | 1486.4 | ~ | ~ | ~ | ~
Simple Cycle Gas Turbine (EU ID 2)
Limited Operation + ULSD (0.0015 wt. pct. S) | 4.0683 | 10875319.1489 | 18978062.6983 | 17516496.7394 | 14036.6995
Limited Operations + No. 1 HSD (0.100 wt. pct. S) | 271.22 | ~ | 206562.4616 | 206562.4616 | 1904.0121
Good Combustion Practices (0.50 wt. pct. S) (existing) | 1356.1 | ~ | ~ | ~ | ~
Combined Cycle Gas Turbines (EU IDs 5 and 6)
ULSD (0.0015 wt. pct. S) | 3.03 | ~ | 34247220 | ~ | 4844019.802
LSR/Naphtha (0.0050 wt. pct. S) + Good Combustion Practices (existing) | 10.1 | ~ | ~ | ~ | ~
Emergency Generator Engine (EU ID 7)
ULSD (0.0015 wt. pct. S) + Limited Operation | 0.00015 | ~ | 443.9552 | ~ | 45071.5939
Limited Operation (0.1 wt. pct. S) (existing) | 0.01 | ~ | ~ | ~ | ~
Propane Fired Boilers (EU IDs 11 and 12)
Low Sulfur Fuel (propane) (existing) | 0 | ~ | ~ | ~ | ~
1 All emission costs are on a per emission unit basis.

## Table - 5-9
Table 5-9. GVEA North Pole Facility - Proposed SO2 BACT and Associated
Emission Rate for Each Emission Unit
ID | Description |  | Description | Emission Rate1
1, 2 | Simple Cycle Gas Turbine | Fuel Oil | Good Combustion Practices (existing) + No. 1 HSD on air quality curtailment days | 500 ppm S in fuel
5, 6 | Combined Cycle Gas Turbine | LSR | LSR/Naphtha (existing) | 50 ppm S in fuel
7 | Emergency Generator Engine | Fuel Oil | Good Combustion Practices (existing) | 500 ppm S in fuel
11, 12 | Boiler | Propane | Low Sulfur Fuel - Propane (existing) | 0.0012 lb/kgal
1 Emissions are on a per emission unit basis.

## 5-10 TCI ULSD EU1-2
Table 5-10. Capital Cost for New ULSD Storage Based on
Maximum Fuel Use and Actual Fuel Use
| North Pole EUs 1 and 2 Maximum Fuel Use | Zehnder EUs 1 and 2 Maximum Fuel Use | North Pole EUs 1 and 2 Actual Fuel Use | Zehnder EUs 1 and 2 Actual Fuel Use
Capital Cost Estimate | 30425000 |  | 21050000
Heat Input, MMBtu/day (combined for each set of combustion turbines) | 32256 | 12864 | 32256 | 12864
Percentage of Heat Input | 71.49% | 28.51% | 71.49% | 28.51%
Capital Cost (apportioned based on heat input ratio) | 21750638.2979 | 8674361.7021 | 15048510.6383 | 6001489.3617
Capital Cost (apportioned per combustion turbine) | 10875319.1489 | 4337180.8511 | 7524255.3191 | 3000744.6809
Capital Recovery (per combustion turbine) | 1026553.1929 | 409399.19 | 710236.4736 | 283249.0698
Administrative Charges, Property Taxes, Insurance (per combustion turbine) | 435012.766 | 173487.234 | 300970.2128 | 120029.7872
Total Annual Indirect Cost (per combustion turbine) | 1461565.9588 | 582886.4241 | 1011206.6864 | 403278.8571
Capital recovery factor | 0.094393
Data Inputs for Capital Recovery Factor:
Annual Interest Rate (EPA OAQPS Control |  | 7 | pct.
Cost Manual)
Project Life (EPA OAQPS Control Cost |  | 20 | years
Manual)
Administrative Charges, Property Taxes |  | 4%
Insurance (percentage of total capital
cost)
Capital cost estimate for 1.27 million gallons of storage capacity.

## DO NOT INCLUDE - Identified-SO2
Table E-1a. Summary of Identified SO2 Control Technology - Liquid Fuel-Fired Simple Cycle Turbines > 25 MW (RBLC 15.190)
Pollutant | Control Technology Used | Number of RBLC Entries (11 Total)
SO2 | Low Sulfur Fuel | 7
| None | 4
| ULSD | 0
Note: Data is based on a RBLC review from January 1, 2005 through September 15, 2015.
Table E-1b. Summary of Identified SO2 Control Technology - Liquid Fuel-Fired Combined Cycle Turbines > 25 MW (RBLC 15.290)
Pollutant | Control Technology Used | Number of RBLC Entries (6 Total)
SO2 | ULSD | 3
| None | 2
| Limited Operation | 2
| Low Sulfur Fuel | 1
Note: Data is based on a RBLC review from January 1, 2005 through September 15, 2015.
Table E-1c. Summary of Identified SO2 Control Technology - Large Diesel Engines > 500 hp (RBLC 17.110)
Pollutant | Control Technology Used | Number of RBLC Entries (35 Total)
SO2 | Low-Sulfur Fuel | 13
| ULSD | 5
| Good Combustion Practices | 5
| Limited Operation | 5
| None | 3
| Federal Standards | 4
Note: Data is based on a RBLC review from January 1, 2005 through September 15, 2015.
Table E-1d. Summary of Identified SO2 Control Technology - Natural Gas-Fired Commercial/Institutional Boilers <100 MMBtu/hr (RBLC 13.310)
Pollutant | Control Technology Used | Number of RBLC Entries (54 Total)
SO2 | Low Sulfur Fuel | 31
| None | 17
| Good Combustion Practices | 7
Note: Data is based on a RBLC review from January 1, 2005 through September 15, 2015.