## Community Readiness
DEC Western Alaska Community Recovery & Readiness
Community | Drinking Water | Sewer/Wastewater | Fuel/Contamination | Solid Waste/Landfill | Honey Bucket | Lead Program/Next Step | Notes - Water/Drinking Water | Notes - SPAR | Notes - Landfills
Bethel | ✅ Operating | ✅ Functioning | ✅ None Identified | ✅ Stable | N/A | Regional hub
Chefornak | ✅ BWN lifted 10/22; system functional | ✅ Functioning - Additional repairs still needed | ⚠️ Limited access | ⚠️ Wet conditions | ✅ Functional | RMW oversight, DW | Update 10/30: DEC engineers inspected the water treatment plant on October 26 and found no storm-related damage. A total coliform sample collected October 14 was negative, and a VOC sample collected October 26 showed non-detect results for all VOCs. The Drinking Water Program Manager spoke with Chefornak City Administrator Leticia to share the results of VOC, lead, and total coliform testing. The water has been confirmed safe for all potable uses. Leticia will notify residents via text and has the program manager’s direct line for any questions. YKHC RMW Sanderson traveled to assess the sewer line in Chefornak. He found about 500 feet of sewer main that is off its supports and turned 90 degrees from where it should be. YKHC RMWs are formulating a plan to address this. This will be a major effort and will require equipment to lift the pipe. Update 10/31: The wastewater force main serving the LKSD school and community washeteria was displaced from its supports and shifted from its normal discharge point, but it appears to still function. YKHC RMWs are planning repairs, which will require heavy equipment, with more details expected in the next day or so. | Update 10/31: SPAR and SW staff along with representative from Forestry ops made contact with owners of the community store and tank farm operator. Reported no interruptions to fuel support or leaks from the tank farm were reported. | Update 10/31: The landfill is accessible.
Eek | ✅ System functional | ✅ Functional | ✅ None Identified | ✅ Accessible | ✅ Active | EH DW support |  | Update 11/3: DEC staff including two SPAR responders were in Eek on October 28th. The November 3rd trip has been cancelled after speaking to the Eek City Administrator. They reported there were no displaced heating oil tanks or used oil spills. No evacuations. No problems in this community.
Goodnews Bay | ✅ Operating | ✅ Working | ✅ None Identified | ✅ Stable | ✅ Functional | EH DW support
Golovin | ✅ In compliance | ✅ Functional | ✅ None Identified | ✅ Stable | ✅ Functional | EH monitoring
Hooper Bay | ✅ In compliance | ✅ Functioning | ✅ None Identified | ✅ Accessible | ✅ Functional | EH monitoring
Kipnuk | ⚠️ Boilers and heat loops online; circulation stabilization in progress | ✅ Functioning - Additional repairs still needed | ⚠️ Fuel sheens widespread | ⚠️ Debris throughout site | ⚠️ Needs assessment | SPAR & VSW | Remote Maintenance Workers drained the water plant on October 16 to prevent freezing. The community and school operate on separate systems, with the school maintaining its own source and treatment plant. ANTHC and YKHC staff visited on October 28 to assess if the school system could provide potable water for reconstruction efforts. No post-storm total coliform or VOC samples have been collected yet. Contractors are running the backup generator on a 55-gallon drum while connecting it to the bulk fuel tank. The operator has restarted the boilers and glycol loops with guidance from RMW White. Circulation pumps and heat loops to the raw water line, water storage tank, sewer force main, and school water line have been brought online and will stabilize overnight before thawing lines and restoring full water service. Additional operator support is scheduled for October 30. | Two DEC responders assessed Kipnuk on Wednesday, October 22nd with the USCG. Responders report a lot of miscellaneous tanks and drums that floated during the storm and are now orphaned as debris. Fuel or sheen is observed in almost every puddle under ice. Under the federal disaster declaration USCG will hire Alaska Chadux Network for response to oil spill concerns. Update 10/31: On October 29, Alaska Chadux retrieved and secured additional small storage oil and oil product containers based on previous assessments. The Chadux team built another containment site to secure collected miscellaneous oily and oil product containers for temporary storage over the winter. | Update 11/3: SWP staff visited Kipnuk on November 2. The boardwalk providing access to the landfill is damaged, and as such, 4-wheeler access is not possible. Staff walked to landfill and took drone footage of the facility. The landfill is full of trash, and the two burn units that are inaccessible are not being used. The landfill fence appears to have taken storm damage. Boardwalks and homes have taken significant damage, including clear flooding damage. Waste is currently being place in a pile in a yard near the school. Staff took photos of damaged homes and took drone footage of the village and the tank farm. We anticipate that there will be a need for building/repairing the boardwalk to the landfill and construction of a debris monofill in Kipnuk. Construction will reportedly be complicated by the general wet conditions in the area, so a gravel pad may be necessary. We will continue to work with Kipnuk and contractors to identify and authorize a solution.
Kongiganak | ⚠️ Raw line detached; repairs ongoing | ⚠️ Functional backup | ⚠️ Potential contamination | ⚠️ Limited landfill capacity | ✅ Operational | RMW & SPAR | Update 10/30: RMWs are on site repairing the damaged and partially frozen raw water line. The community has enough water in storage to last through February. RMWs are developing a plan to begin pumping from an alternate raw water source in January. A VOC sample collected October 23 showed non-detect results, and DEC will work with the community to obtain a current coliform sample. Update 10/31: The RMW team moved and fused back together 1800+ feet of pipe. The remaining gap between the two ends of pipe is 850 feet. The main pump being down for service and the back up pump breaking delayed the pump effort or it would have been completed before the storm. | Update 10/30: DEC staff, including two SPAR responders, visited Kongiganak on October 28. Due to travel constraints, the team was on the ground for about two hours. Three unidentified drums or tanks were located, but no visible oil or hazardous material releases were observed. The team also noted that piping from a residential sewage tank had detached from the house. A spill site was inspected along the cross-town fuel transfer line that supplies the teacher housing tank. The line was closed at the time of the incident, and approximately 800 gallons of fuel oil were drained from the section. Repairs were completed the same day. Field readings showed low vapor levels (60 ppb) with frozen ground limiting fuel migration. Minor soil removal and in-place burning were conducted to aid cleanup. Additional remediation is recommended when conditions allow. | Section of boardwalk/bridge to landfill is missing 8 ft of boards. Other minor damages reported along road to landfill and images show single boards missing throughout boardwalk to landfill. No images or assessment of landfill or salvage area.
Kotzebue | ✅ In compliance | ⚠️ Lagoon erosion; pipe displacement | ⚠️ Minor household spills | ✅ Landfill good | N/A | SPAR, City crews | The main findings in Kotzebue are erosion concerns along the bridge on Ted Steven’s Road, the sewage lagoon 3, and along Front Road. Ted Stevens road is 1 of 2 evacuation points out of town and is still closed and was actively under construction. Sewage concerns include interruptions to lift stations 4, 9, and 12. 4 has been returned to service but 9 and 12 are on bypass. There are several sewer lines to residences that have experienced erosion and flood waters have caused pipes to rise out of earthen trenches and be displaced. These have since frozen and burst. | Lift Station 9 junction box was fully submerged in the flood and was damaged. Lift station 12 was also fully submerged and electrical components damaged. New pumps and controls have been ordered and are enroute. Sewage backups in 3 homes are likely due to flushing rags down the system. Kotzebue spent 6 hours on 10/26 clearing a basketball size clump of rags from system. DEC RMW offered assistance with RMWs and they indicated they would call if they needed additional assistance.
Kwigillingok | ✅ In compliance | ⚠️ Lagoon road access washout; haul trailer repairs pending | ⚠️ Priority A fuel response; contractor mobilizing to secure displaced and at-risk tanks, assess damaged fuel dispenser; results pending. | ⚠️ Main landfill inaccessible; unpermitted site washed out | ✅ Functional | VSW, EH, SPAR field teams; contractors deploying 10/29 | RMWs have been repairing and reattaching the raw water supply line, which was displaced by up to 300 feet and tangled with debris and boats. The line is reconnected but has frozen sections preventing full use; once heat trace repairs are complete and glycol is available, thawing will begin to restore drinking water production. The finished water tank currently holds about 40,000 gallons of safe, treated water, and recent VOC results were non-detect. DEC will assist with coliform sampling once the system is operational. YKHC and Norton Sound RMWs will also address sewer line repairs at the school and residential dog houses. The honeybucket lagoon remains functional, and DOT is repairing a nearby washout; haul trailers are awaiting new pumps for final repairs. | DEC identified several displaced and at-risk oil storage tanks in the community. SPAR issued a contract for a contractor to secure tanks and hazardous materials, stabilize at-risk tanks, and provide safe winter storage. The bulk fuel dispenser was damaged and is being assessed for repair. Update 11/1: Kick-off meeting completed with US Ecology for work in Kwig. Detailed discussion on job requirements, materials required beyond contractor owned equipment and general discussion on travel and travel backup plans. Contractor targeting arrival Saturday, November 1st, weather dependent. SPAR PPR staff planning on a minimum of two site visits while contractor is onsite. Update 11/3: DEC and contractors conducted on-site surveys of Kwigilingok’s northwest, mid-town, and southside areas. Inventories of oil tanks, barrels, and other hazardous containers were completed, with GPS locations and photos recorded. Debris piles contain numerous 55-gallon barrels, 300–500 gallon tanks, and household hazardous waste (HHOT), much of which cannot be safely removed without equipment. Severe damage to boardwalks was noted, particularly on the south side. U.S. Ecology crews identified roughly 3,000 gallons of fuel that could be pumped with a generator and proper containers; however, fuel containers have not yet arrived, and equipment support is required before any container recovery from debris piles. DOT-contracted equipment from Doug’s Backhaul is expected to arrive on 11/4, which will enable safe debris removal and hazardous material recovery. Additional coordination included DOT debris removal contractors, tribal staff, and DEC, ensuring hazardous materials are separated from general rubble and following safe handling protocols. DEC recommendations include removing refrigerants from appliances, segregating debris appropriately, and using exclusion fencing to prevent injuries. The tribal administrator requested water sampling results and bottled water for the school, which are being addressed through SEOC channels. | This site is at high risk of erosion. Since waste has not been covered there is a strong chance that flood waters have picked up and carried waste downstream into the community and the ocean.
Marshall | ✅ In compliance | ✅ Functioning | ✅ None Identified | ✅ Accessible | ✅ Functional
Napakiak | ✅ In compliance | ⚠️ Lagoon integrity under review | ⚠️ Used oil spill at two homes | ⚠️ Landfill saturated | ✅ Operating | RMW, EH, SPAR | The community’s drinking water well was overtopped during flooding but has since been shock chlorinated and tested safe. All coliform and VOC results were non-detect, and the system is now operating normally. The Flush, Tank, Haul (FTH) system sustained widespread damage, with many insulated “doghouses” displaced—though all but one were salvageable. Repairs are ongoing and require various fittings due to age differences across the system. The honeybucket lagoon remains intact but will need to be pumped out in the spring once a dewatering pump is available. Update 11/3: Electrical service is still needed to restore power to the doghouses. | Biggest SPAR concern was reported vapor intrusion and fuel spill inside the post office but the building was locked so DEC wasn’t able to assess. SPAR will follow up with the post master. A dozen or so HHOT that have kinked fuel lines or were knocked off their stands. With new snow and ice the team wasn’t able to reassess the sheening observed on October 20th. | SW staff visited community on 10/23/25. Site is accessible, no road damage. Landfill did flood during the storm and ponded water still remaining in site. Landfill operator reported potential leachate seep to DEC (not SW) and it was inspected. Flood waters carried waste north of the site. Homes took on flood water and there is likely large amounts of structural damage. Update 11/3: SWP staff visited Napakiak on November 2. The road to the landfill is in good shape. National Guard personnel were actively mucking out houses and delivering wet insulation and other debris to the landfill. The landfill appears to be in good shape., and response personnel were bringing wet insulation to the landfill for disposal from their work mucking out houses.
Napaskiak | ✅ BWN lifted 10/22; system functional | ⚠️ Localized issues | ⚠️ Minor diesel spill near city office; small household spills | ⚠️ Wet landfill; access limited - regular garbage operations to resume soon | ✅ Collection resuming | SPAR follow-up; EH monitoring | Update 10/30: DEC engineers inspected the water treatment plant on October 22 and confirmed it was unaffected by the storm. The system continues to operate normally. A total coliform sample collected October 16 was negative, and a VOC sample collected during the inspection showed non-detect results. |  | Waste collection has been paused due to the wet conditions in the landfill. SW Staff on site on 10/23/25 and noted that MSW is piling up at the entrance to the site. Waste should move in once ground is harder. Minimal structural damage and the community has been able to pick up the small amount of storm debris which will go into the LF when collection resumes.
Nightmute | ✅ In compliance; BWN for general traditional water sources is still in effect; School is still awaiting VOC results. | ⚠️ Minor leak near teacher housing; functional school system | ⚠️ Fuel contamination in multiple homes | ⚠️ Waste flooded into town; cleanup underway | ✅ Lagoon functional; pit trench not needed | DW Eng., SPAR, VSW field follow-up | The Nightmute Water Treatment Plant building shifted during flooding, causing the well casing to lean slightly, though it remains intact and is producing water normally. Drinking water testing for both the community and school systems showed no coliforms, and a VOC sample from the community well on October 26 was non-detect for all VOCs, confirming the water is safe to drink. The school operator will collect additional VOC samples for analysis. Staff also identified a traditional drinking water source—a stream culvert used by roughly half the village population. This untreated surface water contained coliforms and should be boiled for at least two minutes before consumption. A precautionary Boil Water Notice for traditional sources was issued on October 24, 2025. YKHC RMWs White and Kamuck arrived on October 29, 1925, and repaired the main leak at teacher housing and reinsulated a storm-damaged sewer junction box. One minor leak in an individual teacher housing unit remains to be addressed. | SPAR visited Nightmute on October 21 and documented 16 damaged homes, with at least half needing heating oil tank restoration. Coordination with DOT is underway to re-plumb the tanks, though it is unclear if this has been added to their task scope. On October 25, DMVA reported 15–18 homes uninhabitable due to fuel fumes or contamination. SPAR assessed homes on October 26, noting wet conditions and indoor air quality concerns. Boot cleaning station kits and additional PPE were shipped on October 27 to support safe operations. Reports of fuel odor along the riverbank near the old tank farm and a swale in a residential area indicate further oil spill response and soil cleanup will be needed, especially ahead of spring break-up. | The landfill and lagoon were compromised, and debris is widespread. The National Guard is assisting with cleanup, and the City has authorization to use a monofill at the new Class III site, though access is currently limited to four-wheelers, preventing large debris removal. The regular landfill across the river is also inaccessible, leaving the community without a reliable way to manage household waste. Road and boardwalk repairs continue, and a phased return is underway as infrastructure stabilizes. SW staff visited on 10/30 to coordinate with DOT and contractors to improve access to the monofill for debris removal. Update 11/2: Knik Construction is mobilizing equipment operators on Monday to assist DEC with the construction of a new landfill site and access road.
Nome | ✅ In compliance | ✅ Functioning
Nunam Iqua | ✅ In compliance | ✅ Functioning | ✅ None Identified | ✅ Accessible | ✅ Functional | EH | Update 10/31: The RMW in Nunam Iqua reported that the operator plans to reinstall the summer intake pump on Monday. The four feet of water currently available is sufficient until pumping resumes. The summer pump had been removed for winter preparations, but the ice isn’t thick enough yet to install the winter setup. VOC test results showed non-detect results. | Update 11/1: SPAR visited the community on October 30th to perform an initial assessment. The team observed one home impacted by flooding, some wind damage, and power outages. Drinking water concerns were noted, including high salinity, and the washeteria remains shut down. Most damaged houses appeared to predate the typhoon. The team also inspected the community tank farm, bulk fuel receiving header, and electrical transformer storage area, and observed no damage or oil/hazardous material releases. The barge landing remains intact. The community currently needs drinking water for approximately 213 people. | Update 11/1: SWM staff visited Nunum Iqua and met with Tribal Office staff, including the major. One home was reportedly flooded, plus there was some wind damage to a couple of homes, particularly to porches. Staff visited the landfill and were able to get drone and ground photos. The landfill does not appear to have taken any damage and is accessible.
Nunapitchuk | ✅ In compliance | ✅ Functioning | ✅ None Identified | ✅ Accessible | ✅ Functional | EH/SPAR coordination
Oscarville | ✅ In compliance | ✅ Functioning | ✅ None Identified | ✅ Accessible | ✅ Functional | SPAR closeout 10/24 | Update 10/30: The Oscarville systems are non-public because they serve fewer than 25 people, and the Washeteria is not currently in use. DEC engineers inspected the school’s water system on October 24 and collected samples for coliform and VOC testing. Both coliform samples were negative; VOC results showed non-detect results. The school currently has 19 students, including three evacuees from Kwigillingok. |  | Solid Waste staff visited Oscarville on 10/24/25. A fair amount of trash around community, some trash was reportedly washed out of landfill by flooding.
Quinhagak | ✅ In compliance | ⚠️ Lagoon erosion risk | ⚠️ Fuel line damage; minor | ✅ Landfill ok | N/A | DOT/DEC/VSW coordination | The wastewater system appears to be functioning. There is concern erosion from the storm is approaching the sewage lagoon. An ARUC engineer has assessed the lagoon and erosion. It appears there is no immediate threat to the lagoon from the ARUC report. A plan is emerging through coordination with DOT, ARUC, DEC and the community to use locally sourced material to add reinforcements to the beach to protect the lagoon from further erosion during the 2025/26 winter storm season. Update 10/30: RMWs have been on site conducting repairs to the system’s controls and intake line. Three wells remain operational. The operators have been working to raise the raw water line and reattach it to all sleepers. Five total coliform samples collected October 22 were negative. A VOC sample collected October 24 showed non-detect results. Update 11/3: The community sustained significant electrical and water system damage. Of the three well pumps, one was displaced and two require electrical repairs; ANTHC is coordinating repairs but may need additional assistance. There are ongoing concerns that if the remaining operational pump fails before the others are restored, water service will be disrupted. High water levels around the intake also pose a risk, and the community recommends raising the intake by five feet to prevent future flood damage. The wastewater lagoon has exposed permafrost and will require gravel and reseeding before spring thaw to prevent erosion. The water system foundation continues to settle, raising concerns about long-term stability. |  | Landfill access has not been impacted. The storm caused erosion of landfill entrance, but not listed as a primary concern. This site is only 600 ft W of the ocean and is threatened by erosion. The community could find a new location for a monofill that could be converted into a Class III site.
St. Michaels | ✅ In compliance | ✅ Functioning | ✅ None Identified | ✅ Accessible | ✅ Functional | SPAR closeout 10/24 | General updates for Stebbins and St. Micheal include general wind damages to homes, sheds, smoke houses including roof, wall, windows, and some sheds and smoke houses demolished. Main community concerns consist of listing power lines in both communities.
Stebbins | ✅ In compliance | ✅ Functioning | ✅ None Identified | ✅ Accessible | ✅ Functional | SPAR closeout 10/24 | See St. Michael's for notes
Teller | ✅ In compliance | ✅ Functioning
Toksook Bay | ✅ In compliance | ✅ Functioning | ✅ None Identified | ✅ Accessible | ✅ Functioning | EH DW closeout |  | Update 11/3: Team visited Toksook Bay on Oct 30th. Ground time approximately 1 hour and 45 minutes. No reported fuel tank spills and minor damage to a few individual homes. Three homes in erosion threat. | Update 11/1: SWM staff visited Toksook Bay and visited the landfill. The landfill is accessible and did not appear to have taken any damage from the storm. SWM staff got drone footage and ground photos of the landfill. Staff also met with both the Tribal office staff and City office staff. There is reportedly not a significant amount of debris in the village; however, City office staff reported that there were storm damaged porches and some materials blown off of fish drying rack structures. SWM staff also got drone footage of both the old and new tank farms. No major damage was seen.
Tuntutuliak | ⚠️ Surface source; turbidity high; BWN in effect | ✅ Working | ⚠️ Minor sheen near storage | ⚠️ Access issues | ✅ Collection ongoing | EH & SPAR | Update 10/30: RMWs have confirmed no damage to the washeteria. The well was overtopped during flooding, but a total coliform sample collected October 20 was negative. The community remains under a long-term boil water notice unrelated to the storm. A VOC sample collected October 23 showed non-detect results. |  | Update 11/3: SWP staff visited Tuntutuliak on November 1. No impact to landfill from storm; however, there were 30 homes reportedly flooded. Crews were mucking out flooded homes at time of visit, including removing insulation, and drying out floors in preparation for new insulation. One home is marked for demolition. Took aerial and thermal drone footage of the landfill, tank farm, damaged homes, and school tank farm, as well as ground photography of the landfill and damaged homes.
Tununak | ✅ BWN lifted 10/22; system functional | ⚠️ Wastewater partial | ⚠️ Limited supplies | ⚠️ Capacity limited | ✅ Active | EH DW field crew | DW conducting hydrocarbon testing for ground water system. |  | The Tununak River Bridge (#1385) has lost roughly half of the roadway width for roughly 100 ft extending toward town along the ocean side. DOT has not listed this as a primary concern, but it should be watched since the landfill is only accessible via this bridge.
Most recent updates in RED
This document is a working draft prepared by the Alaska Department of Environmental Conservation (DEC) for situational awareness and coordination purposes. The information contained herein represents the best available data at the time of compilation and is subject to change as field conditions, assessments, and community reports are updated. This spreadsheet should not be interpreted as a final verification of community readiness or infrastructure condition. Data may be incomplete, unverified, or based on preliminary assessments. DEC and partner agencies continue to refine and validate information through ongoing field operations and coordination with local, Tribal, and federal partners. For official updates or confirmed public health and environmental safety information, please refer to communications released directly by DEC or the State Emergency Operations Center (SEOC).