## July 2020 ETT List Web
July 2020 ETT List
Note: Column titled "Est. New ETT Score" is the estimated new score based on the violations that have Returned to Compliance (RTCd) during the Quarter. Please note that this score will likely change on the next quarter's list due to further violations being generated. Comments submitted by Drinking Water Program staff on August 17, 2020.
Program Staff | RMW | Est. New ETT Score | System Information | 10 Point |  | 5 Point | [6 empty] | 1 Point | [12 empty] | General Comments | How to Return to Compliance | Known Hardware Problems | Best Practices Score
|  |  |  | RTCR | SW | RTCR | SW | GWR | Arsenic | DBPs | LCR | Nitrate | RTCR | TCR | SW | GWR | Arsenic | DBPs | LCR | IOC | VOC | SOC | Rads | CCR | PN
VANSANDT | DEC | 32 | AKHIOK / AK2250037 (90 / C) | [8 empty] | 1 | 7 | 1 | 9 |  | 1 | 2 |  | 1 | 1 |  |  |  |  | System began a decline in their routine monitoring and reporting compliance and missed monthly MORs and TCs beginning 07/2019. | Sample for Nitrate, TC, distribution chlorine, Arsenic, IOC, VOCs, and DBPs. Submit monthly MORs with adequate chlorine and turbidity data. | N/A | 32
VANSANDT | DEC | 26 | AKUTAN / AK2260252 (95 / C) | [11 empty] | 20 |  |  | 1 | 1 |  |  |  |  | 2 |  | Last sampled for LT2 in 2017. | Sample for LT2, LCR, DBPs, and submit 2019 CCR report and certification form in 2020. | N/A | 75
STATZ | YKHC | 88 | ALAKANUK WATER SYSTEM / AK2270362 (570 / C) | [8 empty] | 4 |  |  | 23 |  |  | 34 | 2 | 1 | 4 |  |  |  |  | Last sampled for Nitrate in 03/2015, LT2 (E. COLI) in 08/2017 (monthly monitoring), DBPs in 10/2013, TOC in 01/2016, Lead/Copper in 09/2012, IOC in 05/2010, and VOC in 03/2015. System has not submitted adequate number of EP chlorine measurements since 05/2019. | Begin monitoring for the following contaminants: Nitrate, E. coli, HAA5 and TTHM, TOC, Lead/Copper, IOC, and VOC. Also, submit a complete MOR with an adequate number of EP chlorine measurements. | N/A | 35
MORRISON | No RMW | 11 | ALASKA WEST KANEKTOK RIVER CAMP / AK2272003 (44 / NC) | [8 empty] | 2 | [13 empty] | Last sampled for Nitrate in 2017. | Sample for Nitrate when system is active. | System did not open for seasonal operation in 2020 due to COVID-19. | N/A
BJORKMAN | No RMW | 11 | ALPINE INN / AK2244808 (30 / NC) | [8 empty] | 2 | [13 empty] | Last sampled for Nitrate in 2017. | When in operation, sample for Nitrate. | N/A | N/A
MORRISON | YKHC | 26 | ANVIK WATER SYSTEM / AK2280171 (96 / C) | [8 empty] | 2 |  |  |  | 1 |  | 5 | 5 | 1 | [5 empty] | Last sampled for Nitrate in 2017, DBPs in 2010, Lead/Copper in 2016, and IOCs in 2010. System did not sample triggered source after TC+ in 11/2018. | Sample for Nitrate, DBPs, Lead/Copper, IOCs and sample triggered source. | N/A | 45
MORRISON | YKHC | 11 | ATMAUTLUAK WATER SYSTEM / AK2271033 (311 / C) |  |  |  |  | 2 | [17 empty] | System has overdue corrective actions from 2017 sanitary survey inspection. | Address 2017 sanitary survey deficiencies. | N/A | 33
LATIMER | No RMW | 15 | BEAR CREEK RV PARK / AK2240773 (62 / C) | [8 empty] | 1 | 2 |  |  | 1 |  |  | 1 |  |  |  |  | 2 |  | System has not sampled in 2020 and has not had sanitary survey conducted since 2015. | Provide an operational status update and if still in operation. Sample for overdue Nitrate ASAP and have a sanitary survey conducted. | N/A | N/A
MORRISON | No RMW | 16 | BETHEL LONGHOUSE HOTEL / AK2270401 (90 / NC) |  |  |  |  | 1 |  |  |  | 2 | [13 empty] | System has overdue sanitary survey deficiencies from 2016 inspection and last sampled for Nitrate in 2017. | Address deficiencies from most recent sanitary survey and sample for Nitrate in 2020. | N/A | N/A
MORRISON | No RMW | 12 | BETHEL TROOPER HOUSING / AK2272011 (60 / NTNC) | [8 empty] | 2 | [8 empty] | 1 |  |  |  |  | Last sampled for Nitrate in 2017 and missed VOCs in 2018. | Sample for Nitrate and VOCs. | N/A | N/A
VANSANDT | No RMW | 11 | BRISTOL BAY LODGE / AK2261630 (46 / NC) |  |  | 1 | [5 empty] | 1 | [13 empty] | System has not submitted RTCR Seasonal Startup Form in 2019-2020. System failed to send proof of required samples monitored. | If in operation, sample for TC and Nitrate. Submit completed RTCR Seasonal Startup Form. | N/A | N/A
LITTLE | No RMW | 28 | CAMERON ACRES / AK2220473 (35 / C) | [5 empty] | 5 | [16 empty] | System has exceeded the Arsenic MCL since 2017. DEC received engineering submittal on 4/21/2020, to address the Arsenic exceedance using Point-of Use devices. A final response submittal was received on 8/5/2020. | Install treatment to address the Arsenic MCL exceedance. | DEC received final response submittal on 8/5/2020. Construction Approval for the Arsenic treatment system was issued 8/18/2020. | N/A
VANSANDT | BBAHC | 24 | CLARKS POINT WATER SYSTEM / AK2260202 (128 / C) | [8 empty] | 2 |  |  |  |  | 2 |  |  | 1 | 1 | 4 |  | 1 |  | Last sampled for Nitrate in 2017, Arsenic in 2012, VOCs in 2014, SOC last monitoring waiver granted 2014-2016 period. System has not submitted 2019 CCR certification form in 2020. | Sample for overdue regulated contaminants, apply for Initial SOC Monitoring Waiver for 2020-2022 compliance period, and submit 2019 CCR certification form in 2020. | N/A | 35
LATIMER | No RMW | 11 | CROOKED CREEK RV PARK / AK2244256 (136 / NC) | [8 empty] | 1 |  |  |  | 1 | [9 empty] | System has overdue sanitary survey deficiencies from 2014 inspection and last sampled for Nitrate in 2018. | Address deficiencies from 2014 sanitary survey and sample for Nitrate. | N/A | N/A
MORRISON | YKHC | 12 | CROOKED CREEK WATERING POINT / AK2280302 (147 / C) |  |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 4 | [7 empty] | System has overdue sanitary survey deficiencies from 2020 inspection and last sampled TC in 02/2020, and DBPs in 2016. | Address deficiencies from recent sanitary survey, sample for TC monthly and DBPs in 8/2020. | N/A | 35
VANSANDT | No RMW | 14 | D & D RESTAURANT / AK2262660 (25 / NC) | [8 empty] | 2 | 3 | [12 empty] | Last sampled for Nitrate in 2017 and TC in 11/2018. | Sample for Nitrate and monthly TC. | N/A | N/A
VISSCHER | Maniilaq | 60 | DEERING UTILITY SYSTEM / AK2340222 (160 / C) | [6 empty] | 11 | [5 empty] | 1 | [9 empty] | System is exceeding the MCL for TTHM, and have exceeded since 2017. System has not had sanitary survey conducted since 2015. | Upgrade current treatment and schedule a sanitary survey. | Phase I of a project to install a new direct filtration system with coagulation and pressure sand filters was constructed prior to DEC granting Approval to Construct. Construction completion deadline is unknown. Phase II will address corrosion control and DBPs. Work has paused on this project, due to COVID-19. | 45
SHARP | NSHC | 30 | DIOMEDE JOINT UTILITIES / AK2340141 (184 / C) | [5 empty] | 2 |  |  |  | 7 |  | 4 |  | 2 | 5 | [7 empty] | System exceeded the RAA MCL for Arsenic as of 09/2019 and has historically exceeded the Nitrate and Arsenic RAA since 12/2005. System has not sampled for TC or distribution chlorine residual since 07/2019, missed Arsenic monitoring for 4th quarter 2019 and 1st quarter 2020. System missed 2018-2019 annual TTHM/HAA5 samples due to operational issues. | Install treatment to address historic Nitrate and Arsenic MCLs, and submit a TTHM/HAA5 sample 3rd quarter 2020, monthly TC samples, and quarterly Arsenic samples as soon as travel allows. | ANTHC is planning to install treatment plant upgrades to meet SWTR/LT1 (cartridge filters) and Nitrate and Arsenic MCLs (ion exchange). A pilot study plan, that will include Ion exchange technology and RO to help refine design, has not been submitted to DEC. Another project to clean/paint the water storage tank (due to internal corrosion and sediment build-up) will also be conducted in summer 2021. | 30
MORRISON | YKHC | 23 | EMMONAK WATER SYSTEM / AK2270299 (820 / C) |  |  | 1 |  |  |  | 2 | [7 empty] | 2 | 2 | [6 empty] | System has overdue sanitary defects from 2019 Level 2 Assessment. System had TTHM MCL exceedances, and has not been routinely monitoring quarterly. System last sampled for Lead/Copper in 2018 and had an incomplete set. | Address sanitary defects from Level 2 Assessment, sample DBPs quarterly, submit OEL reports, and sample for Lead/Copper in 2021. | N/A | 48
NAKANISHI | No RMW | 12 | FOREST PARK TC / AK2210794 (175 / C) |  |  |  |  | 1 | [12 empty] | 3 |  | 1 |  |  | System has overdue deficiencies from 2019 sanitary survey inspection. Last sampled for VOCs in 2019 and Rads in 2017. | Address deficiencies from recent sanitary survey, sample for VOCs and Rads. Contact DEC engineering staff regarding NOV, and submit a complete Lead/Copper Sample Plan. | N/A | N/A
NAKANISHI | No RMW | 11 | FOUR SEASONS TC / AK2210320 (365 / C) | [5 empty] | 2 | [7 empty] | 1 | [8 empty] | System exceeds Arsenic MCL since 06/2019. | Continue to work with DEC engineering staff to determine an adequate fix for the Arsenic exceedances. | N/A | N/A
LATIMER | No RMW | 17 | GEORGE INLET CANNERY / AK2121501 (129 / NC) |  |  | 1 | [5 empty] | 1 | 1 |  | 5 | [10 empty] | System has remained closed due to COVID-19. | Submit RTCR Seasonal Startup Form prior to operation, and MORs when back in operation. | N/A | N/A
MORRISON | YKHC | 15 | GOODNEWS BAY / AK2270257 (250 / C) | [7 empty] | 2 | [7 empty] | 3 | [6 empty] | Last sampled for Lead/Copper in 2018 and is now on annual schedule. | Sample 10 Lead/Copper samples in 2020. | N/A | 68
STATZ | YKHC | 46 | GRAYLING WATER SYSTEM / AK2280066 (195 / C) |  | 3 | [9 empty] | 15 | [10 empty] | System fails to meet SWTR requirements for turbidity (<0.3 NTU). Last sampled for LT2 (E.coli) in 02/2018. | Submit a complete MOR with 95% of reported turbidity measurements at or below 0.3 NTU and begin LT2 (E. coli) monitoring. | System is on a long-term BWN due to inadequate treatment. Operator has reported broken meters (specifically flow meters) in the treatment plant. | 35
LITTLE | No RMW | 42 | HEALTH QUEST THERAPY INC / AK2226049 (165 / NTNC) | [5 empty] | 8 | [16 empty] | System has exceeded the Arsenic MCL since 2017. DEC received an engineering submittal to address the Arsenic exceedance on 11/1/2019 with intent to install Point of Use devices. In 07/2020, verbal communication reported population may not meet NTNC classification. DEC is awaiting a Public Water System Classification Form submittal to make a classification determination. | Submit Public Water System Classification Form so classification determination can be made. If it is determined the system is a NTNC, install treatment to address the Arsenic MCL exceedance. | N/A | N/A
BJORKMAN | DEC | 32 | HYDABURG / AK2120224 (415 / C) | [6 empty] | 6 | [9 empty] | 1 | [5 empty] | Last sampled for IOCs in 2002 and system is due to sample DBPs in 08/2020. | Sample for IOCs and complete DBP sampling in August 2020. | N/A | 48
VANSANDT | No RMW | 12 | JAVA FLATS/RUSSIAN RIVER ROADHOUSE / AK2250582 (39 / NC) | [9 empty] | 8 | [12 empty] | Last sampled for TC in 08/2019. | Sample for TC. | N/A | N/A
BJORKMAN | DEC | 31 | KAKE MUNICIPAL WATER / AK2130083 (415 / C) | [6 empty] | 6 | [15 empty] | System has been slowly lowering their LRAA for HAA5 but it is not in compliance yet. System is flushing but may need more changes. | Collect HAA5 samples that allow the LRAA to be below the MCL. | N/A | 48
VANSANDT | DEC | 11 | KARLUK WATER SYSTEM / AK2250087 (52 / C) |  |  |  | 1 | [12 empty] | 1 | [5 empty] | System does not currently meet the SWTR due to lack of coagulant in their filtration system. System is improving meeting monitoring and reporting requirements. | Add coagulant to meet SWTR filtration requirements. | Unable to meet SWTR because filtration system lacks coagulant. | 90
VANSANDT | No RMW | 19 | KING SALMON MALL / AK2261397 (27 / NC) | [8 empty] | 2 | 5 | [12 empty] | Last sampled for Nitrate in 2017 and TC in 11/2019. | Sample for Nitrate and monthly TC. | N/A | N/A
BJORKMAN | DEC | 26 | KLAWOCK / AK2120169 (904 / C) | [6 empty] | 5 | [15 empty] | Last two sets of DBP samples were below the MCL. System will be sampling again in 09/2020 and could be in compliance by the end of 2020 if the next two sets are lower. | Collect a set of DBP samples that allow for the MCL to be below the MCL. | N/A | 75
VANSANDT | BBAHC | 11 | KOLIGANEK WATER SYSTEM / AK2260040 (167 / C) |  |  |  |  | 1 | [15 empty] | 1 |  | System has overdue sanitary survey deficiencies from 2014-2017 inspections. | Address deficiencies from 2014 sanitary survey and submit 2019 CCR report and certification form in 2020. | N/A | 34
VISSCHER | No RMW | 99 | KOTZEBUE MUN. WATER SYSTEM / AK2340060 (3234 / C) | [6 empty] | 19 | [15 empty] | System is exceeding the MCL for TTHM and HAA5 and has exceeded HAA5 MCL since 2015 and TTHM MCL since 2nd quarter 2019. | Upgrade current treatment. | Plans for a new micro-nano membrane filtration system received Construction Approval on 4/30/2020. WTP completion date is expected for summer 2021 and will help reduce DBPs. | 79
STATZ | YKHC | 37 | KWIGILLINGOK WASHETERIA / AK2271700 (338 / C) | [8 empty] | 1 | 3 |  | 17 |  |  | 7 |  |  | 1 |  |  |  |  | System fails to submit complete MORs. Last sampled for Nitrate in 10/2018, LT2 (E. coli) monitoring in 07/2017, HAA5 in 10/2018, TTHM in 02/2013, and VOCs in 10/2018. Last sampled for TC in 12/2019 and distribution chlorine residual monitoring has not been completed since 12/2019. | Submit a complete MOR and begin monitoring for the following contaminants: Nitrate, E. coli, HAA5 and TTHM, VOCs and TC. Distribution chlorine residual must be monitored for at the same time and place monthly TC. | System is on BWN due to line freeze and failure in early 2020. | 38
VANSANDT | No RMW | 15 | L&PSD NEWHALEN SCHOOL / AK2260634 (73 / NTNC) |  |  |  |  | 2 | [17 empty] | System has overdue sanitary survey deficiencies from inspection. | Contact DEC engineering staff on whether to apply for separation distance waiver if warranted, or address corrective action . | N/A | N/A
MORRISON | No RMW | 14 | LKSD QUINHAGAK & TEACHER HSG / AK2270752 (284 / NTNC) | [9 empty] | 10 |  |  |  |  | 1 | 2 | [6 empty] | Last sampled for TC in 02/2019. System did not sample DBPs or Lead/Copper in 2019. | Sample for TC, DBPs, and Lead/Copper. | N/A | N/A
MORRISON | No RMW | 15 | LKSD TUNTUTULIAK ANGAPAK SC / AK2271017 (101 / NTNC) |  |  |  |  | 2 | [17 empty] | System has overdue sanitary survey deficiencies from 2012 and 2017 inspections. | Address deficiencies from 2012 and 2017 sanitary survey inspections. | N/A | N/A
MORRISON | YKHC | 11 | LOWER KALSKAG WATER SYSTEM / AK2270697 (302 / C) |  |  |  |  | 1 | [7 empty] | 1 | [6 empty] | 1 |  |  | System has an overdue deficiencies from 2016 sanitary survey inspection. System is undergoing distribution system transition and will likely wait until after this is finished to perform a sanitary survey. System did not sample 1st quarter 2020 Rads. | Address deficiencies from 2016 sanitary survey inspection, perform sanitary survey once distribution system transition is complete, and sample Rads quarterly from TP002. | System is transitioning old distribution system to new system. | 80
VANSANDT | No RMW | 13 | MANOKOTAK HEIGHTS W/S / AK2262246 (215 / C) | [13 empty] | 1 |  | 2 | 1 | 1 | 4 | 1 |  |  | Last sampled for Arsenic in 2014, VOCs in 2014, cyclic Rads and Gross Alpha in 2006. | Sample for Arsenic, Lead/Copper, IOCs, VOCs, Rads and apply for 2020-2022 Initial SOC Monitoring Waiver. | N/A | 75
VANSANDT | BBAHC | 14 | MANOKOTAK WATER SYSTEM / AK2260090 (293 / C) |  |  |  |  | 1 | [8 empty] | 2 |  |  | 1 | 2 |  | 1 |  |  | Last sampled for Arsenic and VOCs in 2013, and cyclic Rads and Gross Alpha in 2006. System has overdue sanitary survey deficiencies (separation distance, well vent unscreened, no raw source water tap, and lack of proper well sanitary seal) from 2013 and 2017 inspections. | Sample for Arsenic, IOCs, VOCs, Rads. Address 2013 and 2017 sanitary survey deficiencies. | N/A | 75
VISSCHER | Maniilaq | 11 | MCGRATH WATER SYSTEM / AK2280155 (341 / C) | [6 empty] | 2 | [15 empty] | System is exceeding the MCL for TTHM/HAA5 and has been since 4th quarter 2019. | Optimize treatment system to limit DBP formation and increase TOC removal. | DEC conducted a Status Component Inspection in fall 2018 and provided suggestions to reduce DBP formation. In fall 2019, a technical assistance provider was helping optimize coagulant dosing. | 83
LATIMER | No RMW | 141 | MCKENZIE INLET LOGGING CAMP / AK2121522 (45 / NTNC) |  | 14 | [20 empty] | System is not meeting treatment requirements for turbidity. | Develop new source and treatment system in order to address turbidity. | Develop new source and treatment system in order to address turbidity. | N/A
MORRISON | YKHC | 12 | NAPASKIAK WEST WATER SYSTEM / AK2260139 (200 / C) |  |  |  |  | 1 |  |  |  |  | 3 |  |  |  |  | 2 | 1 |  |  |  |  | 1 |  | System has overdue sanitary survey deficiencies from 2019 inspection. Last sampled for TC in 12/2019. Missed sampling for DBPs and Lead/Copper in 2019. | Address deficiencies from 2019 sanitary survey and sample for TC, DBPs, and Lead/Copper. | N/A | 23
MORRISON | YKHC | 97 | NATIVE VILLAGE OF SLEETMUTE / AK2271874 (82 / C) |  | 7 | [7 empty] | 1 |  | 16 |  |  | 3 |  |  | 1 |  |  | 2 |  | System has trouble meeting EP chlorine residual. System last sampled for DBPs in 2017 and VOCs in 2018. Has not completed LT2 sampling, and did not submit CCR certification page for 2018 or 2019. | Submit MOR with EP chlorine readings of 0.2 mg/L or above. Sample for DBPs and VOCs in 2020, complete LT2 sampling, submit CCR certification page by 10/01/2020. Submit 3 satisfactory TC samples and one week of satisfactory EP chlorine and turbidity data in order to be removed from BWN. | System is on BWN due to inadequate treatment. In March 2020, system had submersion pump failure and failed to Chlorinate. | 40
MORRISON | YKHC | 28 | NEWTOK WATER SYSTEM / AK2271431 (435 / C) | [11 empty] | 15 |  |  | 5 |  |  | 3 |  |  | 1 |  | Has not completed LT2 sampling. Last sampled for DBPs in 2014, and is on annual schedule. System did submit CCR certification page in 2019. System missed three quarters of VOC monitoring in 2019 but is now on annual schedule beginning 2020. | Begin LT2 sampling, sample for DBPs and VOCs, and submit CCR certification page on time. | System has been on long-term BWN since 2012 due to inadequate treatment. | 33
STATZ | YKHC | 52 | NIGHTMUTE NEW WATERING POINT / AK2271721 (243 / C) |  |  |  |  | 1 |  |  |  | 3 |  |  |  | 1 | 2 |  | 11 | 2 | 2 | 8 | 1 |  |  | System failed to submit a triggered source sample following a TC+ sample result. Last sampled for Nitrate in 2016, Arsenic in 2003, Lead/Copper in 2007, IOCs in 2003, VOCs in 2003, SOCs in 2003, Rads in 2007. System has three overdue corrective actions from 2019 sanitary survey inspection. | Begin monitoring for the following contaminants: Nitrate, Arsenic, Lead/Copper, IOCs, VOCs, SOCs, Gross Alpha, combined Uranium, and combined Radium. System must submit an Initial SOC Monitoring Waiver in order to be taken off of quarterly SOC monitoring. System must also submit documentation of corrective actions. System may also submit a triggered source sample. | N/A | 25
VANSANDT | DEC | 14 | NONDALTON / AK2260260 (205 / C) | [11 empty] | 11 | [8 empty] | 1 |  | System has not submitted MORs in 2020. | In 2020, submit MORs with turbidity and chlorine data. | N/A | 60
MORRISON | YKHC | 32 | NUNAM IQUA WATER SYSTEM / AK2270207 (213 / C) | [8 empty] | 1 |  |  | 22 |  |  | 1 | [7 empty] | System has trouble submitting timely MORs. System was placed on BWN on 08/26/2019 due to lack of TC sampling. Last sampled for Nitrate in 2019, and has not completed LT2 sampling. | Submit on-time MORs with EP chlorine readings 31 days/month. Sample for Nitrate in 2020, complete LT2 sampling. Submit 3 satisfactory TC samples to remove BWN. | N/A | 68
MORRISON | YKHC | 11 | NUNAPITCHUK WATER SYSTEM / AK2260820 (496 / C) | [8 empty] | 1 | [6 empty] | 1 | [6 empty] | Last sampled for Nitrate in 2019. System did not sample for Lead/Copper in 2019 and is on annual schedule. | Sample Nitrate and Lead/Copper in 2020. | N/A | 65
MORRISON | YKHC | 22 | OSCARVILLE WATERING POINT / AK2270061 (75 / C) | [8 empty] | 1 | 3 |  |  |  | 1 |  | 3 | 1 | 1 |  | 1 | 2 |  | Last sampled for Nitrate in 2005, Arsenic in 2002, TC in 2007, Lead/Copper in 2004, IOCs in 2002, VOCs in 2007, Gross Alpha in 2007, and did not submit CCR in 2007 or 2020. | Install filtration/treatment. Sample for Nitrate, Arsenic, TC, Lead/Copper, IOCs, VOC, Gross Alpha, and submit CCR and certification form. | No WTP to meet GU/SWTR requirements. On BWN. | 23
VANSANDT | No RMW | 52 | PETER PAN SEAFOOD PORT MOLLER / AK2261216 (140 / NC) |  | 3 |  | 1 | [7 empty] | 9 | [10 empty] | System failing to meet SWTR due to current configuration and lack of coagulation. Continues to incur effluent turbidity TT violations for not meeting below 0.3 NTU. | Install filtration system that meets the SWTR. In 2020, submit MORs meeting the turbidity and chlorine parameters, monitor and report for monthly distribution chlorine residual during seasonal operations, and monitor for LT2 samples. | System does not meet SWTR due to lack of coagulant in their direct filtration units. | N/A
MORRISON | YKHC | 12 | PILOT STATION WATER SYSTEM / AK2260163 (580 / C) |  |  |  |  | 1 |  |  |  | 1 | [5 empty] | 1 |  |  | 1 |  |  |  |  | System has open corrective actions from 2017 sanitary survey inspection. Last sampled for Nitrate and DBPs in 2018. Missed VOC sampling between 2017-2019. | Sample Nitrate, VOCs in 2020. Sample DBPs in September 2020. Address 2017 sanitary survey deficiencies. | N/A | 38
MORRISON | YKHC | 111 | PLATINUM CITY WATER SYSTEM / AK2271059 (51 / C) |  |  |  | 1 |  |  |  |  | 5 | 22 |  | 15 |  |  |  | 16 | 1 | 5 | 8 | 1 | 8 |  | System is classified as GWUDI but does not filter or treat. Has been on BWN since 2014. System last sampled TC in 2018, Nitrate in 2014, Arsenic in 2013, VOC in 2012, and has no RTCR Sample Siting Plan. Had Lead/Copper exceedances in 2005 and has accumulated 6M Lead/Copper violations since 2012. | Install filtration/treatment, submit RTCR Sample Siting Plan, and monitor for regulated contaminants. | No WTP to meet GWUDI/SWTR requirements. On BWN. | 37
LITTLE | No RMW | 26 | QUIET CIRCLE APARTMENTS / AK2224476 (90 / C) | [5 empty] | 5 | [16 empty] | System placed on Quarterly Arsenic monitoring in 2016. The 1st quarter 2020 RAA exceeded the MCL with a compliance average of 0.011 mg/L. | Install treatment to address the Arsenic MCL exceedance. | System received approval to connect to the second well, with future plans to incorporate that well, and an Arsenic treatment system. | N/A
VANSANDT | No RMW | 11 | RAINBOW KING LODGE / AK2261606 (55 / NC) |  |  | 1 | [5 empty] | 1 | [13 empty] | System not operating in 2020. Did not submit RTCR Seasonal Startup Form or sample in 2019. Last sampled for Nitrate in 2018. | Next season system operates, sample for Nitrate and TC. Complete RTCR Seasonal Startup Form on time. | N/A | N/A
BJORKMAN | No RMW | 14 | RAZDOLNA ELEMENTARY SCHOOL / AK2244222 (50 / NTNC) | [9 empty] | 8 |  |  |  | 1 |  | 3 | 1 | [5 empty] | Per conversation on 8/4/2020 with PWS confirming they have sample bottles and will get them collected in the next week. | Collect TC, Arsenic, IOCs and Lead/Copper samples. | N/A | N/A
VANSANDT | No RMW | 14 | RENDEZVOUS / AK2250396 (56 / NC) |  |  |  |  | 1 |  |  |  |  | 7 | [12 empty] | System fails to consistently monitor for routine monthly TC since 08/2019. Fails to correct deficiencies from 2017 sanitary survey inspection. | If operational, monitor for monthly TC and annual Nitrate. Address corrective actions from 2017 sanitary survey inspection. | N/A | N/A
VANSANDT | DEC | 31 | SAINT GEORGE WATER SYSTEM / AK2260074 (142 / C) | [8 empty] | 2 | 11 | [5 empty] | 2 |  | 2 |  |  | 2 |  | Last sampled for monthly TC in 04/2019, missed annual Nitrate monitoring in 2018 and 2019, missed 3-year Lead/Copper monitoring from 2007-2018, no VOCs for 2014-2016 period and 2017-2019 period. | In 2020, sample for Nitrate, monthly TC, Lead/Copper, VOCs, and submit timely the 2019 CCR certification form. | N/A | 37
VANSANDT | DEC | 11 | SAINT PAUL WATER SYSTEM / AK2260286 (697 / C) | [9 empty] | 5 |  |  |  |  | 4 | 1 | [6 empty] | Last sampled for TC in 09/2019 and Lead/Copper in 2016. | Sample for TC, Nitrate, and Lead/Copper and coordinate shipment of samples to lab. | N/A | 65
MORRISON | YKHC | 24 | SCAMMON BAY WATER SYSTEM / AK2270184 (484 / C) | [11 empty] | 17 |  |  | 2 | 1 | [6 empty] | System was removed from BWN on 07/10/2020. System has begun LT2 sampling. System missed sampling for Lead/Copper in 2018. | By the 10th of the following month, submit MORs with EP chlorine residual readings 31 days/month. Sample for Lead/Copper. | N/A | 66
MORRISON | YKHC | 19 | SHAGELUK WATER SYSTEM / AK2280040 (60 / C) |  |  | 2 | [9 empty] | 1 |  | 4 |  |  | 1 |  |  |  |  | System has overdue corrective actions from 2017 Level 2 Assessment. Last sampled for DBPs in 2011 and VOCs in 2016. | Address defects from Level 2 Assessment. Sample for VOCs in 2020 and sample DBPs in July 2021. | N/A | 60
GILLESPIE | No RMW | 28 | SNOWSHOE WATER SYSTEM / AK2223315 (180 / C) | [5 empty] | 5 | [9 empty] | 1 | [6 empty] | System exceeds the Arsenic MCL. A leak increased demand in the system, and caused an increase in the use of the high Arsenic source. Historical document review revealed distribution lines extend beyond the subdivision. Awaiting permit from Borough to dig in the Right-of-Way for addressing an identified leak. | Revaluate current process for addressing the Arsenic issue. | Believed to be leaks in the distribution line, causing an increase in the use of the high-Arsenic well. | N/A
BURG | DEC | 24 | TATITLEK WATER SYSTEM / AK2291130 (95 / C) | [6 empty] | 4 | [7 empty] | 2 | [7 empty] | System still exceeding HAA5 MCL. | Reduce quarter LRAA below the MCL of 60 ug/L for HAA5. | Possible shortcut in storage tank causing water stagnation in the tank. Operator periodically overflowing tank in order to reduce stagnation. | 55
VANSANDT | No RMW | 26 | TIKCHIK NARROWS LODGE / AK2261648 (56 / NC) |  | 1 | [9 empty] | 10 | 1 | [9 empty] | System not operating in 2020. Struggles to consistently meet SW turbidity & chlorine requirements. | When in operation, submit MORs that meet the turbidity and chlorine required levels. | N/A | N/A
VANSANDT | No RMW | 14 | TRIDENT SEAFOODS INC. SAND PT / AK2262351 (400 / NTNC) | [6 empty] | 2 | [15 empty] | System continues to exceed quarterly TTHM/HAA5 MCLs requiring an operational evaluation level (OEL) report. | Address TTHM/HAA5 MCL exceedances. Submit OELs when required. Continue to submit monthly MORs with 95% of turbidity readings meeting maximum 0.3 NTU and EP chlorine readings minimum at 0.2 mg/L. | N/A | N/A
MORRISON | YKHC | 15 | TULUKSAK WATER SYSTEM / AK2270223 (373 / C) | [8 empty] | 1 | [5 empty] | 6 | 1 | [6 empty] | Last sampled for Nitrate in 2018, DBPs in 2016 and missed sampling for Lead/Copper in 2019. | Sample for Nitrate and Lead/Copper in 2020. Sample DBPs in June 2021. | N/A | 23
MORRISON | YKHC | 33 | TUNTUTULIAK WASHETERIA AND WATERING PT / AK2271211 (350 / C) |  |  |  |  | 1 | 2 |  | 1 | [5 empty] | 2 |  | 5 | 1 | 1 |  |  |  |  | System has three overdue corrective actions from 2017 sanitary survey inspection. Has MCL violations for Arsenic and has performed one quarter of monitoring. System had a Lead AL exceedance in 2016 and has not monitored since. System did not sample Ph2 IOC or VOCs between 2017-2019. | Address open sanitary survey deficiencies. Sample for Arsenic quarterly. Sample 6-month set of Lead/Copper in 2020. Sample Ph2 Inorganics and VOCs. | Potential problems with greensand filtration and permanganate treatment which led to increased Arsenic values. | 37
GARLAND | NSHC | 16 | UNALAKLEET CITY WATER SUPPLY / AK2340387 (757 / C) |  | 1 | [10 empty] | 1 | [9 empty] | System is currently on track to return to compliance monitoring and reporting violations by 9/10/2020. A sanitary survey is tentatively scheduled for 2020. | Submit turbidity data indicating the water treatment system is able to meet the turbidity limits on a continuous basis and include EP and distribution chlorine residuals. | In July, DEC granted Construction Approval to WTP improvements to help with turbidity spikes during off-hours. Construction is expected to begin this fall. In addition, plans for a groundwater source (not requiring microbial treatment) received funding for Phase II design. Design completion is expected in April 2021. Construction to start Summer 2021. | 87
SHARP | No RMW | 11 | VALLEY WATER COMPANY / AK2310926 (1575 / C) | [7 empty] | 1 |  |  |  |  | 1 | [9 empty] | System continues to exceed the Copper AL. Copper has been exceeded since 12/1994. System contracted with an engineering company to address issues. | Have a sanitary survey conducted. Install approved corrosion control treatment to address high Copper issue and sample for Lead/Copper annually until issue is resolved. | System does not have corrosion control treatment. Authorized engineering firm working to restore the system to a reliable and sustainable condition. | N/A
BJORKMAN | No RMW | 11 | VOLCANO VIEW RV PARK / AK2249303 (100 / NC) | [8 empty] | 2 | [13 empty] | Las sampled Nitrate in 2017. | Collect a Nitrate sample. | N/A | N/A

## Definitions
DW Program Staff Contact Information
Mat-Su = Office located in Wasilla, AK. Covers the Mat-Su area. Staff: Amy Hill (Program Coordinator) 376-1861, Tee Little (EPS) 376‐1860, Darryl Gillespie (EPS) 376-1824, Scott Forgue (Supervising Engineer) 262‐3417
Northern = Office located in Fairbanks, AK. Covers the Northern Alaska PWSs. Staff: Marci Irwin (Program Coordinator) 451-2168, Karen Garland (EPS) 451‐2137, Teslyn Visscher (EPS) 451‐3038, Michael Sharp (EPS) 451-2178, Johnny Mendez (Engineering Supervisor) 451‐2179
Southcentral / ANC= Office located in Anchorage, AK. Covers Anchorage bowl, Bethel/YK Delta, Dillingham area, Aleutian Chain, Pribilof and Kodiak Island area PWSs. Staff: Heather Murray (Program Coordinator) 269-7619, Elizabeth Nakanishi (EPS) 269‐7517, Darryl Stepien (EPS) 269‐7521, Leslie Morrison (EPS) 269-7518, Leah Van Sandt (EPS) 269-7653, Kalah Statz (EPS) 269-7647, Roy Robertson (Engineering Supervisor) 269‐7631. GENERAL ETT QUESTIONS: Jeanine Vance (EPM) 269-2007, Rachel Westbrook (EPS) 269‐7630, Kenna Billups (EPS) 269-8924
Kenai / Southeast = Office located in Soldotna, AK. Covers the Kenai Peninsula and Southeast area. Staff: Jeri Forgue (Program Coordinator) 262-3404, Eric Burg (EPS) 262‐3420, Jamie Bjorkman (EPS) 262‐3423, James Latimer (EPS) 262-3410, Scott Forgue (Engineering Supervisor) 262‐3417
Link to DW Program Directory (contact information) | http://dec.alaska.gov/eh/dw/contact/
Resource Links
Best Practices (BP) Score
The Best Practices (BP) Score is criteria for assessing operations and maintenance capacity of rural water and wastewater utilities. Used for determining eligibility and prioritization for community sanitation projects. STATEMENT FROM BP SCORE WEBSITE: The most effective way to increase a community's chance of receiving project funding is by improving their Best Practice score.
Link to BP Webpage | https://dec.alaska.gov/water/technical-assistance-and-financing/best-practices/
Alaska Community Database Online
The Community Database Online is a portal for information resources about Alaskan Communities and Places of Interest in an interactive format.
Link to Database Online Webpage | https://dcra-cdo-dcced.opendata.arcgis.com/
Alaska Community Photo Library
The Community Photo Library offers a glimpse into Alaska's communities and lifestyle by providing images of places, people, cultural events, public facilities, landscapes, and other dimensions of community life.
Link to Photo Library Webpage | https://www.commerce.alaska.gov/dcra/dcrarepoext/Pages/PhotoLibrary.aspx
Remote Maintenance Worker (RMW) Service Area Abbreviations
BBAHC= Bristol Bay area Health Corporation | Maniilaq= Maniilaq Health Corporation | TCC= Tanana Chiefs Conference
DEC= AK Department of Environmental Conservation | NSHC= Norton Sound Health Corporation | YKHC= Yukon Kuskokwim Health Corporation
No‐RMW= Not served by an RMW Program
Link to RMW Directory | http://dec.alaska.gov/media/18597/rmw-directory-sfy20.pdf
Definitions
AL= Action Level | HAA5= Haloacetic Acids (Stage 1 Rule) | Rads= Radionuclides Rule
ANTHC= Alaska Native Tribal Health Consortium | IFE= Individual Filter Effluent | RMW= Remote Maintenance Worker
BACTI = Total Coliform Sample | IOC= Inorganic Chemicals | RTC= Return to compliance (fall off ETT list)
BWN= Boil Water Notice | LCR= Lead/Copper Rule | RTCR= Revised Total Coliform Rule
CCR= Consumer Confidence Report | LRAA= Locational Running Annual Average (Stage 2) | SOC= Synthetic Organic Chemicals
CFE= Combined Filter Effluent | LT1= Long Term 1 Enhanced Surface Water Treatment Rule | Surface Water (SW)= Surface Water violations Surface Water Treatment Rules (SWTR, LT1, and LT2)
DPB= Disinfection by Products | LT2= Long Term 2 Enhanced Surface Water Treatment Rule
DSRD= Distribution Chlorine Residual | M/R= Monitoring and Reporting (type of violation) | TC= Total Coliform
EHO= Environmental Health Officer | MCL= Maximum Contaminant Level (type of violation) | TOC= Total Organic Carbon
EP= Entry Point | MOR= Monthly operator report | TCR= Total Coliform Rule (Also called Bacti)
EPA= Environmental Protection Agency | NOV= Notice of Violation | TT= Treatment Technique (violation)
EPRD= Entry Point Residual Distribution | OCC= Optimal corrosion control (Pb/Cu Rule) | TTHM= Total Trihalomethanes (Stage 1 Rule)
ETT= Enforcement Targeting Tool | PER= Preliminary Engineering Report | VOC= Volatile Organic Chemicals
FANLs= Facility Analyte Level (refers to SW/Stage 1 monitoring requirements) | PN= Public Notice | VSW= Village Safe Water
GAC= Granular Activated Carbon | PWS= Public Water System | WTP= Water Treatment Plant
GWUDI= Groundwater under the direct influence of surface water | RAA= Running Annual Average