## Dry Sorbent Injection
Large Boiler Dry Sorbent Injection System - Chena Power Plant
Variable | Designation | Units | Value | Calculation
Unit Size (Gross) | A | (MW) | 26.9 | <-- User Input (Conservative assumption based on total heat input of 269 MMBtu/hour)
Retrofit Factor | B |  | 1.5 | <-- User Input (An "average" retrofit has a factor of 1.0. Site-specific considerations provided by Aurora in 12/22/17 BACT Addendum)
Gross Heat Rate | C | (Btu/kWh) | 10000 | <-- User Input
SO2 Rate | D | (lb/MMBtu) | 0.32 | <-- User Input
Type of Coal | E |  | sub-bituminous | <-- User Input
Particulate Capture | F |  | Baghouse | <-- User Input
Milled Trona | G |  | TRUE | Based on in-line milling equipment
Removal Target | H | (%) | 80 | Maximum Removal Targets: Unmilled Trona with an ESP = 65% Milled Trona with an ESP = 80% Unmilled Trona with a Baghouse = 80% Milled Trona with Baghouse = 90%
Heat Input | J | (Btu/hr) | 269000000 | A*C*1000
NSR | K |  | 1.9695 | Unmilled Trona with an ESP = if(H<40,0.0350*H,0.352e^(0.0345*H)) Milled Trona with an ESP = if(H<40,0.0270*H,0.353e^(0.0280*H)) Unmilled Trona with an BGH = if(H<40,0.0215*H,0.295e^(0.0267*H)) Milled Trona with an BGH = if(H<40,0.0160*H,0.208e^(0.0281*H))
Trona Feed Rate | M | (ton/hr) | 0.20363 | (1.2011x10^-06)*K*A*C*D
Sorbent Waste Rate | N | (ton/hr) | 0.13716 | (0.7035-0.00073696*H/K)*M Based on a final reaction product of Na2SO4 and unreacted dry sorbent as Na2CO3.
Fly Ash Waste Rate | P | (ton/hr) | 0.49815 | (A*C)*Ash incoal*(1-Boiler Ash Removal)/(2*HHV) For Bituminous Coal: Ash in Coal = 0.12; Boiler Ash Removal = 0.2, HHV = 11,000 For PRB Coal: Ash in Coal = 0.06; Boiler Ash Removal = 0.2, HHV = 8,400 For Lignite Coal: Ash in Coal = 0.08; Boiler Ash Removal = 0.2, HHV = 7,200 <-- User Input (Usibelli Coal: Ash in Coal = 0.07; Boiler Ash Removal = 0.6; HHV = 7,560)
Aux Power | Q | (%) | 0.1514 | =if Milled Trona M*20/A else M*18/A
Trona Cost | R | ($/ton) | 451 | <-- User Input (based on delivered price paid by Healy)
Waste Disposal Cost | S | ($/ton) | 50
Aux Power Cost | T | ($/kWh) | 0.21 | <-- User Input (http://www.gvea.com/rates/rates)
Operating Labor Rate | U | ($/hr) | 60 | <-- User Input (Labor cost including all benefits)
IPM Model - Updates to Cost and Performance for APC Technologies - Dry Sorbent Injection for SO2 Control Cost Development Methodology, March 2013, prepared by Sargent & Lundy LLC for USEPA. https://www.epa.gov/sites/production/files/2015-07/documents/append5_4.pdf
Capital Cost Calculation (2012 dollars) |  |  |  | Comments
Includes - Equipment, installation, building, foundations, electrical, and a retrofit difficulty factor of 1.5
Base Module (BM) ($) |  | = | 7174443.7853 | Base DSI module includes all equipment from unloading to injection
Unmilled Trona = if(M>25 then (682,000*B*M) else 6,833,000*B*(M^0.284)
Milled Trona = if(M>25 then (750,000*B*M) else 7,516,000*B*(M^0.284)
BM ($/kW) |  | = | 266.7079 | Base module cost per kW
Total Project Cost
A1 = 10% of BM |  | = | 717444.3785 | Engineering and construction management costs (CC Manual)
A2 = 10% of BM |  | = | 717444.3785 | Labor adjustment for 6 x 10 hour shift premium, per diem, etc. (CC Manual)
A3 = 10% of BM |  | = | 717444.3785 | Contractor profit and fees (CC Manual)
CECC ($) - Excludes Owner's Costs = BM + A1 + A2 + A3 |  | = | 9326776.9209 | Capital, engineering, and construction costs subtotal
CECC ($/kW) - Excludes Owner's Costs |  | = | 346.7203 | Capital, engineering, and construction costst subtotal per kW
B1 = 5% of CECC |  | = | 466338.846 | Owner's costs including all "home office" costs (owner's engineering, management, and procurement activities)
TPC ($) - Includes Owners Costs = CECC + B1 |  | = | 9793115.767 | Total project cost without Allowance for Funds Used During Construction (AFUDC)
TPC ($/kW) - Include Owner's Costs |  | = | 364.0563 | Total project cost per kW without AFUDC
B2 = 0% of (CECC + B1) |  | = |  | AFUDC (Zero for less than 1 year engineering and construction cycle)
TPC ($) = CECC + B1 + B2 |  | = | 9793115.767 | Total project cost
TPC ($/kW) |  | = | 364.0563 | Total project cost per kW
Dry Sorbent Injection System - Chena Power Plant
Direct Annual Costs
Fixed Operating and Maintenance (O&M) Cost
FOMO ($/kW yr) = (1 additional operators)*(2080)*U/(A*1000) |  | = | 4.6394 | Fixed O&M additional operating labor costs
FOMM ($/kW yr) = BM*0.01/(B*A*1000) |  | = | 1.7781 | Fixed O&M additional maintenance material and labor costs
FOMA ($/kW yr) = 0.03*(FOMO+0.4*FOMM) |  | = | 0.16052 | Fixed O&M additional administrative labor costs
FOM ($/kW yr) = FOMO + FOMM + FOMA |  | = | 6.578 | Total Fixed O&M costs ($/kW yr)
Variable O&M Cost
VOMR ($/MWh) = M*R/A |  | = | 3.414 | Variable O&M costs for Trona reagent
VOMW ($/MWh) = (N+P)*S/A |  | = | 1.1809 | Variable O&M costs for waste disposal that includes both the sorbent and the fly ash waste not removed prior to the sorbent injection
VOMP ($/MWh) = Q*T*10 |  | = | 0.31793 | Variable O&M costs for additional auxiliary power required (Refer to Aux Power % above)
VOM ($/MWh) = VOMR + VOMW + VOMP |  | = | 4.9128 | Total Variable O&M Costs ($/MW yr)
Indirect Annual Costs
Overhead (60% of total labor and material costs) |  | = | 106168.5484 | CC Manual
Administrative charges (2% of total capital investment) |  | = | 195862.3153 | CC Manual
Property tax (1% of total capital investment) |  | = | 97931.1577 | CC Manual
Insurance (1% of total capital investment) |  | = | 97931.1577 | CC Manual
Capital Recovery Factor (CRF) = [ i (1+i)n ] / [ (1+i)n - 1 ]
i = Interest rate (%) | 7
n = Equipment life (years) | 15
CRF = | 0.10979 | = | 1075231.4703 | CC Manual
TOTAL INDIRECT ANNUAL OPERATING COSTS |  | = | 1573124.6494
TOTAL ANNUALIZED OPERATING COSTS (2012 $) |  | = | 2907742.6639
Composite CE Index for 2012 (cost year of equation) |  | = | 584.6
Composite CE Index for 2016 (cost year of review) |  | = | 536.4
TOTAL ANNUALIZED OPERATING COSTS (2016 $) |  | = | 2668000.6242
TOTAL UNCONTROLLED SO2 EMISSIONS, tons |  | = | 377.0304
SO2 REMOVAL EFFICIENCY, % |  | = | 80
TOTAL SO2 REMOVED, tons |  | = | 301.6243
SO2 COST-EFFECTIVENESS, $/ton removed |  | = | 8845.4426

## Spray Dry Absorber
Large Boiler Spray Dry Absorber - Chena Power Plant
Variable | Designation | Units | Value | Calculation
Unit Size (Gross) | A | (MW) | 26.9 | <-- User Input (Conservative assumption based on total heat input of 269 MMBtu/hour)
Retrofit Factor | B |  | 1.5 | <-- User Input (An "average" retrofit has a factor of 1.0. Site-specific considerations provided by Aurora in 12/22/17 BACT Addendum)
Gross Heat Rate | C | (Btu/kWh) | 10000 | <-- User Input
SO2 Rate | D | (lb/MMBtu) | 0.32 | <-- User Input (SDA FGD Estimation only valid up to 3lb/MMBtu SO2 Rate)
Type of Coal | E |  | sub-bituminous | <-- User Input
Coal Factor | F |  | 1.05 | Bituminous = 1, Sub-Bituminous=1.05, Lignite=1.07
Heat Rate Factor | G |  | 1 | C/10000
Heat Input | H | (Btu/hr) | 269000000 | A*C*1000
Lime Rate | K | (ton/hr) | 0.058683 | (0.6702*(D^2)+13.42*D)*A*G/2000 (Based on 95% SO2 Removal)
Waste Rate | L | (ton/hr) | 0.13535 | (0.8016*(D^2)+31.1917*D)*A*G/2000
Aux Power | M | (%) | 1.3672 | (0.000547*(D^2)+0.00649*D+1.3)*F*G Should be used for model input
Makeup Water Rate | N | (1000 gph) | 1.5621 | (0.04898*(D^2)+0.5925*D+55.11)*A*F*G/1000
Lime Cost | P | ($/ton) | 80 | <-- User Input (https://www3.epa.gov/ttncatc1/dir1/ffdg.pdf)
Waste Disposal Cost | Q | ($/ton) | 30 | <-- User Input (https://www3.epa.gov/ttncatc1/dir1/ffdg.pdf)
Aux Power Cost | R | ($/kWh) | 0.21 | <-- User Input (http://www.gvea.com/rates/rates)
Makeup Water Cost | S | ($/1000 gal) | 7.17 | <-- User Input (http://www.newsminer.com/water-rates/article_11a2ba10-c211-562e-8da9-87dd16a7b104.html)
Operating Labor Rate | T | ($/hr) | 60 | Labor cost including all benefits
IPM Model - Updates to Cost and Performance for APC Technologies - SDA FGD for SO2 Control Cost Development Methodology, March 2013, prepared by Sargent & Lundy LLC for US EPA. https://www.epa.gov/sites/production/files/2015-07/documents/chapter_5_appendix_5-1b_sda_fgd.pdf
Capital Cost Calculation (2012 dollars) |  |  |  | Comments
Includes - Equipment, installation, building, foundations, electrical, and a retrofit difficulty factor of 1.5
BMR ($) = if(A>600 then (A*92,000) else 566,000*(A^0.716))*B*(F*G)^0.6*(D/4)^0.01 |  | = | 9002327.3702 | Base module absorber island cost
BMF ($) = if(A>600 then (A*48,700) else 300,000*(A^0.716))*B*(D*G)^0.2 |  | = | 3783947.8461 | Base module reagent preparation and waste recycle/handling cost
BMB ($) = if(A>600 then (A*129,900) else 799,000*(A^0.716))*B*(F*G)^0.4 |  | = | 12906734.9177 | Base module balance of plan costs inlcuding: ID or booster fans, piping, ductwork, electrical, etc.
BM ($) = BMR + BMF + BMB |  | = | 25693010.1341 | Total base module cost including retrofit factor
BM ($/kW) |  | = | 955.1305 | Base module cost per kW
Total Project Cost
A1 = 10% of BM |  | = | 2569301.0134 | Engineering and construction management costs
A2 = 10% of BM |  | = | 2569301.0134 | Labor adjustment for 6 x 10 hour shift premium, per diem, etc.
A3 = 10% of BM |  | = | 2569301.0134 | Contractor profit and fees
CECC ($) - Excludes Owner's Costs = BM + A1 + A2 + A3 |  | = | 33400913.1743 | Capital, engineering, and construction costs subtotal
CECC ($/kW) - Excludes Owner's Costs = |  | = | 1241.6696 | Capital, engineering, and construction costst subtotal per kW
B1 = 5% of CECC |  | = | 1670045.6587 | Owner's costs including all "home office" costs (owner's engineering, management, and procurement activities)
TPC ($) - Includes Owners Costs = CECC + B1 |  | = | 35070958.833 | Total project cost without Allowance for Funds Used During Construction (AFUDC)
TPC ($/kW) - Include Owner's Costs = |  | = | 1303.7531 | Total project cost per kW without AFUDC
B2 = 10% of (CECC + B1) |  | = | 3507095.8833 | AFUDC (based on a 3 year engineering and construction cycle)
TPC ($) - Includes Owner's Costs and AFUDC = CECC + B1 + B2 |  | = | 38578054.7163 | Total project cost
TPC ($/kW) - Includes Owner's Costs and AFUDC = |  | = | 1434.1284 | Total project cost per kW
Spray Dry Absorber - Chena Power Plant
Direct Annual Costs
Fixed Operating and Maintenance (O&M) Cost
FOMO ($/kW yr) = (4 additional operators)*(2080)*T/(A*1000) |  | = | 37.1152 | Fixed O&M additional operating labor costs
FOMM ($/kW yr) = BM*0.015/(B*A*1000) |  | = | 9.5513 | Fixed O&M additional maintenance material and labor costs
FOMA ($/kW yr) = 0.03*(FOMO+0.4*FOMM) |  | = | 1.2281 | Fixed O&M additional administrative labor costs
FOM ($/kW yr) = FOMO + FOMM + FOMA |  | = | 47.8946 | Total Fixed O&M costs
Variable O&M Cost
VOMR ($/MWh) = K*P/A |  | = | 0.17452 | Variable O&M costs for lime reagent
VOMW ($/MWh) = L*Q/A |  | = | 0.15095 | Variable O&M costs for waste disposal
VOMP ($/MWh) = M*R*10 |  | = | 2.8712 | Variable O&M costs for additional auxiliary power required including additional fan power (Refer to Aux Power % above)
VOMM ($/MWh) = N*S/A |  | = | 0.41636 | Variable O&M costs for makeup water
VOM ($/MWh) = VOMR + VOMW + VOMP + VOMM |  | = | 3.613 | Total Variable O&M Costs
Indirect Annual Costs
Overhead (60% of total labor and material costs) |  | = | 773019.1575 | CC Manual
Administrative charges (2% of total capital investment) |  | = | 771561.0943 | CC Manual
Property tax (1% of total capital investment) |  | = | 385780.5472 | CC Manual
Insurance (1% of total capital investment) |  | = | 385780.5472 | CC Manual
Capital Recovery Factor (CRF) = [ i (1+i)n ] / [ (1+i)n - 1 ]
i = Interest rate (%) | 7
n = Equipment life (years) | 15
CRF = | 0.10979 | = | 4235663.0393 | CC Manual
TOTAL INDIRECT ANNUAL OPERATING COSTS |  | = | 6551804.3855
TOTAL ANNUALIZED OPERATING COSTS (2012 $) |  | = | 8691559.952
Composite CE Index for 2012 (cost year of equation) |  | = | 584.6
Composite CE Index for 2016 (cost year of review) |  | = | 536.4
TOTAL ANNUALIZED OPERATING COSTS (2016 $) |  | = | 7974944.8482
TOTAL UNCONTROLLED SO2 EMISSIONS, tons |  | = | 377.0304
SO2 REMOVAL EFFICIENCY, % |  | = | 90
TOTAL SO2 REMOVED, tons |  | = | 339.3274
SO2 COST-EFFECTIVENESS, $/ton removed |  | = | 23502.2158

## Wet Scrubber
Large Boiler Wet Scrubber - Chena Power Plant
Variable | Designation | Units | Value | Calculation
Unit Size (Gross) | A | (MW) | 26.9 | <-- User Input (Conservative assumption based on a total heat input of 269 MMBtu/hr)
Retrofit Factor | B |  | 1.5 | <-- User Input (An "average" retrofit has a factor of 1.0) Sargent and Lundy has a drop down menu for selection of an additional waste water treatment plant facility, but no capital or operational cost are implemented so it is not reproduced here.
Gross Heat Rate | C | (Btu/kWh) | 10000 | <-- User Input
SO2 Rate | D | (lb/MMBtu) | 0.32 | <-- User Input
Type of Coal | E |  | sub-bituminous | <-- User Input
Coal Factor | F |  | 1.05 | Bituminous = 1, Sub-Bituminous = 1.05, Lignite = 1.07
Heat Rate Factor | G |  | 1 | C/10000
Heat Input | H | (Btu/hr) | 269000000 | A*C*1000
Limestone Rate | K | (ton/hr) | 0.075406 | 17.52*A*D*G/2000
Waste Rate | L | (ton/hr) | 0.13656 | 1.811*K
Aux Power | M | (%) | 1.1586 | (1.05e^(0.155*D))*F*G
Makeup Water Rate | N | (1000 gph) | 2.1245 | (1.674*D+74.68)*A*F*G/1000
Limestone Cost | P | ($/ton) | 20 | <-- User Input (https://www3.epa.gov/ttncatc1/dir1/ffdg.pdf)
Waste Disposal Cost | Q | ($/ton) | 30 | <-- User Input (https://www3.epa.gov/ttncatc1/dir1/ffdg.pdf)
Aux Power Cost | R | ($/kWh) | 0.21 | <-- User Input (http://www.gvea.com/rates/rates)
Makeup Water Cost | S | ($/1000 gal) | 7.17 | <-- User Input (http://www.newsminer.com/water-rates/article_11a2ba10-c211-562e-8da9-87dd16a7b104.html)
Operating Labor Rate | T | ($/hr) | 60 | Labor cost including all benefits
IPM Model - Updates to Cost and Performance for APC Technologies - Wet FGD for SO2 Control Cost Development Methodology, August 2010, prepared by Sargent & Lundy LLC for US EPA. https://www.epa.gov/sites/production/files/2015-07/documents/chapter_5_appendix_5-1a_wet_fgd.pdf
Capital Cost Calculation (2012 dollars) |  |  |  | Comments
Includes - Equipment, installation, building, foundations, electrical, minor physical/chemical waste water treatment, and a retrofit difficulty factor of 1.5
BMR ($) = 550,000*(B)*((F*G)^0.6)*((D/2)^0.02)*(A^0.716) |  | = | 8648734.3973 | Base absorber island cost
BMF ($) = 190,000*(B)*((D*G)^0.3)*(A^0.716) |  | = | 2138417.4317 | Base reagent preparation cost
BMW ($) = 100,000*(B)*((D*G)^0.45)*(A^0.716) |  | = | 948661.7316 | Base waste handling cost
BMB ($) = 1,010,000*(B)*((F*G)^0.4)*(A^0.716) |  | = | 16315146.7671 | Base balance of plan cost including: ID or booster fans, new wet chimney, piping, ductwork, minor waste water treatment, etc…
BMWW ($) = |  | = | 0 | Base wastewater treatment facility, beyond minor physical/chemcial treatment
Base Module (BM) ($) = BMR + BMF + BMW + BMB + BMWW |  | = | 28050960.3277 | Total base cost including retrofit factor
BM ($/kW) |  | = | 1042.7866 | Base cost per kW
Total Project Cost
A1 = 10% of BM |  | = | 2805096.0328 | Engineering and construction management costs (CC Manual)
A2 = 10% of BM |  | = | 2805096.0328 | Labor adjustment for 6 x 10 hour shift premium, per diem, etc. (CC Manual)
A3 = 10% of BM |  | = | 2805096.0328 | Contractor profit and fees (CC Manual)
CECC ($) - Excludes Owner's Costs = BM + A1 + A2 + A3 |  | = | 36466248.4259 | Capital, engineering, and construction costs subtotal
CECC ($/kW) - Excludes Owner's Costs = |  | = | 1355.6226 | Capital, engineering, and construction costst subtotal per kW
B1 = 5% of CECC |  | = | 1823312.4213 | Owner's costs including all "home office" costs (owner's engineering, management, and procurement activities)
TPC ($) - Includes Owners Costs = CECC + B1 |  | = | 38289560.8472 | Total project cost without Allowance for Funds Used During Construction (AFUDC)
TPC ($/kW) - Include Owner's Costs = |  | = | 1423.4037 | Total project cost per kW without AFUDC
B2 = 10% of (CECC + B1) |  | = | 3828956.0847 | AFUDC (based on a 3 year engineering and construction cycle)
TPC ($) - Includes Owner's Costs and AFUDC = CECC + B1 + B2 |  | = | 42118516.932 | Total project cost
TPC ($/kW) - Includes Owner's Costs and AFUDC = |  | = | 1565.7441 | Total project cost per kW
Wet Scrubber - Chena Power Plant
Direct Annual Costs
Fixed O&M Cost
FOMO ($/kW yr) = (6 additional operators)*(2080)*T/(A*1000) |  | = | 27.8364 | Fixed O&M additional operating labor costs
FOMM ($/kW yr) = BM*0.015/(B*A*1000) |  | = | 10.4279 | Fixed O&M additional maintenance material and labor costs
FOMA ($/kW yr) = 0.03*(FOMO+0.4*FOMM) |  | = | 0.96023 | Fixed O&M additional administrative labor costs
FOMWW ($/kW yr) = |  |  | 0 | Fixed O&M costs for wastewater treatment facility
FOM ($/kW yr) = FOMO + FOMM + FOMA + FOMWW |  | = | 39.2245 | Total Fixed O&M costs ($/kW yr)
Variable O&M Cost
VOMR ($/MWh) = K*P/A |  | = | 0.056064 | Variable O&M costs for limestone reagent
VOMW ($/MWh) = L*Q/A |  | = | 0.1523 | Variable O&M costs for waste disposal
VOMP ($/MWh) = M*R*10 |  | = | 2.433 | Variable O&M costs for additional auxiliary power required including additional fan power (Refer to Aux Power % above)
VOMM ($/MWh) = N*S/A |  | = | 0.56626 | Variable O&M costs for makeup water
VOMWW ($/MWh) = |  | = | 0 | Variable O&M costs for wastewater treatment facility
VOM ($/MWh) = VOMR + VOMW + VOMP + VOMM + VOMWW |  | = | 3.2076 | Total Variable O&M Costs ($/MW yr)
Indirect Annual Costs
Overhead (60% of total labor and material costs) |  | = | 633083.8311 | CC Manual
Administrative charges (2% of total capital investment) |  | = | 842370.3386 | CC Manual
Property tax (1% of total capital investment) |  | = | 421185.1693 | CC Manual
Insurance (1% of total capital investment) |  | = | 421185.1693 | CC Manual
Capital Recovery Factor (CRF) = [ i (1+i)n ] / [ (1+i)n - 1 ]
i = Interest rate (%) | 7
n = Equipment life (years) | 15
CRF = | 0.10979 | = | 4624386.7595 | CC Manual
TOTAL INDIRECT ANNUAL OPERATING COSTS |  | = | 6942211.2679
TOTAL ANNUALIZED OPERATING COSTS (2012 $) |  | = | 8753203.8876
Composite CE Index for 2012 (cost year of equation) |  | = | 584.6
Composite CE Index for 2016 (cost year of review) |  | = | 536.4
TOTAL ANNUALIZED OPERATING COSTS (2016 $) |  | = | 8031506.2698
TOTAL UNCONTROLLED SO2 EMISSIONS, tons |  | = | 377.0304
SO2 REMOVAL EFFICIENCY, % |  | = | 99
TOTAL SO2 REMOVED, tons |  | = | 373.2601
SO2 COST-EFFECTIVENESS, $/ton removed |  | = | 21517.1843 | Does not include costs associated with building and maintaining a wastewater treatment facility

## ESRI_MAPINFO_SHEET (hidden)
DO NOT EDIT
For Esri use only