## 15.110 Large Simple Cycle Turbi
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
AK-0085 | GAS TREATMENT PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | NORTH SLOPE BOROUGH | AK | 99734 | USA | LISA HAAS | 907.947.9353 | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - 907.465.5122 - dave.jones2@alaska.gov | AQ1524CPT01 | 4922 | 486210 | None Found | 01/25/2019 &nbsp;ACT | 08/13/2020 &nbsp;ACT | 2020-08-14 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Gas Treatment Plant (GTP) is part of one integrated liquefied natural gas (LNG) project to bring natural gas from Alaskaâ€™s North Slope to international markets in the form of LNG, as well as for in-state deliveries in the form of natural gas. The GTP will take gas from the Prudhoe Bay Unit and the Point Thomson Unit and treat/process the gas, before it is sent 807 miles through a 42-inch diameter pipeline to a liquefaction facility in Nikiski on Alaskaâ€™s Kenai Peninsula for export in foreign commerce. The emissions units at the stationary source will include cogeneration gas-fired turbines with supplemental firing duct burners for gas compression, simple cycle gas-fired turbines for power generation, gas-fired heaters for building and process heat, as well as flares for control of excess gas. In addition, the GTP will include a diesel-fired black start generator, several diesel-fired firewater pumps and emergency generators, and storage tanks for diesel and gasoline fuels. |  | Six (6) Simple Cycle Gas-Turbines (Power Generation) | 15.11 | Natural Gas | 386 | MMBtu/hr | EUs 25 -30 each provide 44 MW of power generation for the facility | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices and clean burning fuel (NG) | 117.1 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Potential CO2e emissions of 197,975 tpy per turbine. The 117.1 lb/MMBtu emission rate is the carbon dioxide equivalent (CO2e) emissions rates for burning natural gas in 40 CFR Part 98: Mandatory Greenhouse Gas Reporting. The total CO2e emissions rate is calculated with the equation CO2(1) + CH4(25) + N2O(298).
AK-0088 | LIQUEFACTION PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | KENAI PENNINSULA BOROUGH | AK | 99635 | USA | LISA HAAS |  | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - Permit Writer - dave.jones2@alaska.gov | AQ1539CPT01 | 4922 | 488999 | Not Found | 01/14/2020 &nbsp;ACT | 07/07/2022 &nbsp;ACT | 2022-08-04 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Liquefaction Plant is planned to encompass 921 acres, including 901 acres onshore for the liquefied natural gas (LNG) Plant as well as 20 acres offshore for the Marine Terminal. The Liquefaction Plant will be the terminus of an approximately 807-mile gas pipeline, allowing natural gas from Alaskaâ€™s North Slope to be shipped to outside markets. The stationary source will consist of structures and equipment associated with processing, storage, and loading of LNG. There will be three liquefaction trains combining to process up to approximately 20 million metric tons per annun of LNG. |  | Six Simle Cycle Gas-Fired Turbines | 15.11 | Natural Gas | 1113 | MMBtu/hr | EUs 1 - 6 are simple cycle gas turbines used for gas compression at LNG facility | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices and burning clean fuels (natural gas) | 117.1 | LB/MMBTU | 3-HOURS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG01 SUSD - Simple-Cycle Combustion Turbine 1 (Startup/Shutdown/ Maintenance/Tuning/Runback) [EQT0019] | 15.11 | Natural Gas | 2201 | MM BTU/hR | Limited to 600 hr/yr | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Facility-wide energy efficiency measures , such as improved combustion measures, and use of pipeline quality natural gas. | 120 | LB/MM BTU | ANNUAL AVERAGE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 50 | KG/GJ | ANNUAL AVERAGE | 0 |  |  | 0 | 0 | N |  | Monitor compliance by maintaining fuel purchase records for permitted fuels in accordance with 40 CFR 60.5525 Subpart TTTT.
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG02 SUSD - Simple-Cycle Combustion Turbine 2 (Startup/Shutdown/ Maintenance/Tuning/Runback) [EQT0020] | 15.11 | Natural Gas | 2201 | MM BTU/hr | limited to 600 hr/yr | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Facility-wide energy efficiency measures , such as improved combustion measures, and use of pipeline quality natural gas. | 120 | LB/MM BTU | ANNUAL AVERAGE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 50 | KG/GJ | ANNUAL AVERAGE | 0 |  |  | 0 | 0 | N |  | Monitor compliance by maintaining fuel purchase records for permitted fuels in accordance with 40 CFR 60.5525 Subpart TTTT.
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG01 NO - Simple-Cycle Combustion Turbine 1 (Normal Operations) [EQT0017] | 15.11 | Natural Gas | 2201 | MM BTU/hr | Normal operations are based on 7000 hrs/yr | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Facility-wide energy efficiency measures , such as improved combustion measures, and use of pipeline quality natural gas. | 50 | KG/GJ | ANNUAL AVERAGE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 120 | LB/MM BTU | ANNUAL AVERAGE | 0 |  |  | 0 | 0 | N |  | Monitor compliance by maintaining fuel purchase records for permitted fuels in accordance with 40 CFR 60.5525 Subpart TTTT.
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG02 NO - Simple-Cycle Combustion Turbine 2 (Normal Operations) [EQT0018] | 15.11 | Natural Gas | 2201 | MM BTU/hr | Normal operations are based on 7000 hours per year | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Facility-wide energy efficiency measures , such as improved combustion measures, and use of pipeline quality natural gas. | 50 | KG/GJ | ANNUAL AVERAGE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 120 | LB/MM BTU | ANNUAL AVERAGE | 0 |  |  | 0 | 0 | N |  | Monitor compliance by maintaining fuel purchase records for permitted fuels in accordance with 40 CFR 60.5525 Subpart TTTT.
LA-0331 | CALCASIEU PASS LNG PROJECT | VENTURE GLOBAL CALCASIEU PASS, LLC | CAMERON | LA | 70631 | USA | GRAHAM MCARTHUR | 202-759-6741 | GMCARTHUR@VGLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Ms. Mei Wu, (225)219-3180 | PDS-LA-805 | 4925 | 221210 | Not Found | 06/25/2018 &nbsp;ACT | 09/21/2018 &nbsp;ACT | 2019-02-14 | 2019-06-19 | A |  | New Liquefied Natural Gas (LNG) production, storage, and export terminal. | Application Received September 2, 2015. | Simple Cycle Combustion Turbines (SCCT1 to SCCT3) | 15.11 | Natural Gas | 927 | MM BTU/h |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Exclusively combust low carbon fuel gas, good combustion practices, good operation and maintenance practices, and insulation | 1426146 | T/YR | ANNUAL TOTAL | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Annual Total for 3 simple cycle turbines. Subject to 40 CFR 60 Subpart KKKK.
LA-0349 | DRIFTWOOD LNG FACILITY | DRIFTWOOD LNG LLC | CALCASIEU | LA | 70663 | USA | CATHY ROURKE | 8329624031 | CATHY.ROURKE@TELLURIANINC.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen | PSD-LA-824 | 4925 | 221210 | Not Found | 10/30/2017 &nbsp;ACT | 07/10/2018 &nbsp;ACT | 2020-04-02 | 2021-08-06 | A |  | Propose a new facility to liquefy natural gas for export |  | Compressor Turbines (20) | 15.11 | natural gas | 540 | mm btu/hr |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Use Low Carbon Fuel, Energy Efficiency Measures, and Good Combustion Practices | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0383 | LAKE CHARLES LNG EXPORT TERMINAL | LAKE CHARLES LNG EXPORT COMPANY, LLC | CALCASIEU PARISH | LA | 70605 | USA | LISA GARCIA | 7039897762 | LISA.GARCIA@ENERGYTRANSFER.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Cathy E. Wilson - 225-219-3585 | PSD-LA-838 | 4925 | 486210 | 110070248334 | 04/30/2020 &nbsp;ACT | 09/03/2020 &nbsp;ACT | 2021-12-20 | 2022-03-04 | A |  | A greenfield facility to liquefy and export natural gas. |  | Turbines (EQT0020 - EQT0031) | 15.11 | Natural gas | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Low carbon fuels Energy efficient designs and operation | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0454 | LBWL-ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions about this permit, please contact the permit engineer, Lauren Magirl, at 517-582-5345, or at MagirlL@michigan.gov. Thank you. | 74-18D | 4911 | 221112 | Not Found | 10/25/2022 &nbsp;ACT | 12/20/2022 &nbsp;ACT | 2022-12-29 | 2023-05-23 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWLâ€™s existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGSC1--A nominally rated 667 MMBTU/H natural gas-fired simple cycle CTG | 15.11 | Natural gas | 667 | MMBTU/H | A nominally rated 667MMBtu/hr, natural gas-fired simple cycle CTG. The CTG will utilize DLNB and good combustion practices. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Low carbon fuel (pipeline quality natural gas), good combustion practices, and energy efficiency measures. | 318404 | T/YR | 12-MO ROLLING TIME PERIOD | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emission limit 1 above = 318,404 tons/yr based on a 12-operating month rolling average as determined at the end of each calendar month. Applies during all operating modes.
*TN-0187 | TENNESSEE VALLEY AUTHORITY - JOHNSONVILLE COMBUSTION TURBINE | TENNESSEE VALLEY AUTHORITY | HUMPHREYS | TN | 37134 | USA | STEVEN TRULL | 731-648-2445 | SGTRULL@TVA.GOV | 4 | TN001 | TENN.DEPT. OF ENVIRONMENT & CONSERVATION, DIV OF AIR POLLUTION CONTROL | LACEY HARDIN | (615) 532-0545 | Lacey.Hardin@tn.gov |  | 979348 | 4911 | 221112 | Not Entered | 09/09/2021 &nbsp;ACT | 08/31/2022 &nbsp;ACT | 2023-03-17 | 2023-03-17 | B |  | Electric Generation Facility |  | Ten Simple Cycle NG Turbines | 15.11 | Natural Gas | 465.8 | MMBtu/hr | 465.8 MMBtu/hr per individual turbine 4658.0 MMBtu/hr total Aeroderivative | Carbon Dioxide Equivalent (CO2e) | Other - none | (Greenhouse Gasses (GHG)) | CO2e | P | Efficient turbine operation and good combustion practices | 120 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0851 | RIO BRAVO PIPELINE FACILITY | RIO GRANDE LNG LLC | CAMERON | TX |  | USA | SHAUN DAVISON |  |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Michael Cheek, P.E., (512) 239-4936, Michael.Cheek@tceq.texas.gov | 140792, PSDTX1498, GHGPSDTX158 | 4922 | 486210 | Not Found | 02/22/2018 &nbsp;ACT | 12/17/2018 &nbsp;ACT | 2019-02-12 | 2019-02-19 | A |  | Natural gas processing and liquefied natural gas (LNG) export terminal |  | Refrigeration Compression Turbines | 15.11 | NATL GAS | 967 | MMBTU/HR | Twelve General Electric Frame 7EA simple cycle combustion turbines to serve as drivers for refrigeration and compression at the site. There are six process trains and there are two turbines per train. One each of the pairs of turbines has a downstream heat exchanger in the exhaust stream. The heat exchanger heats oil in a closed circuit for process uses elsewhere in the natural gas liquefaction system. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices and use of pipeline quality natural gas. | 0 |  |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0900 | ECTOR COUNTY ENERGY CENTER | ECTOR COUNTY ENERGY CENTER LLC | ECTOR | TX |  | USA | RICH DOWNEN | 360-593-2830 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Huy Pham, (512) 239-1358, Huy.Pham@tceq.texas.gov | 110423, PSDTX1366M1 GHGPSD49M1 | 4911 | 221112 | Not Found | 06/23/2020 &nbsp;ACT | 08/17/2020 &nbsp;ACT | 2020-06-25 | 2021-09-10 | C |  | increase the hours of operation for the two simple cycle gas turbines |  | Simple Cycle Turbines | 15.11 | natural gas | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Best management practices and good combustion practices, clean fuel | 1514 | LB/MWHR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0933 | NACERO PENWELL FACILITY | NACERO TX 1 LLC | ECTOR | TX |  | USA | HAL BOUKNIGHT | 864-354-6062 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Cara Hill, (512) 239-5123, Cara.Hill@tceq.texas.gov | 164137 PSDTX1594 GHGPSDTX207 | 2869 | 325110 | NOT FOUND | 09/20/2021 &nbsp;ACT | 11/17/2021 &nbsp;ACT | 2021-10-27 | 2022-03-08 | A |  | Nacero proposes to construct and operate a plant that will convert natural gas to methanol and then convert methanol to a finished gasoline component. |  | TURBINE | 15.11 | NATURAL GAS | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practices and the use of gaseous fuel | 0 |  |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
WV-0028 | WAVERLY POWER PLANT | PLEASANTS ENERGY LLC | PLEASANTS | WV | 26170 | USA | GERALD GATTI | 3046654201 | GERALD.GATTI@DYNEGY.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Mr. Steve Pursley, PE Engineer West Virginia Division of Air Quality 601-57th St., SE Charleston, WV 25304 Phone: (304) 926-0499 x1218 Fax: (304) 926-0478 steve.r.pursley@wv.gov | R14-0034A | 4911 | 221112 | 110063231042 | 11/30/2017 &nbsp;ACT | 03/13/2018 &nbsp;ACT | 2018-05-29 | 2019-02-20 | U | https://dep.wv.gov/daq/Documents/March 2018 Permits and Evals/073-00022_PERM_R14-0034A.pdf | 300 MW Sinple-Cycle Peaking Plant | Modification to existing PSD Permit (R14-0034, RBLC Number WV-0027) to add &lsquo;&lsquo;advanced gas path&lsquo;&lsquo; technology to the turbines that was defined as a &lsquo;&lsquo;change in the method of operation&lsquo;&lsquo; that resulted a major modification to the turbines. | GE 7FA.004 Turbine | 15.11 | Natural Gas | 167.8 | MW | This one entry is for both turbines as they are the same. Each turbine, after this modification, is a nominal 167.8 MW GE Model 7FA.004. Has oil-fire backup. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Use of natural gas & use of GE 7FA.004 | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 1300 | LB/MW-HR | 12 MONTH ROLLING AVERAGE | 0 | 0 | N
AK-0085 | GAS TREATMENT PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | NORTH SLOPE BOROUGH | AK | 99734 | USA | LISA HAAS | 907.947.9353 | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - 907.465.5122 - dave.jones2@alaska.gov | AQ1524CPT01 | 4922 | 486210 | None Found | 01/25/2019 &nbsp;ACT | 08/13/2020 &nbsp;ACT | 2020-08-14 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Gas Treatment Plant (GTP) is part of one integrated liquefied natural gas (LNG) project to bring natural gas from Alaskaâ€™s North Slope to international markets in the form of LNG, as well as for in-state deliveries in the form of natural gas. The GTP will take gas from the Prudhoe Bay Unit and the Point Thomson Unit and treat/process the gas, before it is sent 807 miles through a 42-inch diameter pipeline to a liquefaction facility in Nikiski on Alaskaâ€™s Kenai Peninsula for export in foreign commerce. The emissions units at the stationary source will include cogeneration gas-fired turbines with supplemental firing duct burners for gas compression, simple cycle gas-fired turbines for power generation, gas-fired heaters for building and process heat, as well as flares for control of excess gas. In addition, the GTP will include a diesel-fired black start generator, several diesel-fired firewater pumps and emergency generators, and storage tanks for diesel and gasoline fuels. |  | Six (6) Simple Cycle Gas-Turbines (Power Generation) | 15.11 | Natural Gas | 386 | MMBtu/hr | EUs 25 -30 each provide 44 MW of power generation for the facility | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good Combustion Practices and burning clean fuels (NG) | 15 | PPMV @ 15% O2 | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Potential CO emissions of 55.72 tpy for each turbine.
AK-0088 | LIQUEFACTION PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | KENAI PENNINSULA BOROUGH | AK | 99635 | USA | LISA HAAS |  | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - Permit Writer - dave.jones2@alaska.gov | AQ1539CPT01 | 4922 | 488999 | Not Found | 01/14/2020 &nbsp;ACT | 07/07/2022 &nbsp;ACT | 2022-08-04 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Liquefaction Plant is planned to encompass 921 acres, including 901 acres onshore for the liquefied natural gas (LNG) Plant as well as 20 acres offshore for the Marine Terminal. The Liquefaction Plant will be the terminus of an approximately 807-mile gas pipeline, allowing natural gas from Alaskaâ€™s North Slope to be shipped to outside markets. The stationary source will consist of structures and equipment associated with processing, storage, and loading of LNG. There will be three liquefaction trains combining to process up to approximately 20 million metric tons per annun of LNG. |  | Six Simle Cycle Gas-Fired Turbines | 15.11 | Natural Gas | 1113 | MMBtu/hr | EUs 1 - 6 are simple cycle gas turbines used for gas compression at LNG facility | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst and good combustion practices | 5 | PPMV @ 15% O2 | 3-HOURS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Allowed 40 hours per year per turbine of operation without SCR and OxCat.
AL-0329 | COLBERT COMBUSTION TURBINE PLANT | TENNESSEE VALLEY AUTHORITY | COLBERT | AL | 35674 | USA |  |  |  | 4 | AL001 | ALABAMA DEPT OF ENVIRONMENTAL MGMT | MR. DALE HURST | (334) 271-7882 | ADH@ADEM.STATE.AL.US |  | 701-0010 | 4911 | 221112 | 110000367834 | 06/10/2021 &nbsp;ACT | 09/21/2021 &nbsp;ACT | 2021-09-30 | 2022-03-04 | B |  | Electric Generating Facility |  | Three 229 MW Simple Cycle Combustion Turbines | 15.11 | Natural Gas | 229 | MW |  | Carbon Monoxide | Other - CEMS | (InOrganic Compounds) | 630-08-0 | N |  | 9 | PPMVD | 3 HOUR AVG / @15% O2 | BACT-PSD |  | U | 0 | N | 500 | LBS/EVENT | STARTUP AND SHUTDOWN | 0 |  |  | 0 | 0 | N
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG01 CO - Simple-Cycle Combustion Turbine 1 (Commissioning) [SCN0005] | 15.11 | Natural Gas | 2201 | MM BTU/hr | Commissioning is a one-time event which occurs after construction and is not anticipated to exceed 180 days. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices & use of pipeline quality natural gas | 2000 | LB/HR | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 350 | TONS/YR | ANNUAL AVEERAGE | 0 |  |  | 0 | 0 | N
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG02 CO - Simple-Cycle Combustion Turbine 2 (Commissioning) [SCN0006] | 15.11 | natural gas | 2201 | MM BTU/hr | Commissioning is a one-time event which occurs after construction and is not anticipated to exceed 180 days. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices & use of pipeline quality natural gas | 2000 | LB/HR | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 350 | TONS/YR | ANNUAL AVERAGE | 0 |  |  | 0 | 0 | N
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG01 SUSD - Simple-Cycle Combustion Turbine 1 (Startup/Shutdown/ Maintenance/Tuning/Runback) [EQT0019] | 15.11 | Natural Gas | 2201 | MM BTU/hR | Limited to 600 hr/yr | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices & use of pipeline quality natural gas | 800.08 | LB/HR | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | CO emissions will be monitored with a Continuous Emissions Monitoring System (CEMS).
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG02 SUSD - Simple-Cycle Combustion Turbine 2 (Startup/Shutdown/ Maintenance/Tuning/Runback) [EQT0020] | 15.11 | Natural Gas | 2201 | MM BTU/hr | limited to 600 hr/yr | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices & use of pipeline quality natural gas | 800.08 | LB/HR | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | CO emissions will be monitored with a Continuous Emissions Monitoring System (CEMS).
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG01 NO - Simple-Cycle Combustion Turbine 1 (Normal Operations) [EQT0017] | 15.11 | Natural Gas | 2201 | MM BTU/hr | Normal operations are based on 7000 hrs/yr | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices & use of pipeline quality natural gas | 6 | PPMVD AT 15% OXYGEN | ANNUAL AVERAGE | BACT-PSD | OPERATING PERMIT | U | 0 | U | 34.42 | LB/HR | HOURLY MAXIMUM | 0 |  |  | 0 | 0 | N |  | CO emissions will be monitored with a Continuous Emissions Monitoring System (CEMS).
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG02 NO - Simple-Cycle Combustion Turbine 2 (Normal Operations) [EQT0018] | 15.11 | Natural Gas | 2201 | MM BTU/hr | Normal operations are based on 7000 hours per year | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices & use of pipeline quality natural gas | 6 | PPMVD AT 15% O2 | ANNUAL AVERAGE | BACT-PSD | OPERATING PERMIT | U | 0 | U | 34.42 | LB/HR | HOURLY MAXIMUM | 0 |  |  | 0 | 0 | N |  | CO emissions will be monitored with a Continuous Emissions Monitoring System (CEMS).
LA-0331 | CALCASIEU PASS LNG PROJECT | VENTURE GLOBAL CALCASIEU PASS, LLC | CAMERON | LA | 70631 | USA | GRAHAM MCARTHUR | 202-759-6741 | GMCARTHUR@VGLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Ms. Mei Wu, (225)219-3180 | PDS-LA-805 | 4925 | 221210 | Not Found | 06/25/2018 &nbsp;ACT | 09/21/2018 &nbsp;ACT | 2019-02-14 | 2019-06-19 | A |  | New Liquefied Natural Gas (LNG) production, storage, and export terminal. | Application Received September 2, 2015. | Simple Cycle Combustion Turbines (SCCT1 to SCCT3) | 15.11 | Natural Gas | 927 | MM BTU/h |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Proper Equipment Design, Proper Operation, and Good Combustion Practices. | 25 | PPMV | 30 DAY ROLLING AVERAGE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Units are in ppmv @ 15% O2; 30 day rolling average during normal operations. Subject to 40 CFR 60 Subpart KKKK
LA-0349 | DRIFTWOOD LNG FACILITY | DRIFTWOOD LNG LLC | CALCASIEU | LA | 70663 | USA | CATHY ROURKE | 8329624031 | CATHY.ROURKE@TELLURIANINC.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen | PSD-LA-824 | 4925 | 221210 | Not Found | 10/30/2017 &nbsp;ACT | 07/10/2018 &nbsp;ACT | 2020-04-02 | 2021-08-06 | A |  | Propose a new facility to liquefy natural gas for export |  | Compressor Turbines (20) | 15.11 | natural gas | 540 | mm btu/hr |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good Combustion Practices | 25 | PPMVD | @ 15% O2 | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0383 | LAKE CHARLES LNG EXPORT TERMINAL | LAKE CHARLES LNG EXPORT COMPANY, LLC | CALCASIEU PARISH | LA | 70605 | USA | LISA GARCIA | 7039897762 | LISA.GARCIA@ENERGYTRANSFER.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Cathy E. Wilson - 225-219-3585 | PSD-LA-838 | 4925 | 486210 | 110070248334 | 04/30/2020 &nbsp;ACT | 09/03/2020 &nbsp;ACT | 2021-12-20 | 2022-03-04 | A |  | A greenfield facility to liquefy and export natural gas. |  | Turbines (EQT0020 - EQT0031) | 15.11 | Natural gas | 0 |  |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | catalytic oxidation and carbon monoxide turndown | 10 | PPMVD @15%O2 | 3-HOUR AVERAGE, @ LOAD =>50% | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0441 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, for technical questions regarding this permit. She may be reached at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 74-18 | 4911 | 221112 | 110040958425 | 10/16/2018 &nbsp;ACT | 12/21/2018 &nbsp;ACT | 2019-10-18 | 2021-08-09 | D |  | Natural gas combined-cycle power plant. | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGSC1-A nominally rated 667 MMBTU/hr natural gas-fired simple cycle CTG | 15.11 | Natural gas | 667 | MMBTU/H | A nominally rated 667 MMBTU/H natural gas-fired simple cycle CTG. The CTG will utilize DLNB and good combustion practices. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Dry low NOx burners and good combustion practices. | 9 | LB/H | HOURLY EXCEPT DURING STARTUP/SHUTDOWN | BACT-PSD | SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The use of combustion controls are considered technically feasible options for controlling CO emissions from the proposed natural gas-fired simple-cycle CTG, it is not economical in this case.
MI-0447 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-648-6339 or at ByrnesM@michigan.gov for technical questions related to this permit. Thank you. | 74-18A | 4911 | 221112 | 110040958425 | 09/22/2020 &nbsp;ACT | 01/07/2021 &nbsp;ACT | 2021-06-28 | 2021-09-10 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGSC1-natural gas fired simple cycle CTG | 15.11 | Natural gas | 667 | MMBTU/H | A nominally rated 667 MMBTU/hr natural gas-fired simple cycle CTG. The CTG will utilize DLNB and good combustion practices. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Dry low NOx burners and good combustion practices | 9 | LB/H | HOURLY; EXCEPT DURING STARTUP/SHUTDOWN | BACT-PSD | SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The use of combustion controls are considered technically feasible options for controlling CO emissions from the proposed natural gas-fired simple cycle CTG, it is not economical in this case.
MI-0454 | LBWL-ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions about this permit, please contact the permit engineer, Lauren Magirl, at 517-582-5345, or at MagirlL@michigan.gov. Thank you. | 74-18D | 4911 | 221112 | Not Found | 10/25/2022 &nbsp;ACT | 12/20/2022 &nbsp;ACT | 2022-12-29 | 2023-05-23 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWLâ€™s existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGSC1--A nominally rated 667 MMBTU/H natural gas-fired simple cycle CTG | 15.11 | Natural gas | 667 | MMBTU/H | A nominally rated 667MMBtu/hr, natural gas-fired simple cycle CTG. The CTG will utilize DLNB and good combustion practices. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Dry low NOx burners and good combustion practices. | 9 | LB/H | HOURLY EXCEPT DURING SU/SD | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emission limit 1 above = 9.0 lbs/hr, hourly except during startup and shutdown. The use of combustion controls are considered technically feasible options for controlling CO emissions from the proposed natural gas-fired simple-cycle CTG, it is not economical in this case.
*TN-0187 | TENNESSEE VALLEY AUTHORITY - JOHNSONVILLE COMBUSTION TURBINE | TENNESSEE VALLEY AUTHORITY | HUMPHREYS | TN | 37134 | USA | STEVEN TRULL | 731-648-2445 | SGTRULL@TVA.GOV | 4 | TN001 | TENN.DEPT. OF ENVIRONMENT & CONSERVATION, DIV OF AIR POLLUTION CONTROL | LACEY HARDIN | (615) 532-0545 | Lacey.Hardin@tn.gov |  | 979348 | 4911 | 221112 | Not Entered | 09/09/2021 &nbsp;ACT | 08/31/2022 &nbsp;ACT | 2023-03-17 | 2023-03-17 | B |  | Electric Generation Facility |  | Ten Simple Cycle NG Turbines | 15.11 | Natural Gas | 465.8 | MMBtu/hr | 465.8 MMBtu/hr per individual turbine 4658.0 MMBtu/hr total Aeroderivative | Carbon Monoxide | Other - CEMS RATA accordance with 40 CFR 60 Appendix B Spec 4 or 4A | (InOrganic Compounds) | 630-08-0 | A | oxidation catalyst | 5 | PPMVD @ 15% O2 | 4-HOUR ROLLING AVERAGE EXCLUDING STA/SHU | BACT-PSD |  | U | 0 | U | 25 | LB/EVENT | STARTUP AND SHUTDOWN | 0 |  |  | 0 | 0 | N
TX-0833 | JACKSON COUNTY GENERATORS | SOUTHERN POWER | JACKSON | TX |  | USA | SUSAN COMENSKY | 205-257-2098 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | PSDTX1422 | 4911 | 221112 | not found | 01/26/2016 &nbsp;ACT | 01/26/2018 &nbsp;ACT | 2018-04-26 | 2019-02-19 | A |  | four natural gas-fired simple-cycle combustion turbines, five fuel gas heaters, and a firewater pump engine |  | Combustion Turbines | 15.11 | natural gas | 920 | MW | 4 identical units, each limited to 2500 hours of operation per year | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Dry low NOx burners | 9 | PPMVD |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
TX-0833 | JACKSON COUNTY GENERATORS | SOUTHERN POWER | JACKSON | TX |  | USA | SUSAN COMENSKY | 205-257-2098 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | PSDTX1422 | 4911 | 221112 | not found | 01/26/2016 &nbsp;ACT | 01/26/2018 &nbsp;ACT | 2018-04-26 | 2019-02-19 | A |  | four natural gas-fired simple-cycle combustion turbines, five fuel gas heaters, and a firewater pump engine |  | Combustion Turbines MSS | 15.11 | NATURAL GAS | 0 |  |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Minimizing duration of startup/shutdown, using good air pollution control practices and safe operating practices. | 0.01 | TON/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0851 | RIO BRAVO PIPELINE FACILITY | RIO GRANDE LNG LLC | CAMERON | TX |  | USA | SHAUN DAVISON |  |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Michael Cheek, P.E., (512) 239-4936, Michael.Cheek@tceq.texas.gov | 140792, PSDTX1498, GHGPSDTX158 | 4922 | 486210 | Not Found | 02/22/2018 &nbsp;ACT | 12/17/2018 &nbsp;ACT | 2019-02-12 | 2019-02-19 | A |  | Natural gas processing and liquefied natural gas (LNG) export terminal |  | Refrigeration Compression Turbines | 15.11 | NATL GAS | 967 | MMBTU/HR | Twelve General Electric Frame 7EA simple cycle combustion turbines to serve as drivers for refrigeration and compression at the site. There are six process trains and there are two turbines per train. One each of the pairs of turbines has a downstream heat exchanger in the exhaust stream. The heat exchanger heats oil in a closed circuit for process uses elsewhere in the natural gas liquefaction system. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Dry Low NOx burners. Good combustion practices | 25 | PPMVD | 15% O2 | BACT-PSD | NSPS , NESHAP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0933 | NACERO PENWELL FACILITY | NACERO TX 1 LLC | ECTOR | TX |  | USA | HAL BOUKNIGHT | 864-354-6062 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Cara Hill, (512) 239-5123, Cara.Hill@tceq.texas.gov | 164137 PSDTX1594 GHGPSDTX207 | 2869 | 325110 | NOT FOUND | 09/20/2021 &nbsp;ACT | 11/17/2021 &nbsp;ACT | 2021-10-27 | 2022-03-08 | A |  | Nacero proposes to construct and operate a plant that will convert natural gas to methanol and then convert methanol to a finished gasoline component. |  | TURBINE | 15.11 | NATURAL GAS | 0 |  |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Oxidization catalyst, good combustion practices and the use of gaseous fuel | 9 | PPMVD | 15% O2 | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
WV-0028 | WAVERLY POWER PLANT | PLEASANTS ENERGY LLC | PLEASANTS | WV | 26170 | USA | GERALD GATTI | 3046654201 | GERALD.GATTI@DYNEGY.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Mr. Steve Pursley, PE Engineer West Virginia Division of Air Quality 601-57th St., SE Charleston, WV 25304 Phone: (304) 926-0499 x1218 Fax: (304) 926-0478 steve.r.pursley@wv.gov | R14-0034A | 4911 | 221112 | 110063231042 | 11/30/2017 &nbsp;ACT | 03/13/2018 &nbsp;ACT | 2018-05-29 | 2019-02-20 | U | https://dep.wv.gov/daq/Documents/March 2018 Permits and Evals/073-00022_PERM_R14-0034A.pdf | 300 MW Sinple-Cycle Peaking Plant | Modification to existing PSD Permit (R14-0034, RBLC Number WV-0027) to add &lsquo;&lsquo;advanced gas path&lsquo;&lsquo; technology to the turbines that was defined as a &lsquo;&lsquo;change in the method of operation&lsquo;&lsquo; that resulted a major modification to the turbines. | GE 7FA.004 Turbine | 15.11 | Natural Gas | 167.8 | MW | This one entry is for both turbines as they are the same. Each turbine, after this modification, is a nominal 167.8 MW GE Model 7FA.004. Has oil-fire backup. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Combustion Controls | 33.9 | LB/HR |  | BACT-PSD |  | U | 0 | U | 235.54 | TONS/YEAR |  | 9 | PPM |  | 0 | 0 | N
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG01 CO - Simple-Cycle Combustion Turbine 1 (Commissioning) [SCN0005] | 15.11 | Natural Gas | 2201 | MM BTU/hr | Commissioning is a one-time event which occurs after construction and is not anticipated to exceed 180 days. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Pipeline quality natural gas & dry-low-NOX burners | 240 | LB/HR | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 42 | TONS/YR | ANNUAL AVERAGE | 0 |  |  | 0 | 0 | N
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG02 CO - Simple-Cycle Combustion Turbine 2 (Commissioning) [SCN0006] | 15.11 | natural gas | 2201 | MM BTU/hr | Commissioning is a one-time event which occurs after construction and is not anticipated to exceed 180 days. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Pipeline quality natural gas & dry-low-NOX burners | 240 | LB/HR | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 42 | TONS/YR | ANNUAL AVERAGE | 0 |  |  | 0 | 0 | N
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG01 SUSD - Simple-Cycle Combustion Turbine 1 (Startup/Shutdown/ Maintenance/Tuning/Runback) [EQT0019] | 15.11 | Natural Gas | 2201 | MM BTU/hR | Limited to 600 hr/yr | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Pipeline quality natural gas & dry-low-NOX burners | 86.38 | LB/HR | HOURLY MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NOX monitored with a Continuous Emissions Monitoring System (CEMS) as required by NSPS Subpart KKKK.
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG02 SUSD - Simple-Cycle Combustion Turbine 2 (Startup/Shutdown/ Maintenance/Tuning/Runback) [EQT0020] | 15.11 | Natural Gas | 2201 | MM BTU/hr | limited to 600 hr/yr | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Pipeline quality natural gas & dry-low-NOX burners | 86.38 | LB/HR | HOURLY MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NOX monitored with a Continuous Emissions Monitoring System (CEMS) as required by NSPS Subpart KKKK.
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG01 NO - Simple-Cycle Combustion Turbine 1 (Normal Operations) [EQT0017] | 15.11 | Natural Gas | 2201 | MM BTU/hr | Normal operations are based on 7000 hrs/yr | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Pipeline quality natural gas & dry-low-NOX burners | 9 | PPMVD @15%O2 | 30-DAY ROLLING AVERAGE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 73.08 | LB/HR | HOURLY MAXIMUM | 0 |  |  | 0 | 0 | N |  | NOX monitored with a Continuous Emissions Monitoring System (CEMS) as required by NSPS Subpart KKKK.
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG02 NO - Simple-Cycle Combustion Turbine 2 (Normal Operations) [EQT0018] | 15.11 | Natural Gas | 2201 | MM BTU/hr | Normal operations are based on 7000 hours per year | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Pipeline quality natural gas & dry-low-NOX burners | 9 | PPMVD @15%O2 | 30-DAY ROLLING AVERAGE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 73.08 | LB/HR | HOURLY MAXIMUM | 0 |  |  | 0 | 0 | N |  | NOX monitored with a Continuous Emissions Monitoring System (CEMS) as required by NSPS Subpart KKKK.
*TN-0187 | TENNESSEE VALLEY AUTHORITY - JOHNSONVILLE COMBUSTION TURBINE | TENNESSEE VALLEY AUTHORITY | HUMPHREYS | TN | 37134 | USA | STEVEN TRULL | 731-648-2445 | SGTRULL@TVA.GOV | 4 | TN001 | TENN.DEPT. OF ENVIRONMENT & CONSERVATION, DIV OF AIR POLLUTION CONTROL | LACEY HARDIN | (615) 532-0545 | Lacey.Hardin@tn.gov |  | 979348 | 4911 | 221112 | Not Entered | 09/09/2021 &nbsp;ACT | 08/31/2022 &nbsp;ACT | 2023-03-17 | 2023-03-17 | B |  | Electric Generation Facility |  | Ten Simple Cycle NG Turbines | 15.11 | Natural Gas | 465.8 | MMBtu/hr | 465.8 MMBtu/hr per individual turbine 4658.0 MMBtu/hr total Aeroderivative | Nitrogen Oxides (NOx) | Other - CEMS certified in accordance with 40 CFR Part 75 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | dry low-NOx burners selective catalytic reduction | 5 | PPMVD @ 15% O2 | 4-HOUR ROLLING AVERAGE EXCLUDING STA/SHU | BACT-PSD | NSPS | N | 0 | U | 21.8 | LB/EVENT | STARTUP AND SHUTDOWN | 0 |  |  | 0 | 0 | N
AK-0085 | GAS TREATMENT PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | NORTH SLOPE BOROUGH | AK | 99734 | USA | LISA HAAS | 907.947.9353 | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - 907.465.5122 - dave.jones2@alaska.gov | AQ1524CPT01 | 4922 | 486210 | None Found | 01/25/2019 &nbsp;ACT | 08/13/2020 &nbsp;ACT | 2020-08-14 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Gas Treatment Plant (GTP) is part of one integrated liquefied natural gas (LNG) project to bring natural gas from Alaskaâ€™s North Slope to international markets in the form of LNG, as well as for in-state deliveries in the form of natural gas. The GTP will take gas from the Prudhoe Bay Unit and the Point Thomson Unit and treat/process the gas, before it is sent 807 miles through a 42-inch diameter pipeline to a liquefaction facility in Nikiski on Alaskaâ€™s Kenai Peninsula for export in foreign commerce. The emissions units at the stationary source will include cogeneration gas-fired turbines with supplemental firing duct burners for gas compression, simple cycle gas-fired turbines for power generation, gas-fired heaters for building and process heat, as well as flares for control of excess gas. In addition, the GTP will include a diesel-fired black start generator, several diesel-fired firewater pumps and emergency generators, and storage tanks for diesel and gasoline fuels. |  | Six (6) Simple Cycle Gas-Turbines (Power Generation) | 15.11 | Natural Gas | 386 | MMBtu/hr | EUs 25 -30 each provide 44 MW of power generation for the facility | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | DLN combustors and Good Combustion Practices | 15 | PPMV @ 15% O2 | 3-HOUR AVERAGE | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Potential NOx emissions of 91.53 tpy for each turbine.
AK-0088 | LIQUEFACTION PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | KENAI PENNINSULA BOROUGH | AK | 99635 | USA | LISA HAAS |  | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - Permit Writer - dave.jones2@alaska.gov | AQ1539CPT01 | 4922 | 488999 | Not Found | 01/14/2020 &nbsp;ACT | 07/07/2022 &nbsp;ACT | 2022-08-04 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Liquefaction Plant is planned to encompass 921 acres, including 901 acres onshore for the liquefied natural gas (LNG) Plant as well as 20 acres offshore for the Marine Terminal. The Liquefaction Plant will be the terminus of an approximately 807-mile gas pipeline, allowing natural gas from Alaskaâ€™s North Slope to be shipped to outside markets. The stationary source will consist of structures and equipment associated with processing, storage, and loading of LNG. There will be three liquefaction trains combining to process up to approximately 20 million metric tons per annun of LNG. |  | Six Simle Cycle Gas-Fired Turbines | 15.11 | Natural Gas | 1113 | MMBtu/hr | EUs 1 - 6 are simple cycle gas turbines used for gas compression at LNG facility | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR, DLN combustors, and good combustion practices | 2 | PPMV @ 15% O2 | 3-HOURS | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Allowed 40 hours per year per turbine of operation without SCR and OxCat.
AL-0329 | COLBERT COMBUSTION TURBINE PLANT | TENNESSEE VALLEY AUTHORITY | COLBERT | AL | 35674 | USA |  |  |  | 4 | AL001 | ALABAMA DEPT OF ENVIRONMENTAL MGMT | MR. DALE HURST | (334) 271-7882 | ADH@ADEM.STATE.AL.US |  | 701-0010 | 4911 | 221112 | 110000367834 | 06/10/2021 &nbsp;ACT | 09/21/2021 &nbsp;ACT | 2021-09-30 | 2022-03-04 | B |  | Electric Generating Facility |  | Three 229 MW Simple Cycle Combustion Turbines | 15.11 | Natural Gas | 229 | MW |  | Nitrogen Oxides (NOx) | Other - CEMS | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 9 | PPMVD | 3 HOUR AVG @ 15% O2 | BACT-PSD | NSPS , SIP | U | 0 | N | 380 | TONS | 12 MONTH | 0 |  |  | 0 | 0 | N
LA-0331 | CALCASIEU PASS LNG PROJECT | VENTURE GLOBAL CALCASIEU PASS, LLC | CAMERON | LA | 70631 | USA | GRAHAM MCARTHUR | 202-759-6741 | GMCARTHUR@VGLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Ms. Mei Wu, (225)219-3180 | PDS-LA-805 | 4925 | 221210 | Not Found | 06/25/2018 &nbsp;ACT | 09/21/2018 &nbsp;ACT | 2019-02-14 | 2019-06-19 | A |  | New Liquefied Natural Gas (LNG) production, storage, and export terminal. | Application Received September 2, 2015. | Simple Cycle Combustion Turbines (SCCT1 to SCCT3) | 15.11 | Natural Gas | 927 | MM BTU/h |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry Low NOx Combustor Design, Good Combustion Practices, and Natural Gas Combustion. | 9 | PPMV | 30 DAY ROLLING AVERAGE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Units are in ppmv @ 15% O2; 30 day rolling average during normal operations. Subject to 40 CFR 60 Subpart KKKK
LA-0343 | SABINE PASS LNG TERMINAL | SABINE PASS LNG LP AND SABINE PASS LIQUEFACTION LL | CAMERON | LA | 70631 | USA | PATTY KUSEK | 3375697915 | PATTY.KUSEK@CHENIERE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Dan nguyen - 225-219-3395 | PSD-LA-703(M7) | 4925 | 488999 | Not Found | 03/15/2019 &nbsp;ACT | 09/06/2019 &nbsp;ACT | 2020-03-31 | 2021-08-06 | C |  | a terminal to import lng and liquefy/export natural gas Modification to add startup, shutdown, maintenance scenarios |  | gas turbines during startups, shutdowns, and maintenance | 15.11 | natural gas | 0 |  | during startups, shutdowns, and maintenance | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | good combustion practices | 96 | PPMV | @ 15% O2 | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0349 | DRIFTWOOD LNG FACILITY | DRIFTWOOD LNG LLC | CALCASIEU | LA | 70663 | USA | CATHY ROURKE | 8329624031 | CATHY.ROURKE@TELLURIANINC.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen | PSD-LA-824 | 4925 | 221210 | Not Found | 10/30/2017 &nbsp;ACT | 07/10/2018 &nbsp;ACT | 2020-04-02 | 2021-08-06 | A |  | Propose a new facility to liquefy natural gas for export |  | Compressor Turbines (20) | 15.11 | natural gas | 540 | mm btu/hr |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | DLN and SCR | 5 | PPMVD | @ 15% O2 | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0383 | LAKE CHARLES LNG EXPORT TERMINAL | LAKE CHARLES LNG EXPORT COMPANY, LLC | CALCASIEU PARISH | LA | 70605 | USA | LISA GARCIA | 7039897762 | LISA.GARCIA@ENERGYTRANSFER.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Cathy E. Wilson - 225-219-3585 | PSD-LA-838 | 4925 | 486210 | 110070248334 | 04/30/2020 &nbsp;ACT | 09/03/2020 &nbsp;ACT | 2021-12-20 | 2022-03-04 | A |  | A greenfield facility to liquefy and export natural gas. |  | Turbines (EQT0020 - EQT0031) | 15.11 | Natural gas | 0 |  |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | LNB + SCR | 3.1 | PPMVD @15%O2 | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0441 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, for technical questions regarding this permit. She may be reached at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 74-18 | 4911 | 221112 | 110040958425 | 10/16/2018 &nbsp;ACT | 12/21/2018 &nbsp;ACT | 2019-10-18 | 2021-08-09 | D |  | Natural gas combined-cycle power plant. | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGSC1-A nominally rated 667 MMBTU/hr natural gas-fired simple cycle CTG | 15.11 | Natural gas | 667 | MMBTU/H | A nominally rated 667 MMBTU/H natural gas-fired simple cycle CTG. The CTG will utilize DLNB and good combustion practices. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Dry low NOx burners (DLNB) and good combustion practices. | 25 | PPM | AT 15%O2;4-HR ROLL AVG; SEE NOTES BELOW | BACT-PSD | NSPS , SIP | N | 0 | U | 60 | LB/H | 24-HR ROLL AVG; SEE NOTES BELOW | 0 |  |  | 0 | 0 | N |  | Emission Limit 1 is 25 ppmvd at 15%Ox. It is based on a 4-hour rolling average, except during operation less than 75 percent of peak load. Emission Limit 2 is 60.0 lb/h based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown. Efficiency for DLNB ranges from 70-80%.
MI-0447 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-648-6339 or at ByrnesM@michigan.gov for technical questions related to this permit. Thank you. | 74-18A | 4911 | 221112 | 110040958425 | 09/22/2020 &nbsp;ACT | 01/07/2021 &nbsp;ACT | 2021-06-28 | 2021-09-10 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGSC1-natural gas fired simple cycle CTG | 15.11 | Natural gas | 667 | MMBTU/H | A nominally rated 667 MMBTU/hr natural gas-fired simple cycle CTG. The CTG will utilize DLNB and good combustion practices. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | DLNB and good combustion practices. | 25 | PPM | 4-HR ROLL AVG EXCEPT LESS THAN 75% PEAK | BACT-PSD | NSPS , SIP | N | 70 | U | 60 | LB/H | 24-HR ROLL AVG EXCEPT SS | 0 |  |  | 0 | 0 | N |  | Emission Limit 1 = 25 ppmvd at 15% oxygen (O2) based on a 4-hour rolling average, except during operation less than 75% of peak load. Emission Limit 2 = 60.0 lb/hour based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown. Efficiency for DLNB ranges from 70-80%.
MI-0454 | LBWL-ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions about this permit, please contact the permit engineer, Lauren Magirl, at 517-582-5345, or at MagirlL@michigan.gov. Thank you. | 74-18D | 4911 | 221112 | Not Found | 10/25/2022 &nbsp;ACT | 12/20/2022 &nbsp;ACT | 2022-12-29 | 2023-05-23 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWLâ€™s existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGSC1--A nominally rated 667 MMBTU/H natural gas-fired simple cycle CTG | 15.11 | Natural gas | 667 | MMBTU/H | A nominally rated 667MMBtu/hr, natural gas-fired simple cycle CTG. The CTG will utilize DLNB and good combustion practices. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | DLNB and good combustion practices. | 25 | PPM | 4-HR ROLLING AVG EXCEPT <75% PEAK LOAD | BACT-PSD | NSPS , SIP | N | 70 | N | 60 | LB/H | 24-HR ROLLING AVG EXCEPT SU/SD | 0 |  |  | 0 | 0 | N |  | Emission limit 1 above = 25 ppmvd at 15% O2 based on a 4-hour rolling average, except during operation less than 75% of peak load. Emission limit 2 above = 60.0 lbs/hr based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown. Efficiency for DLNB ranges from 70-80%.
TX-0833 | JACKSON COUNTY GENERATORS | SOUTHERN POWER | JACKSON | TX |  | USA | SUSAN COMENSKY | 205-257-2098 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | PSDTX1422 | 4911 | 221112 | not found | 01/26/2016 &nbsp;ACT | 01/26/2018 &nbsp;ACT | 2018-04-26 | 2019-02-19 | A |  | four natural gas-fired simple-cycle combustion turbines, five fuel gas heaters, and a firewater pump engine |  | Combustion Turbines | 15.11 | natural gas | 920 | MW | 4 identical units, each limited to 2500 hours of operation per year | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry low NOx burners | 9 | PPMVD |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
TX-0833 | JACKSON COUNTY GENERATORS | SOUTHERN POWER | JACKSON | TX |  | USA | SUSAN COMENSKY | 205-257-2098 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | PSDTX1422 | 4911 | 221112 | not found | 01/26/2016 &nbsp;ACT | 01/26/2018 &nbsp;ACT | 2018-04-26 | 2019-02-19 | A |  | four natural gas-fired simple-cycle combustion turbines, five fuel gas heaters, and a firewater pump engine |  | Combustion Turbines MSS | 15.11 | NATURAL GAS | 0 |  |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Minimizing duration of startup/shutdown, using good air pollution control practices and safe operating practices. | 0.01 | TON/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0851 | RIO BRAVO PIPELINE FACILITY | RIO GRANDE LNG LLC | CAMERON | TX |  | USA | SHAUN DAVISON |  |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Michael Cheek, P.E., (512) 239-4936, Michael.Cheek@tceq.texas.gov | 140792, PSDTX1498, GHGPSDTX158 | 4922 | 486210 | Not Found | 02/22/2018 &nbsp;ACT | 12/17/2018 &nbsp;ACT | 2019-02-12 | 2019-02-19 | A |  | Natural gas processing and liquefied natural gas (LNG) export terminal |  | Refrigeration Compression Turbines | 15.11 | NATL GAS | 967 | MMBTU/HR | Twelve General Electric Frame 7EA simple cycle combustion turbines to serve as drivers for refrigeration and compression at the site. There are six process trains and there are two turbines per train. One each of the pairs of turbines has a downstream heat exchanger in the exhaust stream. The heat exchanger heats oil in a closed circuit for process uses elsewhere in the natural gas liquefaction system. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Dry Low NOx burners. Good combustion practices | 9 | PPMVD | 15% O2 | BACT-PSD | NSPS , NESHAP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0900 | ECTOR COUNTY ENERGY CENTER | ECTOR COUNTY ENERGY CENTER LLC | ECTOR | TX |  | USA | RICH DOWNEN | 360-593-2830 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Huy Pham, (512) 239-1358, Huy.Pham@tceq.texas.gov | 110423, PSDTX1366M1 GHGPSD49M1 | 4911 | 221112 | Not Found | 06/23/2020 &nbsp;ACT | 08/17/2020 &nbsp;ACT | 2020-06-25 | 2021-09-10 | C |  | increase the hours of operation for the two simple cycle gas turbines |  | Simple Cycle Turbines | 15.11 | natural gas | 0 |  |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Equipped with dry-low NOx burners with best management practices and good combustion practices. Minimize the duration of startup and shutdown events to less than 60 minutes per event. Limit MSS by 140 lb/hr maximum allowable emission rate for each turbine. | 9 | PPMVD | 3% O2 3 HR AVG | BACT-PSD | NSPS , MACT , SIP | N | 0 | U | 15 | PPMVD | PEAK 3% O2 1 HR AVG | 0 |  |  | 0 | 0 | N
TX-0933 | NACERO PENWELL FACILITY | NACERO TX 1 LLC | ECTOR | TX |  | USA | HAL BOUKNIGHT | 864-354-6062 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Cara Hill, (512) 239-5123, Cara.Hill@tceq.texas.gov | 164137 PSDTX1594 GHGPSDTX207 | 2869 | 325110 | NOT FOUND | 09/20/2021 &nbsp;ACT | 11/17/2021 &nbsp;ACT | 2021-10-27 | 2022-03-08 | A |  | Nacero proposes to construct and operate a plant that will convert natural gas to methanol and then convert methanol to a finished gasoline component. |  | TURBINE | 15.11 | NATURAL GAS | 0 |  |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | LOW NOX BURNERS AND SCR | 9 | PPMVD | 15% O2 | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
WV-0028 | WAVERLY POWER PLANT | PLEASANTS ENERGY LLC | PLEASANTS | WV | 26170 | USA | GERALD GATTI | 3046654201 | GERALD.GATTI@DYNEGY.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Mr. Steve Pursley, PE Engineer West Virginia Division of Air Quality 601-57th St., SE Charleston, WV 25304 Phone: (304) 926-0499 x1218 Fax: (304) 926-0478 steve.r.pursley@wv.gov | R14-0034A | 4911 | 221112 | 110063231042 | 11/30/2017 &nbsp;ACT | 03/13/2018 &nbsp;ACT | 2018-05-29 | 2019-02-20 | U | https://dep.wv.gov/daq/Documents/March 2018 Permits and Evals/073-00022_PERM_R14-0034A.pdf | 300 MW Sinple-Cycle Peaking Plant | Modification to existing PSD Permit (R14-0034, RBLC Number WV-0027) to add &lsquo;&lsquo;advanced gas path&lsquo;&lsquo; technology to the turbines that was defined as a &lsquo;&lsquo;change in the method of operation&lsquo;&lsquo; that resulted a major modification to the turbines. | GE 7FA.004 Turbine | 15.11 | Natural Gas | 167.8 | MW | This one entry is for both turbines as they are the same. Each turbine, after this modification, is a nominal 167.8 MW GE Model 7FA.004. Has oil-fire backup. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry LNB | 69 | LB/HR |  | BACT-PSD | NSPS | U | 0 | U | 232.3 | TONS/YEAR |  | 9 | PPM |  | 0 | 0 | N
TX-0851 | RIO BRAVO PIPELINE FACILITY | RIO GRANDE LNG LLC | CAMERON | TX |  | USA | SHAUN DAVISON |  |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Michael Cheek, P.E., (512) 239-4936, Michael.Cheek@tceq.texas.gov | 140792, PSDTX1498, GHGPSDTX158 | 4922 | 486210 | Not Found | 02/22/2018 &nbsp;ACT | 12/17/2018 &nbsp;ACT | 2019-02-12 | 2019-02-19 | A |  | Natural gas processing and liquefied natural gas (LNG) export terminal |  | Refrigeration Compression Turbines | 15.11 | NATL GAS | 967 | MMBTU/HR | Twelve General Electric Frame 7EA simple cycle combustion turbines to serve as drivers for refrigeration and compression at the site. There are six process trains and there are two turbines per train. One each of the pairs of turbines has a downstream heat exchanger in the exhaust stream. The heat exchanger heats oil in a closed circuit for process uses elsewhere in the natural gas liquefaction system. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and use of pipeline quality natural gas. | 7 | LB/HR |  | BACT-PSD | NSPS , NESHAP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0933 | NACERO PENWELL FACILITY | NACERO TX 1 LLC | ECTOR | TX |  | USA | HAL BOUKNIGHT | 864-354-6062 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Cara Hill, (512) 239-5123, Cara.Hill@tceq.texas.gov | 164137 PSDTX1594 GHGPSDTX207 | 2869 | 325110 | NOT FOUND | 09/20/2021 &nbsp;ACT | 11/17/2021 &nbsp;ACT | 2021-10-27 | 2022-03-08 | A |  | Nacero proposes to construct and operate a plant that will convert natural gas to methanol and then convert methanol to a finished gasoline component. |  | TURBINE | 15.11 | NATURAL GAS | 0 |  |  | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices and the use of gaseous fuel | 0.0075 | LB/MMBTU |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0851 | RIO BRAVO PIPELINE FACILITY | RIO GRANDE LNG LLC | CAMERON | TX |  | USA | SHAUN DAVISON |  |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Michael Cheek, P.E., (512) 239-4936, Michael.Cheek@tceq.texas.gov | 140792, PSDTX1498, GHGPSDTX158 | 4922 | 486210 | Not Found | 02/22/2018 &nbsp;ACT | 12/17/2018 &nbsp;ACT | 2019-02-12 | 2019-02-19 | A |  | Natural gas processing and liquefied natural gas (LNG) export terminal |  | Refrigeration Compression Turbines | 15.11 | NATL GAS | 967 | MMBTU/HR | Twelve General Electric Frame 7EA simple cycle combustion turbines to serve as drivers for refrigeration and compression at the site. There are six process trains and there are two turbines per train. One each of the pairs of turbines has a downstream heat exchanger in the exhaust stream. The heat exchanger heats oil in a closed circuit for process uses elsewhere in the natural gas liquefaction system. | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and use of pipeline quality natural gas. | 7 | LB/HR |  | BACT-PSD | NSPS , NESHAP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0933 | NACERO PENWELL FACILITY | NACERO TX 1 LLC | ECTOR | TX |  | USA | HAL BOUKNIGHT | 864-354-6062 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Cara Hill, (512) 239-5123, Cara.Hill@tceq.texas.gov | 164137 PSDTX1594 GHGPSDTX207 | 2869 | 325110 | NOT FOUND | 09/20/2021 &nbsp;ACT | 11/17/2021 &nbsp;ACT | 2021-10-27 | 2022-03-08 | A |  | Nacero proposes to construct and operate a plant that will convert natural gas to methanol and then convert methanol to a finished gasoline component. |  | TURBINE | 15.11 | NATURAL GAS | 0 |  |  | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices and the use of gaseous fuel | 0.0075 | LB/MMBTU |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0833 | JACKSON COUNTY GENERATORS | SOUTHERN POWER | JACKSON | TX |  | USA | SUSAN COMENSKY | 205-257-2098 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | PSDTX1422 | 4911 | 221112 | not found | 01/26/2016 &nbsp;ACT | 01/26/2018 &nbsp;ACT | 2018-04-26 | 2019-02-19 | A |  | four natural gas-fired simple-cycle combustion turbines, five fuel gas heaters, and a firewater pump engine |  | Combustion Turbines | 15.11 | natural gas | 920 | MW | 4 identical units, each limited to 2500 hours of operation per year | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of pipeline quality natural gas and good combustion practices. | 11.81 | TON/YR |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
TX-0933 | NACERO PENWELL FACILITY | NACERO TX 1 LLC | ECTOR | TX |  | USA | HAL BOUKNIGHT | 864-354-6062 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Cara Hill, (512) 239-5123, Cara.Hill@tceq.texas.gov | 164137 PSDTX1594 GHGPSDTX207 | 2869 | 325110 | NOT FOUND | 09/20/2021 &nbsp;ACT | 11/17/2021 &nbsp;ACT | 2021-10-27 | 2022-03-08 | A |  | Nacero proposes to construct and operate a plant that will convert natural gas to methanol and then convert methanol to a finished gasoline component. |  | TURBINE | 15.11 | NATURAL GAS | 0 |  |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices and the use of gaseous fuel | 0.0075 | LB/MMBTU |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0085 | GAS TREATMENT PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | NORTH SLOPE BOROUGH | AK | 99734 | USA | LISA HAAS | 907.947.9353 | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - 907.465.5122 - dave.jones2@alaska.gov | AQ1524CPT01 | 4922 | 486210 | None Found | 01/25/2019 &nbsp;ACT | 08/13/2020 &nbsp;ACT | 2020-08-14 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Gas Treatment Plant (GTP) is part of one integrated liquefied natural gas (LNG) project to bring natural gas from Alaskaâ€™s North Slope to international markets in the form of LNG, as well as for in-state deliveries in the form of natural gas. The GTP will take gas from the Prudhoe Bay Unit and the Point Thomson Unit and treat/process the gas, before it is sent 807 miles through a 42-inch diameter pipeline to a liquefaction facility in Nikiski on Alaskaâ€™s Kenai Peninsula for export in foreign commerce. The emissions units at the stationary source will include cogeneration gas-fired turbines with supplemental firing duct burners for gas compression, simple cycle gas-fired turbines for power generation, gas-fired heaters for building and process heat, as well as flares for control of excess gas. In addition, the GTP will include a diesel-fired black start generator, several diesel-fired firewater pumps and emergency generators, and storage tanks for diesel and gasoline fuels. |  | Six (6) Simple Cycle Gas-Turbines (Power Generation) | 15.11 | Natural Gas | 386 | MMBtu/hr | EUs 25 -30 each provide 44 MW of power generation for the facility | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion Practices and burning clean fuels (NG) | 0.007 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Potential particulate matter emissions of 11.78 tpy for each turbine.
AK-0088 | LIQUEFACTION PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | KENAI PENNINSULA BOROUGH | AK | 99635 | USA | LISA HAAS |  | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - Permit Writer - dave.jones2@alaska.gov | AQ1539CPT01 | 4922 | 488999 | Not Found | 01/14/2020 &nbsp;ACT | 07/07/2022 &nbsp;ACT | 2022-08-04 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Liquefaction Plant is planned to encompass 921 acres, including 901 acres onshore for the liquefied natural gas (LNG) Plant as well as 20 acres offshore for the Marine Terminal. The Liquefaction Plant will be the terminus of an approximately 807-mile gas pipeline, allowing natural gas from Alaskaâ€™s North Slope to be shipped to outside markets. The stationary source will consist of structures and equipment associated with processing, storage, and loading of LNG. There will be three liquefaction trains combining to process up to approximately 20 million metric tons per annun of LNG. |  | Six Simle Cycle Gas-Fired Turbines | 15.11 | Natural Gas | 1113 | MMBtu/hr | EUs 1 - 6 are simple cycle gas turbines used for gas compression at LNG facility | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and burning clean fuel (natural gas) | 0.007 | LB/MMBTU | 3-HOURS | BACT-PSD |  | U | 0 | U | 10 | % OPACITY | 6 CONSECUTIVE MINUTES | 0 |  |  | 0 | 0 | N
AL-0329 | COLBERT COMBUSTION TURBINE PLANT | TENNESSEE VALLEY AUTHORITY | COLBERT | AL | 35674 | USA |  |  |  | 4 | AL001 | ALABAMA DEPT OF ENVIRONMENTAL MGMT | MR. DALE HURST | (334) 271-7882 | ADH@ADEM.STATE.AL.US |  | 701-0010 | 4911 | 221112 | 110000367834 | 06/10/2021 &nbsp;ACT | 09/21/2021 &nbsp;ACT | 2021-09-30 | 2022-03-04 | B |  | Electric Generating Facility |  | Three 229 MW Simple Cycle Combustion Turbines | 15.11 | Natural Gas | 229 | MW |  | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | N |  | 0.008 | LB/MMBTU | 3 HOUR AVG | BACT-PSD | SIP | U | 0 | N | 18 | LB/HR | 3 HOUR AVG | 0 |  |  | 0 | 0 | N
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG01 CO - Simple-Cycle Combustion Turbine 1 (Commissioning) [SCN0005] | 15.11 | Natural Gas | 2201 | MM BTU/hr | Commissioning is a one-time event which occurs after construction and is not anticipated to exceed 180 days. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of low sulfur fuels (pipeline quality natural gas) | 6.3 | LB/HR | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.1 | TONS/YR | ANNUAL AVERAGE | 0 |  |  | 0 | 0 | N
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG02 CO - Simple-Cycle Combustion Turbine 2 (Commissioning) [SCN0006] | 15.11 | natural gas | 2201 | MM BTU/hr | Commissioning is a one-time event which occurs after construction and is not anticipated to exceed 180 days. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of low sulfur fuels (pipeline quality natural gas) | 6.3 | LB/HR | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.1 | TONS/YR | ANNUAL AVERAGE | 0 |  |  | 0 | 0 | N
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG01 SUSD - Simple-Cycle Combustion Turbine 1 (Startup/Shutdown/ Maintenance/Tuning/Runback) [EQT0019] | 15.11 | Natural Gas | 2201 | MM BTU/hR | Limited to 600 hr/yr | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of low sulfur fuels (pipeline quality natural gas) | 6.3 | LB/HR | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG02 SUSD - Simple-Cycle Combustion Turbine 2 (Startup/Shutdown/ Maintenance/Tuning/Runback) [EQT0020] | 15.11 | Natural Gas | 2201 | MM BTU/hr | limited to 600 hr/yr | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of low sulfur fuels (pipeline quality natural gas) | 6.3 | LB/HR | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG01 NO - Simple-Cycle Combustion Turbine 1 (Normal Operations) [EQT0017] | 15.11 | Natural Gas | 2201 | MM BTU/hr | Normal operations are based on 7000 hrs/yr | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of low sulfur fuels (pipeline quality natural gas) | 6.3 | LB/HR | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG02 NO - Simple-Cycle Combustion Turbine 2 (Normal Operations) [EQT0018] | 15.11 | Natural Gas | 2201 | MM BTU/hr | Normal operations are based on 7000 hours per year | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of low sulfur fuels (pipeline quality natural gas) | 6.3 | LB/HR | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0331 | CALCASIEU PASS LNG PROJECT | VENTURE GLOBAL CALCASIEU PASS, LLC | CAMERON | LA | 70631 | USA | GRAHAM MCARTHUR | 202-759-6741 | GMCARTHUR@VGLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Ms. Mei Wu, (225)219-3180 | PDS-LA-805 | 4925 | 221210 | Not Found | 06/25/2018 &nbsp;ACT | 09/21/2018 &nbsp;ACT | 2019-02-14 | 2019-06-19 | A |  | New Liquefied Natural Gas (LNG) production, storage, and export terminal. | Application Received September 2, 2015. | Simple Cycle Combustion Turbines (SCCT1 to SCCT3) | 15.11 | Natural Gas | 927 | MM BTU/h |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Exclusive Combustion of Fuel Gas and Good Combustion Practices, Including Proper Burner Design. | 8 | LB/H | 3 HOUR AVERAGE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Averaging time 3-hour Average during normal operations. Subject to 40 CFR 60 Subpart KKKK
LA-0349 | DRIFTWOOD LNG FACILITY | DRIFTWOOD LNG LLC | CALCASIEU | LA | 70663 | USA | CATHY ROURKE | 8329624031 | CATHY.ROURKE@TELLURIANINC.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen | PSD-LA-824 | 4925 | 221210 | Not Found | 10/30/2017 &nbsp;ACT | 07/10/2018 &nbsp;ACT | 2020-04-02 | 2021-08-06 | A |  | Propose a new facility to liquefy natural gas for export |  | Compressor Turbines (20) | 15.11 | natural gas | 540 | mm btu/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion Practices and Use of low sulfur facility fuel gas | 0.0066 | LB/MM BTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0383 | LAKE CHARLES LNG EXPORT TERMINAL | LAKE CHARLES LNG EXPORT COMPANY, LLC | CALCASIEU PARISH | LA | 70605 | USA | LISA GARCIA | 7039897762 | LISA.GARCIA@ENERGYTRANSFER.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Cathy E. Wilson - 225-219-3585 | PSD-LA-838 | 4925 | 486210 | 110070248334 | 04/30/2020 &nbsp;ACT | 09/03/2020 &nbsp;ACT | 2021-12-20 | 2022-03-04 | A |  | A greenfield facility to liquefy and export natural gas. |  | Turbines (EQT0020 - EQT0031) | 15.11 | Natural gas | 0 |  |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and clean natural gas | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0441 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, for technical questions regarding this permit. She may be reached at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 74-18 | 4911 | 221112 | 110040958425 | 10/16/2018 &nbsp;ACT | 12/21/2018 &nbsp;ACT | 2019-10-18 | 2021-08-09 | D |  | Natural gas combined-cycle power plant. | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGSC1-A nominally rated 667 MMBTU/hr natural gas-fired simple cycle CTG | 15.11 | Natural gas | 667 | MMBTU/H | A nominally rated 667 MMBTU/H natural gas-fired simple cycle CTG. The CTG will utilize DLNB and good combustion practices. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas, inlet air conditioning and good combustion practices. | 4.5 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Add-on control technology was not technically feasible; however, options were evaluated and it was determined they were not economically feasible.
MI-0447 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-648-6339 or at ByrnesM@michigan.gov for technical questions related to this permit. Thank you. | 74-18A | 4911 | 221112 | 110040958425 | 09/22/2020 &nbsp;ACT | 01/07/2021 &nbsp;ACT | 2021-06-28 | 2021-09-10 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGSC1-natural gas fired simple cycle CTG | 15.11 | Natural gas | 667 | MMBTU/H | A nominally rated 667 MMBTU/hr natural gas-fired simple cycle CTG. The CTG will utilize DLNB and good combustion practices. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | B | Pipeline quality natural gas, inlet air conditioning and good combustion practices. | 4.5 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Add-on control technology was not technically feasible; however, options were evaluated, and it was determined they were not economically feasible.
MI-0454 | LBWL-ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions about this permit, please contact the permit engineer, Lauren Magirl, at 517-582-5345, or at MagirlL@michigan.gov. Thank you. | 74-18D | 4911 | 221112 | Not Found | 10/25/2022 &nbsp;ACT | 12/20/2022 &nbsp;ACT | 2022-12-29 | 2023-05-23 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWLâ€™s existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGSC1--A nominally rated 667 MMBTU/H natural gas-fired simple cycle CTG | 15.11 | Natural gas | 667 | MMBTU/H | A nominally rated 667MMBtu/hr, natural gas-fired simple cycle CTG. The CTG will utilize DLNB and good combustion practices. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | B | Pipeline quality natural gas, inlet air conditioning and good combustion practices. | 4.5 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Add-on control technology was not technically feasible; however, options were evaluated, and it was determined they were not economically feasible.
TX-0833 | JACKSON COUNTY GENERATORS | SOUTHERN POWER | JACKSON | TX |  | USA | SUSAN COMENSKY | 205-257-2098 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | PSDTX1422 | 4911 | 221112 | not found | 01/26/2016 &nbsp;ACT | 01/26/2018 &nbsp;ACT | 2018-04-26 | 2019-02-19 | A |  | four natural gas-fired simple-cycle combustion turbines, five fuel gas heaters, and a firewater pump engine |  | Combustion Turbines | 15.11 | natural gas | 920 | MW | 4 identical units, each limited to 2500 hours of operation per year | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of pipeline quality natural gas and good combustion practices. | 11.81 | TON/YR |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
TX-0833 | JACKSON COUNTY GENERATORS | SOUTHERN POWER | JACKSON | TX |  | USA | SUSAN COMENSKY | 205-257-2098 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | PSDTX1422 | 4911 | 221112 | not found | 01/26/2016 &nbsp;ACT | 01/26/2018 &nbsp;ACT | 2018-04-26 | 2019-02-19 | A |  | four natural gas-fired simple-cycle combustion turbines, five fuel gas heaters, and a firewater pump engine |  | Combustion Turbines MSS | 15.11 | NATURAL GAS | 0 |  |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Minimizing duration of startup/shutdown, using good air pollution control practices and safe operating practices. | 0.01 | TON/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0085 | GAS TREATMENT PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | NORTH SLOPE BOROUGH | AK | 99734 | USA | LISA HAAS | 907.947.9353 | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - 907.465.5122 - dave.jones2@alaska.gov | AQ1524CPT01 | 4922 | 486210 | None Found | 01/25/2019 &nbsp;ACT | 08/13/2020 &nbsp;ACT | 2020-08-14 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Gas Treatment Plant (GTP) is part of one integrated liquefied natural gas (LNG) project to bring natural gas from Alaskaâ€™s North Slope to international markets in the form of LNG, as well as for in-state deliveries in the form of natural gas. The GTP will take gas from the Prudhoe Bay Unit and the Point Thomson Unit and treat/process the gas, before it is sent 807 miles through a 42-inch diameter pipeline to a liquefaction facility in Nikiski on Alaskaâ€™s Kenai Peninsula for export in foreign commerce. The emissions units at the stationary source will include cogeneration gas-fired turbines with supplemental firing duct burners for gas compression, simple cycle gas-fired turbines for power generation, gas-fired heaters for building and process heat, as well as flares for control of excess gas. In addition, the GTP will include a diesel-fired black start generator, several diesel-fired firewater pumps and emergency generators, and storage tanks for diesel and gasoline fuels. |  | Six (6) Simple Cycle Gas-Turbines (Power Generation) | 15.11 | Natural Gas | 386 | MMBtu/hr | EUs 25 -30 each provide 44 MW of power generation for the facility | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion Practices and burning clean fuels (NG) | 0.007 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Potential particulate matter emissions of 11.78 tpy for each turbine.
AK-0088 | LIQUEFACTION PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | KENAI PENNINSULA BOROUGH | AK | 99635 | USA | LISA HAAS |  | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - Permit Writer - dave.jones2@alaska.gov | AQ1539CPT01 | 4922 | 488999 | Not Found | 01/14/2020 &nbsp;ACT | 07/07/2022 &nbsp;ACT | 2022-08-04 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Liquefaction Plant is planned to encompass 921 acres, including 901 acres onshore for the liquefied natural gas (LNG) Plant as well as 20 acres offshore for the Marine Terminal. The Liquefaction Plant will be the terminus of an approximately 807-mile gas pipeline, allowing natural gas from Alaskaâ€™s North Slope to be shipped to outside markets. The stationary source will consist of structures and equipment associated with processing, storage, and loading of LNG. There will be three liquefaction trains combining to process up to approximately 20 million metric tons per annun of LNG. |  | Six Simle Cycle Gas-Fired Turbines | 15.11 | Natural Gas | 1113 | MMBtu/hr | EUs 1 - 6 are simple cycle gas turbines used for gas compression at LNG facility | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and burning clean fuel (natural gas) | 0.007 | LB/MMBTU | 3-HOURS | BACT-PSD |  | U | 0 | U | 10 | % OPACITY | 6 CONSECUTIVE MINUTES | 0 |  |  | 0 | 0 | N
AL-0329 | COLBERT COMBUSTION TURBINE PLANT | TENNESSEE VALLEY AUTHORITY | COLBERT | AL | 35674 | USA |  |  |  | 4 | AL001 | ALABAMA DEPT OF ENVIRONMENTAL MGMT | MR. DALE HURST | (334) 271-7882 | ADH@ADEM.STATE.AL.US |  | 701-0010 | 4911 | 221112 | 110000367834 | 06/10/2021 &nbsp;ACT | 09/21/2021 &nbsp;ACT | 2021-09-30 | 2022-03-04 | B |  | Electric Generating Facility |  | Three 229 MW Simple Cycle Combustion Turbines | 15.11 | Natural Gas | 229 | MW |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - 5,17, or 201 and 202 | (Particulate Matter (PM)) | PM | N |  | 0.008 | LB/MMBTU | 3 HOUR AVG | BACT-PSD |  | U | 0 | N | 18 | LB/HR | 3 HOUR AVG | 0 |  |  | 0 | 0 | N
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG01 CO - Simple-Cycle Combustion Turbine 1 (Commissioning) [SCN0005] | 15.11 | Natural Gas | 2201 | MM BTU/hr | Commissioning is a one-time event which occurs after construction and is not anticipated to exceed 180 days. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of low sulfur fuels (pipeline quality natural gas) | 6.3 | LB/HR | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.1 | TONS/YR | ANNUAL AVERAGE | 0 |  |  | 0 | 0 | N
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG02 CO - Simple-Cycle Combustion Turbine 2 (Commissioning) [SCN0006] | 15.11 | natural gas | 2201 | MM BTU/hr | Commissioning is a one-time event which occurs after construction and is not anticipated to exceed 180 days. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of low sulfur fuels (pipeline quality natural gas) | 6.3 | LB/HR | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.1 | TONS/YR | ANNUAL AVERAGE | 0 |  |  | 0 | 0 | N
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG01 SUSD - Simple-Cycle Combustion Turbine 1 (Startup/Shutdown/ Maintenance/Tuning/Runback) [EQT0019] | 15.11 | Natural Gas | 2201 | MM BTU/hR | Limited to 600 hr/yr | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of low sulfur fuels (pipeline quality natural gas) | 6.3 | LB/HR | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG02 SUSD - Simple-Cycle Combustion Turbine 2 (Startup/Shutdown/ Maintenance/Tuning/Runback) [EQT0020] | 15.11 | Natural Gas | 2201 | MM BTU/hr | limited to 600 hr/yr | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of low sulfur fuels (pipeline quality natural gas) | 6.3 | LB/HR | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG01 NO - Simple-Cycle Combustion Turbine 1 (Normal Operations) [EQT0017] | 15.11 | Natural Gas | 2201 | MM BTU/hr | Normal operations are based on 7000 hrs/yr | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices & use of low sulfur fuels (pipeline quality natural gas) | 6.3 | LB/HR | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG02 NO - Simple-Cycle Combustion Turbine 2 (Normal Operations) [EQT0018] | 15.11 | Natural Gas | 2201 | MM BTU/hr | Normal operations are based on 7000 hours per year | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices & use of low sulfur fuels (pipeline quality natural gas) | 6.3 | LB/HR | HOULY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0331 | CALCASIEU PASS LNG PROJECT | VENTURE GLOBAL CALCASIEU PASS, LLC | CAMERON | LA | 70631 | USA | GRAHAM MCARTHUR | 202-759-6741 | GMCARTHUR@VGLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Ms. Mei Wu, (225)219-3180 | PDS-LA-805 | 4925 | 221210 | Not Found | 06/25/2018 &nbsp;ACT | 09/21/2018 &nbsp;ACT | 2019-02-14 | 2019-06-19 | A |  | New Liquefied Natural Gas (LNG) production, storage, and export terminal. | Application Received September 2, 2015. | Simple Cycle Combustion Turbines (SCCT1 to SCCT3) | 15.11 | Natural Gas | 927 | MM BTU/h |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Exclusive Combustion of Fuel Gas and Good Combustion Practices, Including Proper Burner Design. | 8 | LB/H | 3 HOUR AVERAGE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Averaging time is 3-hour average during normal operations. Subject to 40 CFR 60 Subpart KKKK
LA-0349 | DRIFTWOOD LNG FACILITY | DRIFTWOOD LNG LLC | CALCASIEU | LA | 70663 | USA | CATHY ROURKE | 8329624031 | CATHY.ROURKE@TELLURIANINC.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen | PSD-LA-824 | 4925 | 221210 | Not Found | 10/30/2017 &nbsp;ACT | 07/10/2018 &nbsp;ACT | 2020-04-02 | 2021-08-06 | A |  | Propose a new facility to liquefy natural gas for export |  | Compressor Turbines (20) | 15.11 | natural gas | 540 | mm btu/hr |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion Practices and Use of low sulfur facility fuel gas | 0.0066 | LB/MM BTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0383 | LAKE CHARLES LNG EXPORT TERMINAL | LAKE CHARLES LNG EXPORT COMPANY, LLC | CALCASIEU PARISH | LA | 70605 | USA | LISA GARCIA | 7039897762 | LISA.GARCIA@ENERGYTRANSFER.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Cathy E. Wilson - 225-219-3585 | PSD-LA-838 | 4925 | 486210 | 110070248334 | 04/30/2020 &nbsp;ACT | 09/03/2020 &nbsp;ACT | 2021-12-20 | 2022-03-04 | A |  | A greenfield facility to liquefy and export natural gas. |  | Turbines (EQT0020 - EQT0031) | 15.11 | Natural gas | 0 |  |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and clean natural gas | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0441 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, for technical questions regarding this permit. She may be reached at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 74-18 | 4911 | 221112 | 110040958425 | 10/16/2018 &nbsp;ACT | 12/21/2018 &nbsp;ACT | 2019-10-18 | 2021-08-09 | D |  | Natural gas combined-cycle power plant. | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGSC1-A nominally rated 667 MMBTU/hr natural gas-fired simple cycle CTG | 15.11 | Natural gas | 667 | MMBTU/H | A nominally rated 667 MMBTU/H natural gas-fired simple cycle CTG. The CTG will utilize DLNB and good combustion practices. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas, inlet air conditioning and good combustion practices. | 4.5 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Add-on control technology was not technically feasible; however, options were evaluated and it was determined they were not economically feasible.
MI-0447 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-648-6339 or at ByrnesM@michigan.gov for technical questions related to this permit. Thank you. | 74-18A | 4911 | 221112 | 110040958425 | 09/22/2020 &nbsp;ACT | 01/07/2021 &nbsp;ACT | 2021-06-28 | 2021-09-10 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGSC1-natural gas fired simple cycle CTG | 15.11 | Natural gas | 667 | MMBTU/H | A nominally rated 667 MMBTU/hr natural gas-fired simple cycle CTG. The CTG will utilize DLNB and good combustion practices. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | B | Pipeline quality natural gas, inlet air conditioning and good combustion practices. | 4.5 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Add-on control technology was not technically feasible; however, options were evaluated and it was determined they were not economically feasible.
MI-0454 | LBWL-ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions about this permit, please contact the permit engineer, Lauren Magirl, at 517-582-5345, or at MagirlL@michigan.gov. Thank you. | 74-18D | 4911 | 221112 | Not Found | 10/25/2022 &nbsp;ACT | 12/20/2022 &nbsp;ACT | 2022-12-29 | 2023-05-23 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWLâ€™s existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGSC1--A nominally rated 667 MMBTU/H natural gas-fired simple cycle CTG | 15.11 | Natural gas | 667 | MMBTU/H | A nominally rated 667MMBtu/hr, natural gas-fired simple cycle CTG. The CTG will utilize DLNB and good combustion practices. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | B | Pipeline quality natural gas, inlet air conditioning and good combustion practices. | 4.5 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Add-on control technology was not technically feasible; however, options were evaluated, and it was determined they were not economically feasible.
TX-0833 | JACKSON COUNTY GENERATORS | SOUTHERN POWER | JACKSON | TX |  | USA | SUSAN COMENSKY | 205-257-2098 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | PSDTX1422 | 4911 | 221112 | not found | 01/26/2016 &nbsp;ACT | 01/26/2018 &nbsp;ACT | 2018-04-26 | 2019-02-19 | A |  | four natural gas-fired simple-cycle combustion turbines, five fuel gas heaters, and a firewater pump engine |  | Combustion Turbines | 15.11 | natural gas | 920 | MW | 4 identical units, each limited to 2500 hours of operation per year | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of pipeline quality natural gas and good combustion practices. | 11.81 | TON/YR |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
TX-0833 | JACKSON COUNTY GENERATORS | SOUTHERN POWER | JACKSON | TX |  | USA | SUSAN COMENSKY | 205-257-2098 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | PSDTX1422 | 4911 | 221112 | not found | 01/26/2016 &nbsp;ACT | 01/26/2018 &nbsp;ACT | 2018-04-26 | 2019-02-19 | A |  | four natural gas-fired simple-cycle combustion turbines, five fuel gas heaters, and a firewater pump engine |  | Combustion Turbines MSS | 15.11 | NATURAL GAS | 0 |  |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Minimizing duration of startup/shutdown, using good air pollution control practices and safe operating practices. | 0.01 | TON/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
WV-0028 | WAVERLY POWER PLANT | PLEASANTS ENERGY LLC | PLEASANTS | WV | 26170 | USA | GERALD GATTI | 3046654201 | GERALD.GATTI@DYNEGY.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Mr. Steve Pursley, PE Engineer West Virginia Division of Air Quality 601-57th St., SE Charleston, WV 25304 Phone: (304) 926-0499 x1218 Fax: (304) 926-0478 steve.r.pursley@wv.gov | R14-0034A | 4911 | 221112 | 110063231042 | 11/30/2017 &nbsp;ACT | 03/13/2018 &nbsp;ACT | 2018-05-29 | 2019-02-20 | U | https://dep.wv.gov/daq/Documents/March 2018 Permits and Evals/073-00022_PERM_R14-0034A.pdf | 300 MW Sinple-Cycle Peaking Plant | Modification to existing PSD Permit (R14-0034, RBLC Number WV-0027) to add &lsquo;&lsquo;advanced gas path&lsquo;&lsquo; technology to the turbines that was defined as a &lsquo;&lsquo;change in the method of operation&lsquo;&lsquo; that resulted a major modification to the turbines. | GE 7FA.004 Turbine | 15.11 | Natural Gas | 167.8 | MW | This one entry is for both turbines as they are the same. Each turbine, after this modification, is a nominal 167.8 MW GE Model 7FA.004. Has oil-fire backup. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Inlet air filtration. | 15.09 | LB/HR |  | BACT-PSD |  | U | 0 | U | 41.65 | TONS/YEAR |  | 15.09 | LB/HR |  | 0 | 0 | N
AK-0085 | GAS TREATMENT PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | NORTH SLOPE BOROUGH | AK | 99734 | USA | LISA HAAS | 907.947.9353 | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - 907.465.5122 - dave.jones2@alaska.gov | AQ1524CPT01 | 4922 | 486210 | None Found | 01/25/2019 &nbsp;ACT | 08/13/2020 &nbsp;ACT | 2020-08-14 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Gas Treatment Plant (GTP) is part of one integrated liquefied natural gas (LNG) project to bring natural gas from Alaskaâ€™s North Slope to international markets in the form of LNG, as well as for in-state deliveries in the form of natural gas. The GTP will take gas from the Prudhoe Bay Unit and the Point Thomson Unit and treat/process the gas, before it is sent 807 miles through a 42-inch diameter pipeline to a liquefaction facility in Nikiski on Alaskaâ€™s Kenai Peninsula for export in foreign commerce. The emissions units at the stationary source will include cogeneration gas-fired turbines with supplemental firing duct burners for gas compression, simple cycle gas-fired turbines for power generation, gas-fired heaters for building and process heat, as well as flares for control of excess gas. In addition, the GTP will include a diesel-fired black start generator, several diesel-fired firewater pumps and emergency generators, and storage tanks for diesel and gasoline fuels. |  | Six (6) Simple Cycle Gas-Turbines (Power Generation) | 15.11 | Natural Gas | 386 | MMBtu/hr | EUs 25 -30 each provide 44 MW of power generation for the facility | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion Practices and burning clean fuels (NG) | 0.007 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Potential particulate matter emissions of 11.78 tpy for each turbine.
AK-0088 | LIQUEFACTION PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | KENAI PENNINSULA BOROUGH | AK | 99635 | USA | LISA HAAS |  | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - Permit Writer - dave.jones2@alaska.gov | AQ1539CPT01 | 4922 | 488999 | Not Found | 01/14/2020 &nbsp;ACT | 07/07/2022 &nbsp;ACT | 2022-08-04 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Liquefaction Plant is planned to encompass 921 acres, including 901 acres onshore for the liquefied natural gas (LNG) Plant as well as 20 acres offshore for the Marine Terminal. The Liquefaction Plant will be the terminus of an approximately 807-mile gas pipeline, allowing natural gas from Alaskaâ€™s North Slope to be shipped to outside markets. The stationary source will consist of structures and equipment associated with processing, storage, and loading of LNG. There will be three liquefaction trains combining to process up to approximately 20 million metric tons per annun of LNG. |  | Six Simle Cycle Gas-Fired Turbines | 15.11 | Natural Gas | 1113 | MMBtu/hr | EUs 1 - 6 are simple cycle gas turbines used for gas compression at LNG facility | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and burning clean fuel (natural gas) | 0.007 | LB/MMBTU | 3-HOURS | BACT-PSD |  | U | 0 | U | 10 | % OPACITY | 6 CONSECUTIVE MINUTES | 0 |  |  | 0 | 0 | N
*TN-0187 | TENNESSEE VALLEY AUTHORITY - JOHNSONVILLE COMBUSTION TURBINE | TENNESSEE VALLEY AUTHORITY | HUMPHREYS | TN | 37134 | USA | STEVEN TRULL | 731-648-2445 | SGTRULL@TVA.GOV | 4 | TN001 | TENN.DEPT. OF ENVIRONMENT & CONSERVATION, DIV OF AIR POLLUTION CONTROL | LACEY HARDIN | (615) 532-0545 | Lacey.Hardin@tn.gov |  | 979348 | 4911 | 221112 | Not Entered | 09/09/2021 &nbsp;ACT | 08/31/2022 &nbsp;ACT | 2023-03-17 | 2023-03-17 | B |  | Electric Generation Facility |  | Ten Simple Cycle NG Turbines | 15.11 | Natural Gas | 465.8 | MMBtu/hr | 465.8 MMBtu/hr per individual turbine 4658.0 MMBtu/hr total Aeroderivative | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion design and operating practices and the use of low sulfur fuel | 3.65 | LB/HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0833 | JACKSON COUNTY GENERATORS | SOUTHERN POWER | JACKSON | TX |  | USA | SUSAN COMENSKY | 205-257-2098 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | PSDTX1422 | 4911 | 221112 | not found | 01/26/2016 &nbsp;ACT | 01/26/2018 &nbsp;ACT | 2018-04-26 | 2019-02-19 | A |  | four natural gas-fired simple-cycle combustion turbines, five fuel gas heaters, and a firewater pump engine |  | Combustion Turbines MSS | 15.11 | NATURAL GAS | 0 |  |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Minimizing duration of startup/shutdown, using good air pollution control practices and safe operating practices. | 0.01 | TON/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0085 | GAS TREATMENT PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | NORTH SLOPE BOROUGH | AK | 99734 | USA | LISA HAAS | 907.947.9353 | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - 907.465.5122 - dave.jones2@alaska.gov | AQ1524CPT01 | 4922 | 486210 | None Found | 01/25/2019 &nbsp;ACT | 08/13/2020 &nbsp;ACT | 2020-08-14 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Gas Treatment Plant (GTP) is part of one integrated liquefied natural gas (LNG) project to bring natural gas from Alaskaâ€™s North Slope to international markets in the form of LNG, as well as for in-state deliveries in the form of natural gas. The GTP will take gas from the Prudhoe Bay Unit and the Point Thomson Unit and treat/process the gas, before it is sent 807 miles through a 42-inch diameter pipeline to a liquefaction facility in Nikiski on Alaskaâ€™s Kenai Peninsula for export in foreign commerce. The emissions units at the stationary source will include cogeneration gas-fired turbines with supplemental firing duct burners for gas compression, simple cycle gas-fired turbines for power generation, gas-fired heaters for building and process heat, as well as flares for control of excess gas. In addition, the GTP will include a diesel-fired black start generator, several diesel-fired firewater pumps and emergency generators, and storage tanks for diesel and gasoline fuels. |  | Six (6) Simple Cycle Gas-Turbines (Power Generation) | 15.11 | Natural Gas | 386 | MMBtu/hr | EUs 25 -30 each provide 44 MW of power generation for the facility | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Good combustion practices and clean burning fuel low sulfur natural gas | 96 | PPMV SULFUR IN FUEL | PRIOR TO COMPLETING TREATMENT TRAINS | BACT-PSD |  | U | 0 | U | 16 | PPMV SULFUR IN FUEL | AFTER COMPLETING TREATMENT TRAINS | 0 |  |  | 0 | 0 | N |  | Potential SO2 emissions of 25.36 tpy and 4.23 tpy per turbine @ 96ppmv and 16 ppmv total sulfur in fuel respectively.
AK-0088 | LIQUEFACTION PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | KENAI PENNINSULA BOROUGH | AK | 99635 | USA | LISA HAAS |  | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - Permit Writer - dave.jones2@alaska.gov | AQ1539CPT01 | 4922 | 488999 | Not Found | 01/14/2020 &nbsp;ACT | 07/07/2022 &nbsp;ACT | 2022-08-04 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Liquefaction Plant is planned to encompass 921 acres, including 901 acres onshore for the liquefied natural gas (LNG) Plant as well as 20 acres offshore for the Marine Terminal. The Liquefaction Plant will be the terminus of an approximately 807-mile gas pipeline, allowing natural gas from Alaskaâ€™s North Slope to be shipped to outside markets. The stationary source will consist of structures and equipment associated with processing, storage, and loading of LNG. There will be three liquefaction trains combining to process up to approximately 20 million metric tons per annun of LNG. |  | Six Simle Cycle Gas-Fired Turbines | 15.11 | Natural Gas | 1113 | MMBtu/hr | EUs 1 - 6 are simple cycle gas turbines used for gas compression at LNG facility | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | pipeline quality natural gas and good combustion practices | 16 | PPMV SULFUR IN FUEL |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0331 | CALCASIEU PASS LNG PROJECT | VENTURE GLOBAL CALCASIEU PASS, LLC | CAMERON | LA | 70631 | USA | GRAHAM MCARTHUR | 202-759-6741 | GMCARTHUR@VGLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Ms. Mei Wu, (225)219-3180 | PDS-LA-805 | 4925 | 221210 | Not Found | 06/25/2018 &nbsp;ACT | 09/21/2018 &nbsp;ACT | 2019-02-14 | 2019-06-19 | A |  | New Liquefied Natural Gas (LNG) production, storage, and export terminal. | Application Received September 2, 2015. | Simple Cycle Combustion Turbines (SCCT1 to SCCT3) | 15.11 | Natural Gas | 927 | MM BTU/h |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Exclusive Combustion of low sulfur fuel - Fuel sulfur content <4 ppm, proper engineering practices. | 4 | PPMV | ANNUAL AVERAGE | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Units are in ppmv H2S; Annual Average Sulfur Content in Fuel
LA-0349 | DRIFTWOOD LNG FACILITY | DRIFTWOOD LNG LLC | CALCASIEU | LA | 70663 | USA | CATHY ROURKE | 8329624031 | CATHY.ROURKE@TELLURIANINC.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen | PSD-LA-824 | 4925 | 221210 | Not Found | 10/30/2017 &nbsp;ACT | 07/10/2018 &nbsp;ACT | 2020-04-02 | 2021-08-06 | A |  | Propose a new facility to liquefy natural gas for export |  | Compressor Turbines (20) | 15.11 | natural gas | 540 | mm btu/hr |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Good Combustion Practices and Use of low sulfur facility fuel gas | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0933 | NACERO PENWELL FACILITY | NACERO TX 1 LLC | ECTOR | TX |  | USA | HAL BOUKNIGHT | 864-354-6062 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Cara Hill, (512) 239-5123, Cara.Hill@tceq.texas.gov | 164137 PSDTX1594 GHGPSDTX207 | 2869 | 325110 | NOT FOUND | 09/20/2021 &nbsp;ACT | 11/17/2021 &nbsp;ACT | 2021-10-27 | 2022-03-08 | A |  | Nacero proposes to construct and operate a plant that will convert natural gas to methanol and then convert methanol to a finished gasoline component. |  | TURBINE | 15.11 | NATURAL GAS | 0 |  |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Low sulfur content in fuel | 0 |  |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0085 | GAS TREATMENT PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | NORTH SLOPE BOROUGH | AK | 99734 | USA | LISA HAAS | 907.947.9353 | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - 907.465.5122 - dave.jones2@alaska.gov | AQ1524CPT01 | 4922 | 486210 | None Found | 01/25/2019 &nbsp;ACT | 08/13/2020 &nbsp;ACT | 2020-08-14 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Gas Treatment Plant (GTP) is part of one integrated liquefied natural gas (LNG) project to bring natural gas from Alaskaâ€™s North Slope to international markets in the form of LNG, as well as for in-state deliveries in the form of natural gas. The GTP will take gas from the Prudhoe Bay Unit and the Point Thomson Unit and treat/process the gas, before it is sent 807 miles through a 42-inch diameter pipeline to a liquefaction facility in Nikiski on Alaskaâ€™s Kenai Peninsula for export in foreign commerce. The emissions units at the stationary source will include cogeneration gas-fired turbines with supplemental firing duct burners for gas compression, simple cycle gas-fired turbines for power generation, gas-fired heaters for building and process heat, as well as flares for control of excess gas. In addition, the GTP will include a diesel-fired black start generator, several diesel-fired firewater pumps and emergency generators, and storage tanks for diesel and gasoline fuels. |  | Six (6) Simple Cycle Gas-Turbines (Power Generation) | 15.11 | Natural Gas | 386 | MMBtu/hr | EUs 25 -30 each provide 44 MW of power generation for the facility | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good Combustion Practices and burning clean fuels (NG) | 0.0022 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Potential CO emissions of 3.75 tpy for each turbine.
AK-0088 | LIQUEFACTION PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | KENAI PENNINSULA BOROUGH | AK | 99635 | USA | LISA HAAS |  | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - Permit Writer - dave.jones2@alaska.gov | AQ1539CPT01 | 4922 | 488999 | Not Found | 01/14/2020 &nbsp;ACT | 07/07/2022 &nbsp;ACT | 2022-08-04 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Liquefaction Plant is planned to encompass 921 acres, including 901 acres onshore for the liquefied natural gas (LNG) Plant as well as 20 acres offshore for the Marine Terminal. The Liquefaction Plant will be the terminus of an approximately 807-mile gas pipeline, allowing natural gas from Alaskaâ€™s North Slope to be shipped to outside markets. The stationary source will consist of structures and equipment associated with processing, storage, and loading of LNG. There will be three liquefaction trains combining to process up to approximately 20 million metric tons per annun of LNG. |  | Six Simle Cycle Gas-Fired Turbines | 15.11 | Natural Gas | 1113 | MMBtu/hr | EUs 1 - 6 are simple cycle gas turbines used for gas compression at LNG facility | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation catalyst and good combustion practices | 2 | PPMV @ 15% O2 | 3-HOURS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Allowed 40 hours per year per turbine of operation without SCR and OxCat.
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG01 CO - Simple-Cycle Combustion Turbine 1 (Commissioning) [SCN0005] | 15.11 | Natural Gas | 2201 | MM BTU/hr | Commissioning is a one-time event which occurs after construction and is not anticipated to exceed 180 days. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices & use of pipeline quality natural gas | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG02 CO - Simple-Cycle Combustion Turbine 2 (Commissioning) [SCN0006] | 15.11 | natural gas | 2201 | MM BTU/hr | Commissioning is a one-time event which occurs after construction and is not anticipated to exceed 180 days. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices & use of pipeline quality natural gas | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG01 SUSD - Simple-Cycle Combustion Turbine 1 (Startup/Shutdown/ Maintenance/Tuning/Runback) [EQT0019] | 15.11 | Natural Gas | 2201 | MM BTU/hR | Limited to 600 hr/yr | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices & use of pipeline quality natural gas | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG02 SUSD - Simple-Cycle Combustion Turbine 2 (Startup/Shutdown/ Maintenance/Tuning/Runback) [EQT0020] | 15.11 | Natural Gas | 2201 | MM BTU/hr | limited to 600 hr/yr | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices & use of pipeline quality natural gas | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG01 NO - Simple-Cycle Combustion Turbine 1 (Normal Operations) [EQT0017] | 15.11 | Natural Gas | 2201 | MM BTU/hr | Normal operations are based on 7000 hrs/yr | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices & use of pipeline quality natural gas | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*LA-0327 | WASHINGTON PARISH ENERGY CENTER | WASHINGTON PARISH ENERGY CENTER ONE, LLC | WSHINGTON PARISH | LA | 70427 | USA | SETH BEREND | (713)830-8715 | SETH.BEREND@CALPINE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Mr. Christopher Smith (225) 219-3439 | PSD-LA-829 | 4911 | 221112 | Not Found | 10/20/2017 &nbsp;ACT | 05/23/2018 &nbsp;ACT | 2018-08-22 | 2021-06-03 | A |  | New 414 MW electric generating plant which provides electricity during peak demand. It consists of two simple-cycle turbine generators which fire natural gas only. | Application Accepted Date reflects date of administrative completeness. | CTG02 NO - Simple-Cycle Combustion Turbine 2 (Normal Operations) [EQT0018] | 15.11 | Natural Gas | 2201 | MM BTU/hr | Normal operations are based on 7000 hours per year | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices & use of pipeline quality natural gas | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0331 | CALCASIEU PASS LNG PROJECT | VENTURE GLOBAL CALCASIEU PASS, LLC | CAMERON | LA | 70631 | USA | GRAHAM MCARTHUR | 202-759-6741 | GMCARTHUR@VGLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Ms. Mei Wu, (225)219-3180 | PDS-LA-805 | 4925 | 221210 | Not Found | 06/25/2018 &nbsp;ACT | 09/21/2018 &nbsp;ACT | 2019-02-14 | 2019-06-19 | A |  | New Liquefied Natural Gas (LNG) production, storage, and export terminal. | Application Received September 2, 2015. | Simple Cycle Combustion Turbines (SCCT1 to SCCT3) | 15.11 | Natural Gas | 927 | MM BTU/h |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Proper Equipment Design, Proper Operation, and Good Combustion Practices. | 1.4 | PPMV | 3 HOUR AVERAGE | BACT-PSD | OPERATING PERMIT , NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Units are in PPMV @ 15% O2; Averaging period is 3 hour average during normal operations. Subject to 40 CFR 60 Subpart KKKK.
LA-0349 | DRIFTWOOD LNG FACILITY | DRIFTWOOD LNG LLC | CALCASIEU | LA | 70663 | USA | CATHY ROURKE | 8329624031 | CATHY.ROURKE@TELLURIANINC.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen | PSD-LA-824 | 4925 | 221210 | Not Found | 10/30/2017 &nbsp;ACT | 07/10/2018 &nbsp;ACT | 2020-04-02 | 2021-08-06 | A |  | Propose a new facility to liquefy natural gas for export |  | Compressor Turbines (20) | 15.11 | natural gas | 540 | mm btu/hr |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good Combustion Practices and Use of low sulfur facility fuel gas | 0.002 | LB/MM BTU | HHV | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0383 | LAKE CHARLES LNG EXPORT TERMINAL | LAKE CHARLES LNG EXPORT COMPANY, LLC | CALCASIEU PARISH | LA | 70605 | USA | LISA GARCIA | 7039897762 | LISA.GARCIA@ENERGYTRANSFER.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Cathy E. Wilson - 225-219-3585 | PSD-LA-838 | 4925 | 486210 | 110070248334 | 04/30/2020 &nbsp;ACT | 09/03/2020 &nbsp;ACT | 2021-12-20 | 2022-03-04 | A |  | A greenfield facility to liquefy and export natural gas. |  | Turbines (EQT0020 - EQT0031) | 15.11 | Natural gas | 0 |  |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0441 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, for technical questions regarding this permit. She may be reached at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 74-18 | 4911 | 221112 | 110040958425 | 10/16/2018 &nbsp;ACT | 12/21/2018 &nbsp;ACT | 2019-10-18 | 2021-08-09 | D |  | Natural gas combined-cycle power plant. | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGSC1-A nominally rated 667 MMBTU/hr natural gas-fired simple cycle CTG | 15.11 | Natural gas | 667 | MMBTU/H | A nominally rated 667 MMBTU/H natural gas-fired simple cycle CTG. The CTG will utilize DLNB and good combustion practices. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices. | 5 | LB/H | HOURLY EXCEPT DURING STARTUP/SHUTDOWN | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The thermal oxidation and NSCR were considered not technically feasible for these applications.
MI-0447 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-648-6339 or at ByrnesM@michigan.gov for technical questions related to this permit. Thank you. | 74-18A | 4911 | 221112 | 110040958425 | 09/22/2020 &nbsp;ACT | 01/07/2021 &nbsp;ACT | 2021-06-28 | 2021-09-10 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGSC1-natural gas fired simple cycle CTG | 15.11 | Natural gas | 667 | MMBTU/H | A nominally rated 667 MMBTU/hr natural gas-fired simple cycle CTG. The CTG will utilize DLNB and good combustion practices. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices | 5 | LB/H | HOURLY; EXCEPT DURING STARTUP/SHUTDOWN | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The thermal oxidation and NSCR were considered not technically feasible for the application.
MI-0454 | LBWL-ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions about this permit, please contact the permit engineer, Lauren Magirl, at 517-582-5345, or at MagirlL@michigan.gov. Thank you. | 74-18D | 4911 | 221112 | Not Found | 10/25/2022 &nbsp;ACT | 12/20/2022 &nbsp;ACT | 2022-12-29 | 2023-05-23 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWLâ€™s existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGSC1--A nominally rated 667 MMBTU/H natural gas-fired simple cycle CTG | 15.11 | Natural gas | 667 | MMBTU/H | A nominally rated 667MMBtu/hr, natural gas-fired simple cycle CTG. The CTG will utilize DLNB and good combustion practices. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices. | 5 | LB/H | HOURLY EXCEPT DURING SU/SD | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The thermal oxidation and NSCR were considered not technically feasible for these applications.
TX-0833 | JACKSON COUNTY GENERATORS | SOUTHERN POWER | JACKSON | TX |  | USA | SUSAN COMENSKY | 205-257-2098 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | PSDTX1422 | 4911 | 221112 | not found | 01/26/2016 &nbsp;ACT | 01/26/2018 &nbsp;ACT | 2018-04-26 | 2019-02-19 | A |  | four natural gas-fired simple-cycle combustion turbines, five fuel gas heaters, and a firewater pump engine |  | Combustion Turbines | 15.11 | natural gas | 920 | MW | 4 identical units, each limited to 2500 hours of operation per year | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices | 2 | PPMVD |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
TX-0833 | JACKSON COUNTY GENERATORS | SOUTHERN POWER | JACKSON | TX |  | USA | SUSAN COMENSKY | 205-257-2098 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | PSDTX1422 | 4911 | 221112 | not found | 01/26/2016 &nbsp;ACT | 01/26/2018 &nbsp;ACT | 2018-04-26 | 2019-02-19 | A |  | four natural gas-fired simple-cycle combustion turbines, five fuel gas heaters, and a firewater pump engine |  | Combustion Turbines MSS | 15.11 | NATURAL GAS | 0 |  |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Minimizing duration of startup/shutdown, using good air pollution control practices and safe operating practices. | 0.06 | TON/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0851 | RIO BRAVO PIPELINE FACILITY | RIO GRANDE LNG LLC | CAMERON | TX |  | USA | SHAUN DAVISON |  |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Michael Cheek, P.E., (512) 239-4936, Michael.Cheek@tceq.texas.gov | 140792, PSDTX1498, GHGPSDTX158 | 4922 | 486210 | Not Found | 02/22/2018 &nbsp;ACT | 12/17/2018 &nbsp;ACT | 2019-02-12 | 2019-02-19 | A |  | Natural gas processing and liquefied natural gas (LNG) export terminal |  | Refrigeration Compression Turbines | 15.11 | NATL GAS | 967 | MMBTU/HR | Twelve General Electric Frame 7EA simple cycle combustion turbines to serve as drivers for refrigeration and compression at the site. There are six process trains and there are two turbines per train. One each of the pairs of turbines has a downstream heat exchanger in the exhaust stream. The heat exchanger heats oil in a closed circuit for process uses elsewhere in the natural gas liquefaction system. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices | 2 | PPMVD | 15% O2 | BACT-PSD | NSPS , NESHAP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0933 | NACERO PENWELL FACILITY | NACERO TX 1 LLC | ECTOR | TX |  | USA | HAL BOUKNIGHT | 864-354-6062 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Cara Hill, (512) 239-5123, Cara.Hill@tceq.texas.gov | 164137 PSDTX1594 GHGPSDTX207 | 2869 | 325110 | NOT FOUND | 09/20/2021 &nbsp;ACT | 11/17/2021 &nbsp;ACT | 2021-10-27 | 2022-03-08 | A |  | Nacero proposes to construct and operate a plant that will convert natural gas to methanol and then convert methanol to a finished gasoline component. |  | TURBINE | 15.11 | NATURAL GAS | 0 |  |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidization catalyst, good combustion practices and the use of gaseous fuel | 1.7 | PPMVD |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N