## GTP Model Emissions
[19 empty] | Emission Rates (g/s) | [14 empty] | AQRV PM Speciation
Modeled ID | Emission Unit | Configuration | Coordinates (UTM, NAD 83, Zone 6) |  | Coordinates (Polar Stereographic) |  | Base Elevation (m) | Actual Height |  | Modeled Height |  | Temperature |  | Velocity |  | Diameter |  | In-Stack Ratio | NOx |  |  | CO |  | PM10 |  | PM2.5 |  | SO2 @16 ppmvd |  |  | SO2 @96 ppmvd |  |  | Equip Type | Fuel Type | PMF/SOIL | EC - PM2.5 | EC - PM10 | SOA - PM2.5 | SOA - PM10
|  |  | x | y | x | y |  | (ft) | (m) | (ft) | (m) | (°F) | (°K) | (ft/s) | (m/s) | (ft) | (m) | (-) | 1-hour | 24-hour | Annual | 1-hour | 8-hour | 24-hour | Annual | 24-hour | Annual | 1-hour | 3&24-hour | Annual | 1-hour | 3&24-hour | Annual |  |  | g/s | g/s | g/s | g/s | g/s | Conversion Table
Turbines | [40 empty] | 1 lb = | 453.59 | g
1A | Train 1a Treated Gas Compressor Turbine Primary Stack1 | Vert./no Cap | 441632.91 | 7802266.08 | 240.9746 | -96.1767 | 1.8288 | 240 | 73.152 | 240 | 73.152 | 410 | 483.15 | 52 | 15.8496 | 10 | 3.048 | 0.4 | 4.8427 | 4.8427 | 3.8362 | 5.5998 | 5.5998 | 0.54634 | 0.45801 | 0.54634 | 0.45801 | 0.22244 | 0.22244 | 0.18168 | 1.3325 | 1.3325 | 1.0884 | Turbine | Gas | 0 | 0.15728 | 0.15728 | 0.38906 | 0.38906 | 1 hr = | 3600 | sec
1B | Train 1b Treated Gas Compressor Turbine Primary Stack1 | Vert./no Cap | 441598.78 | 7802260.05 | 240.9417 | -96.1871 | 1.8288 | 240 | 73.152 | 240 | 73.152 | 410 | 483.15 | 52 | 15.8496 | 10 | 3.048 | 0.4 | 4.8427 | 4.8427 | 3.8362 | 5.5998 | 5.5998 | 0.54634 | 0.45801 | 0.54634 | 0.45801 | 0.22244 | 0.22244 | 0.18168 | 1.3325 | 1.3325 | 1.0884 | Turbine | Gas | 0 | 0.15728 | 0.15728 | 0.38906 | 0.38906
2A | Train 2a Treated Gas Compressor Turbine Primary Stack1 | Vert./no Cap | 441514.39 | 7802158.49 | 240.8716 | -96.2985 | 1.8288 | 240 | 73.152 | 240 | 73.152 | 410 | 483.15 | 52 | 15.8496 | 10 | 3.048 | 0.4 | 4.8427 | 4.8427 | 3.8362 | 5.5998 | 5.5998 | 0.54634 | 0.45801 | 0.54634 | 0.45801 | 0.22244 | 0.22244 | 0.18168 | 1.3325 | 1.3325 | 1.0884 | Turbine | Gas | 0 | 0.15728 | 0.15728 | 0.38906 | 0.38906
2B | Train 2b Treated Gas Compressor Turbine Primary Stack1 | Vert./no Cap | 441546.76 | 7802163.61 | 240.9029 | -96.2892 | 1.8288 | 240 | 73.152 | 240 | 73.152 | 410 | 483.15 | 52 | 15.8496 | 10 | 3.048 | 0.4 | 4.8427 | 4.8427 | 3.8362 | 5.5998 | 5.5998 | 0.54634 | 0.45801 | 0.54634 | 0.45801 | 0.22244 | 0.22244 | 0.18168 | 1.3325 | 1.3325 | 1.0884 | Turbine | Gas | 0 | 0.15728 | 0.15728 | 0.38906 | 0.38906
3A | Train 3a Treated Gas Compressor Turbine Primary Stack1 | Vert./no Cap | 441489.81 | 7802265.02 | 240.8334 | -96.1964 | 1.8288 | 240 | 73.152 | 240 | 73.152 | 410 | 483.15 | 52 | 15.8496 | 10 | 3.048 | 0.4 | 4.8427 | 4.8427 | 3.8362 | 5.5998 | 5.5998 | 0.54634 | 0.45801 | 0.54634 | 0.45801 | 0.22244 | 0.22244 | 0.18168 | 1.3325 | 1.3325 | 1.0884 | Turbine | Gas | 0 | 0.15728 | 0.15728 | 0.38906 | 0.38906
3B | Train 3b Treated Gas Compressor Turbine Primary Stack1 | Vert./no Cap | 441523.94 | 7802269.8 | 240.8665 | -96.1873 | 1.8288 | 240 | 73.152 | 240 | 73.152 | 410 | 483.15 | 52 | 15.8496 | 10 | 3.048 | 0.4 | 4.8427 | 4.8427 | 3.8362 | 5.5998 | 5.5998 | 0.54634 | 0.45801 | 0.54634 | 0.45801 | 0.22244 | 0.22244 | 0.18168 | 1.3325 | 1.3325 | 1.0884 | Turbine | Gas | 0 | 0.15728 | 0.15728 | 0.38906 | 0.38906
4A | Train 1a CO2 Compressor Turbine Primary Stack1 | Vert./no Cap | 441721.04 | 7802288.18 | 241.0588 | -96.1433 | 1.8288 | 240 | 73.152 | 240 | 73.152 | 410 | 483.15 | 41 | 12.4968 | 10 | 3.048 | 0.2 | 3.5028 | 3.5028 | 2.9037 | 4.1071 | 4.1071 | 0.39354 | 0.34483 | 0.39354 | 0.34483 | 0.15874 | 0.15874 | 0.13688 | 0.95098 | 0.95098 | 0.81997 | Turbine | Gas | 0 | 0.11329 | 0.11329 | 0.28025 | 0.28025
4B | Train 1b CO2 Compressor Turbine Primary Stack1 | Vert./no Cap | 441753.31 | 7802294.87 | 241.0898 | -96.1324 | 1.8288 | 240 | 73.152 | 240 | 73.152 | 410 | 483.15 | 41 | 12.4968 | 10 | 3.048 | 0.2 | 3.5028 | 3.5028 | 2.9037 | 4.1071 | 4.1071 | 0.39354 | 0.34483 | 0.39354 | 0.34483 | 0.15874 | 0.15874 | 0.13688 | 0.95098 | 0.95098 | 0.81997 | Turbine | Gas | 0 | 0.11329 | 0.11329 | 0.28025 | 0.28025
5A | Train 2a CO2 Compressor Turbine Primary Stack1 | Vert./no Cap | 441392.32 | 7802127.98 | 240.755 | -96.3447 | 1.8288 | 240 | 73.152 | 240 | 73.152 | 410 | 483.15 | 41 | 12.4968 | 10 | 3.048 | 0.2 | 3.5028 | 3.5028 | 2.9037 | 4.1071 | 4.1071 | 0.39354 | 0.34483 | 0.39354 | 0.34483 | 0.15874 | 0.15874 | 0.13688 | 0.95098 | 0.95098 | 0.81997 | Turbine | Gas | 0 | 0.11329 | 0.11329 | 0.28025 | 0.28025
5B | Train 2b CO2 Compressor Turbine Primary Stack1 | Vert./no Cap | 441426.3 | 7802135.49 | 240.7876 | -96.3328 | 1.8288 | 240 | 73.152 | 240 | 73.152 | 410 | 483.15 | 41 | 12.4968 | 10 | 3.048 | 0.2 | 3.5028 | 3.5028 | 2.9037 | 4.1071 | 4.1071 | 0.39354 | 0.34483 | 0.39354 | 0.34483 | 0.15874 | 0.15874 | 0.13688 | 0.95098 | 0.95098 | 0.81997 | Turbine | Gas | 0 | 0.11329 | 0.11329 | 0.28025 | 0.28025
6A | Train 3a CO2 Compressor Turbine Primary Stack1 | Vert./no Cap | 441370.37 | 7802235.9 | 240.7192 | -96.2409 | 1.8288 | 240 | 73.152 | 240 | 73.152 | 410 | 483.15 | 41 | 12.4968 | 10 | 3.048 | 0.2 | 3.5028 | 3.5028 | 2.9037 | 4.1071 | 4.1071 | 0.39354 | 0.34483 | 0.39354 | 0.34483 | 0.15874 | 0.15874 | 0.13688 | 0.95098 | 0.95098 | 0.81997 | Turbine | Gas | 0 | 0.11329 | 0.11329 | 0.28025 | 0.28025
6B | Train 3b CO2 Compressor Turbine Primary Stack1 | Vert./no Cap | 441403.41 | 7802241.7 | 240.7511 | -96.2308 | 1.8288 | 240 | 73.152 | 240 | 73.152 | 410 | 483.15 | 41 | 12.4968 | 10 | 3.048 | 0.2 | 3.5028 | 3.5028 | 2.9037 | 4.1071 | 4.1071 | 0.39354 | 0.34483 | 0.39354 | 0.34483 | 0.15874 | 0.15874 | 0.13688 | 0.95098 | 0.95098 | 0.81997 | Turbine | Gas | 0 | 0.11329 | 0.11329 | 0.28025 | 0.28025
7A_1A | Power Generator Turbines | Vert./no Cap | 441683.89 | 7802104.89 | 241.0461 | -96.3293 | 1.8288 | 240 | 73.152 | 240 | 73.152 | 871 | 739.2611 | 83 | 25.2984 | 10 | 3.048 | 0.4 | 1.6148 | 1.6148 | 1.5798 | 2.7307 | 2.7307 | 0.36703 | 0.33893 | 0.36703 | 0.33893 | 0.13225 | 0.13225 | 0.12179 | 0.79228 | 0.79228 | 0.72961 | Turbine | Gas | 0 | 0.10566 | 0.10566 | 0.26137 | 0.26137
7A_1B | Power Generator Turbines | Vert./no Cap | 441728.16 | 7802114.5 | 241.0886 | -96.314 | 1.8288 | 240 | 73.152 | 240 | 73.152 | 871 | 739.2611 | 83 | 25.2984 | 10 | 3.048 | 0.4 | 1.6148 | 1.6148 | 1.5798 | 2.7307 | 2.7307 | 0.36703 | 0.33893 | 0.36703 | 0.33893 | 0.13225 | 0.13225 | 0.12179 | 0.79228 | 0.79228 | 0.72961 | Turbine | Gas | 0 | 0.10566 | 0.10566 | 0.26137 | 0.26137
7A_2A | Power Generator Turbines | Vert./no Cap | 441468.06 | 7802061.38 | 240.8386 | -96.4006 | 1.8288 | 240 | 73.152 | 240 | 73.152 | 871 | 739.2611 | 83 | 25.2984 | 10 | 3.048 | 0.4 | 1.6148 | 1.6148 | 1.5798 | 2.7307 | 2.7307 | 0.36703 | 0.33893 | 0.36703 | 0.33893 | 0.13225 | 0.13225 | 0.12179 | 0.79228 | 0.79228 | 0.72961 | Turbine | Gas | 0 | 0.10566 | 0.10566 | 0.26137 | 0.26137
7A_2B | Power Generator Turbines | Vert./no Cap | 441514.13 | 7802070.8 | 240.8829 | -96.3853 | 1.8288 | 240 | 73.152 | 240 | 73.152 | 871 | 739.2611 | 83 | 25.2984 | 10 | 3.048 | 0.4 | 1.6148 | 1.6148 | 1.5798 | 2.7307 | 2.7307 | 0.36703 | 0.33893 | 0.36703 | 0.33893 | 0.13225 | 0.13225 | 0.12179 | 0.79228 | 0.79228 | 0.72961 | Turbine | Gas | 0 | 0.10566 | 0.10566 | 0.26137 | 0.26137
7A_3A | Power Generator Turbines | Vert./no Cap | 441569.32 | 7802082.04 | 240.9359 | -96.3669 | 1.8288 | 240 | 73.152 | 240 | 73.152 | 871 | 739.2611 | 83 | 25.2984 | 10 | 3.048 | 0.4 | 1.6148 | 1.6148 | 1.5798 | 2.7307 | 2.7307 | 0.36703 | 0.33893 | 0.36703 | 0.33893 | 0.13225 | 0.13225 | 0.12179 | 0.79228 | 0.79228 | 0.72961 | Turbine | Gas | 0 | 0.10566 | 0.10566 | 0.26137 | 0.26137
7A_3B | Power Generator Turbines | Vert./no Cap | 441613.4 | 7802091.54 | 240.9782 | -96.3518 | 1.8288 | 240 | 73.152 | 240 | 73.152 | 871 | 739.2611 | 83 | 25.2984 | 10 | 3.048 | 0.4 | 1.6148 | 1.6148 | 1.5798 | 2.7307 | 2.7307 | 0.36703 | 0.33893 | 0.36703 | 0.33893 | 0.13225 | 0.13225 | 0.12179 | 0.79228 | 0.79228 | 0.72961 | Turbine | Gas | 0 | 0.10566 | 0.10566 | 0.26137 | 0.26137
Diesel Equipment
9_1 | Black Start Diesel Generator (2500 kW)2 | Vert./no Cap | 441618.73 | 7802154.47 | 240.9752 | -96.2889 | 1.8288 | 115 | 35.052 | 115 | 35.052 | 879 | 743.7056 | 68 | 20.7264 | 2.5 | 0.762 | 0.5 | 0.26251 | 4.5991 | 0.26251 | 4.5991 | 4.5991 | 0.052561 | 0.0030001 | 0.042049 | 0.0024001 | 0.00027019 | 0.0047337 | 0.00027019 | N/A | N/A | N/A | Generator | Diesel | 0 | 0.036226 | 0.045498 | 0.0058234 | 0.0070632
31A | Main Diesel Firewater Pump (250 hp)2 | Vert./no Cap | 440709.65 | 7803298.16 | 239.9273 | -95.2772 | 1.8288 | 76 | 23.1648 | 76 | 23.1648 | 850 | 727.5944 | 35.5413 | 10.833 | 1 | 0.3048 | 0.5 | 0.017651 | 0.30924 | 0.017651 | 0.28212 | 0.28212 | 0.016276 | 0.000929 | 0.013021 | 0.0007432 | 2.0947e-05 | 0.00036699 | 2.0947e-05 | N/A | N/A | N/A | Pump | Diesel | 0 | 0.011218 | 0.014089 | 0.0018032 | 0.0021872
31B | Main Diesel Firewater Pump (250 hp)2 | Vert./no Cap | 440733.3 | 7803462.72 | 239.9291 | -95.1115 | 1.8288 | 76 | 23.1648 | 76 | 23.1648 | 850 | 727.5944 | 35.5413 | 10.833 | 1 | 0.3048 | 0.5 | 0.017651 | 0.30924 | 0.017651 | 0.28212 | 0.28212 | 0.016276 | 0.000929 | 0.013021 | 0.0007432 | 2.0947e-05 | 0.00036699 | 2.0947e-05 | N/A | N/A | N/A | Pump | Diesel | 0 | 0.011218 | 0.014089 | 0.0018032 | 0.0021872
31C | Main Diesel Firewater Pump (250 hp)2 | Vert./no Cap | 440738.35 | 7803589.7 | 239.9174 | -94.9853 | 1.8288 | 76 | 23.1648 | 76 | 23.1648 | 850 | 727.5944 | 35.5413 | 10.833 | 1 | 0.3048 | 0.5 | 0.017651 | 0.30924 | 0.017651 | 0.28212 | 0.28212 | 0.016276 | 0.000929 | 0.013021 | 0.0007432 | 2.0947e-05 | 0.00036699 | 2.0947e-05 | N/A | N/A | N/A | Pump | Diesel | 0 | 0.011218 | 0.014089 | 0.0018032 | 0.0021872
33 | Dormitory Emergency Diesel Generator (250 kW)2 | Vert./no Cap | 440714.68 | 7803289.84 | 239.9333 | -95.2848 | 1.8288 | 76 | 23.1648 | 76 | 23.1648 | 852 | 728.7056 | 48 | 14.6304 | 1 | 0.3048 | 0.5 | 0.023535 | 0.41233 | 0.023535 | 0.37977 | 0.37977 | 0.021701 | 0.0012387 | 0.017361 | 0.00099093 | 2.809e-05 | 0.00049214 | 2.809e-05 | N/A | N/A | N/A | Generator | Diesel | 0 | 0.014957 | 0.018785 | 0.0024043 | 0.0029162
36 | Communications Tower Diesel Generator (150 kW)2 | Vert./no Cap | 440690.81 | 7803243.08 | 239.9159 | -95.3342 | 1.8288 | 29 | 8.8392 | 29 | 8.8392 | 850 | 727.5944 | 28.597 | 8.7164 | 1 | 0.3048 | 0.5 | 0.014121 | 0.2474 | 0.014121 | 0.22786 | 0.22786 | 0.013021 | 0.0007432 | 0.010417 | 0.00059456 | 1.6854e-05 | 0.00029528 | 1.6854e-05 | N/A | N/A | N/A | Generator | Diesel | 0 | 0.0089741 | 0.011271 | 0.0014426 | 0.0017497
Flares
10E | LP CO2 Flare East Pilot/Purge (3 Flare Tips) | Vert./no Cap | 441601.84 | 7802718.49 | 240.8846 | -95.7335 | 1.8288 | 220 | 67.056 | 220.6705 | 67.2604 | 1831.73 | 1273 | 65.6168 | 20 | 1.4352 | 0.43746 | 0.5 | 0.05852 | 0.05852 | 0.05852 | 0.26678 | 0.26678 | 0.024286 | 0.024286 | 0.024286 | 0.024286 | 0.0021585 | 0.0021585 | 0.0021585 | 0.012931 | 0.012931 | 0.012931 | Flare | Gas | 0 | 0.0060715 | 0.0060715 | 0.018215 | 0.018215
10W | LP CO2 Flare West Pilot/Purge (3 Flare Tips) | Vert./no Cap | 441335.91 | 7802643.1 | 240.6318 | -95.8428 | 1.8288 | 220 | 67.056 | 220.6705 | 67.2604 | 1831.73 | 1273 | 65.6168 | 20 | 1.4352 | 0.43746 | 0.5 | 0.05852 | 0.05852 | 0.05852 | 0.26678 | 0.26678 | 0.024286 | 0.024286 | 0.024286 | 0.024286 | 0.0021585 | 0.0021585 | 0.0021585 | 0.012931 | 0.012931 | 0.012931 | Flare | Gas | 0 | 0.0060715 | 0.0060715 | 0.018215 | 0.018215
11E | HP CO2 Flare East Pilot/Purge | Vert./no Cap | 441601.72 | 7802711.65 | 240.8854 | -95.7402 | 1.8288 | 220 | 67.056 | 218.2302 | 66.5165 | 1831.73 | 1273 | 65.6168 | 20 | 0.94542 | 0.28816 | 0.5 | 0.025392 | 0.025392 | 0.025392 | 0.11576 | 0.11576 | 0.010538 | 0.010538 | 0.010538 | 0.010538 | 0.00093659 | 0.00093659 | 0.00093659 | 0.0056107 | 0.0056107 | 0.0056107 | Flare | Gas | 0 | 0.0026345 | 0.0026345 | 0.0079034 | 0.0079034
11W | HP CO2 Flare West Pilot/Purge | Vert./no Cap | 441335.9 | 7802648.61 | 240.6311 | -95.8374 | 1.8288 | 220 | 67.056 | 218.2302 | 66.5165 | 1831.73 | 1273 | 65.6168 | 20 | 0.94542 | 0.28816 | 0.5 | 0.025392 | 0.025392 | 0.025392 | 0.11576 | 0.11576 | 0.010538 | 0.010538 | 0.010538 | 0.010538 | 0.00093659 | 0.00093659 | 0.00093659 | 0.0056107 | 0.0056107 | 0.0056107 | Flare | Gas | 0 | 0.0026345 | 0.0026345 | 0.0079034 | 0.0079034
12E | HP Hydrocarbon Flare East Pilot/Purge | Vert./no Cap | 441601.9 | 7802705.72 | 240.8864 | -95.7461 | 1.8288 | 220 | 67.056 | 221.1799 | 67.4156 | 1831.73 | 1273 | 65.6168 | 20 | 1.5385 | 0.46894 | 0.5 | 0.067245 | 0.067245 | 0.067245 | 0.30656 | 0.30656 | 0.027907 | 0.027907 | 0.027907 | 0.027907 | 0.0024803 | 0.0024803 | 0.0024803 | 0.014859 | 0.014859 | 0.014859 | Flare | Gas | 0 | 0.0069767 | 0.0069767 | 0.02093 | 0.02093
12W | HP Hydrocarbon Flare West Pilot/Purge | Vert./no Cap | 441335.95 | 7802655.24 | 240.6302 | -95.8308 | 1.8288 | 220 | 67.056 | 221.1799 | 67.4156 | 1831.73 | 1273 | 65.6168 | 20 | 1.5385 | 0.46894 | 0.5 | 0.067245 | 0.067245 | 0.067245 | 0.30656 | 0.30656 | 0.027907 | 0.027907 | 0.027907 | 0.027907 | 0.0024803 | 0.0024803 | 0.0024803 | 0.014859 | 0.014859 | 0.014859 | Flare | Gas | 0 | 0.0069767 | 0.0069767 | 0.02093 | 0.02093
13E | LP Hydrocarbon Flare East Pilot/Purge | Vert./no Cap | 441601.77 | 7802699.63 | 240.887 | -95.7521 | 1.8288 | 220 | 67.056 | 216.775 | 66.073 | 1831.73 | 1273 | 65.6168 | 20 | 0.65836 | 0.20067 | 0.5 | 0.012313 | 0.012313 | 0.012313 | 0.056135 | 0.056135 | 0.0051101 | 0.0051101 | 0.0051101 | 0.0051101 | 0.00045418 | 0.00045418 | 0.00045418 | 0.0027208 | 0.0027208 | 0.0027208 | Flare | Gas | 0 | 0.0012775 | 0.0012775 | 0.0038326 | 0.0038326
13W | LP Hydrocarbon Flare West Pilot/Purge | Vert./no Cap | 441335.94 | 7802661.87 | 240.6294 | -95.8243 | 1.8288 | 220 | 67.056 | 216.775 | 66.073 | 1831.73 | 1273 | 65.6168 | 20 | 0.65836 | 0.20067 | 0.5 | 0.012313 | 0.012313 | 0.012313 | 0.056135 | 0.056135 | 0.0051101 | 0.0051101 | 0.0051101 | 0.0051101 | 0.00045418 | 0.00045418 | 0.00045418 | 0.0027208 | 0.0027208 | 0.0027208 | Flare | Gas | 0 | 0.0012775 | 0.0012775 | 0.0038326 | 0.0038326
10E_M | LP CO2 Flare East MAX2 (3 Flare Tips) | Vert./no Cap | 441601.84 | 7802718.49 | 240.8846 | -95.7335 | 1.8288 | 220 | 67.056 | 450.6457 | 137.3568 | 1831.73 | 1273 | 65.6168 | 20 | 53.8895 | 16.4255 | 0.5 | 4.7094 | 1.7189 | 4.7094 | 188.0699 | 23.5087 | 0.71335 | 1.9544 | 0.71335 | 1.9544 | 0.56726 | 1.6564 | 0.56726 | 3.3983 | 9.923 | 3.3983 | Flare | Gas | 0 | 0.17834 | 0.17834 | 0.53502 | 0.53502
11E_M | HP CO2 Flare East MAX2 | Vert./no Cap | 441601.72 | 7802711.65 | 240.8854 | -95.7402 | 1.8288 | 220 | 67.056 | 352.5058 | 107.4438 | 1831.73 | 1273 | 65.6168 | 20 | 30.8444 | 9.4014 | 0.5 | 1.5426 | 0.56307 | 1.5426 | 61.6061 | 7.7008 | 0.23367 | 0.6402 | 0.23367 | 0.6402 | 0.18584 | 0.54266 | 0.18584 | 1.1133 | 3.2509 | 1.1133 | Flare | Gas | 0 | 0.058418 | 0.058418 | 0.17526 | 0.17526
12E_M | HP Hydrocarbon Flare East MAX2 | Vert./no Cap | 441601.9 | 7802705.72 | 240.8864 | -95.7461 | 1.8288 | 220 | 67.056 | 839.7912 | 255.9683 | 1831.73 | 1273 | 65.6168 | 20 | 148.7253 | 45.3315 | 0.5 | 35.8495 | 13.0851 | 35.8495 | 1431.6611 | 178.9576 | 5.4303 | 14.8776 | 5.4303 | 14.8776 | 1.4851 | 4.3365 | 1.4851 | 8.8968 | 25.9785 | 8.8968 | Flare | Gas | 0 | 1.3576 | 1.3576 | 4.0727 | 4.0727
13E_M | LP Hydrocarbon Flare East MAX2 | Vert./no Cap | 441601.77 | 7802699.63 | 240.887 | -95.7521 | 1.8288 | 220 | 67.056 | 378.2164 | 115.2804 | 1831.73 | 1273 | 65.6168 | 20 | 36.8254 | 11.2244 | 0.5 | 2.199 | 0.80262 | 2.199 | 87.8162 | 10.977 | 0.33309 | 0.91257 | 0.33309 | 0.91257 | 0.081154 | 0.23697 | 0.081154 | 0.48616 | 1.4196 | 0.48616 | Flare | Gas | 0 | 0.083272 | 0.083272 | 0.24982 | 0.24982
Heaters and Incinerators
14_1 | Building Heat Medium Heater | Vert./no Cap | 441702.17 | 7802020.12 | 241.0753 | -96.4107 | 1.8288 | 232 | 70.7136 | 232 | 70.7136 | 370 | 460.9278 | 26 | 7.9248 | 9 | 2.7432 | 0.5 | 1.2462 | 1.2462 | 1.2462 | 0.24232 | 0.24232 | 0.25793 | 0.25793 | 0.25793 | 0.25793 | 0.086792 | 0.086792 | 0.086792 | 0.51994 | 0.51994 | 0.51994 | Heater | Gas | 0 | 0.064483 | 0.064483 | 0.19345 | 0.19345
14_2 | Building Heat Medium Heater | Vert./no Cap | 441697.18 | 7802044.48 | 241.0671 | -96.3873 | 1.8288 | 232 | 70.7136 | 232 | 70.7136 | 370 | 460.9278 | 26 | 7.9248 | 9 | 2.7432 | 0.5 | 1.2462 | 1.2462 | 1.2462 | 0.24232 | 0.24232 | 0.25793 | 0.25793 | 0.25793 | 0.25793 | 0.086792 | 0.086792 | 0.086792 | 0.51994 | 0.51994 | 0.51994 | Heater | Gas | 0 | 0.064483 | 0.064483 | 0.19345 | 0.19345
14_3 | Building Heat Medium Heater (Spare) | Vert./no Cap | 441692.46 | 7802069.05 | 241.0593 | -96.3636 | 1.8288 | 232 | 70.7136 | 232 | 70.7136 | 370 | 460.9278 | 26 | 7.9248 | 9 | 2.7432 | 0.5
21A | Buyback Gas Bath Heater Primary Heater Standby | Vert./no Cap | 441654.1 | 7802479.72 | 240.9675 | -95.9627 | 1.8288 | 20 | 6.096 | 20 | 6.096 | 601 | 589.2611 | 0.33 | 0.10058 | 2 | 0.6096 | 0.5 | 0.00069788 | 0.00069788 | 0.00069788 | 0.0015965 | 0.0015965 | 0.00014444 | 0.00014444 | 0.00014444 | 0.00014444 | 5.1662e-05 | 5.1662e-05 | 5.1662e-05 | 0.00030949 | 0.00030949 | 0.00030949 | Heater | Gas | 0 | 3.611e-05 | 3.611e-05 | 0.00010833 | 0.00010833
21B | Buyback Gas Bath Heater Secondary Heater Standby | Vert./no Cap | 441652.81 | 7802486.16 | 240.9654 | -95.9565 | 1.8288 | 20 | 6.096 | 20 | 6.096 | 887 | 748.15 | 0.41 | 0.12497 | 2 | 0.6096 | 0.5 | 0.00069788 | 0.00069788 | 0.00069788 | 0.0015965 | 0.0015965 | 0.00014444 | 0.00014444 | 0.00014444 | 0.00014444 | 5.1662e-05 | 5.1662e-05 | 5.1662e-05 | 0.00030949 | 0.00030949 | 0.00030949 | Heater | Gas | 0 | 3.611e-05 | 3.611e-05 | 0.00010833 | 0.00010833
21A_M | Buyback Gas Bath Heater Primary Heater MAX2 | Vert./no Cap | 441654.1 | 7802479.72 | 240.9675 | -95.9627 | 1.8288 | 20 | 6.096 | 20 | 6.096 | 601 | 589.2611 | 54.79 | 16.7 | 2 | 0.6096 | 0.5 | 0.0065554 | 0.11485 | 0.0065554 | 0.26273 | 0.26273 | 0.023771 | 0.0013568 | 0.023771 | 0.0013568 | 0.00045705 | 0.0080076 | 0.00045705 | 0.002738 | 0.04797 | 0.002738 | Heater | Gas | 0 | 0.0059427 | 0.0059427 | 0.017828 | 0.017828
21B_M | Buyback Gas Bath Heater Secondary Heater MAX2 | Vert./no Cap | 441652.81 | 7802486.16 | 240.9654 | -95.9565 | 1.8288 | 20 | 6.096 | 20 | 6.096 | 887 | 748.15 | 57.49 | 17.523 | 2 | 0.6096 | 0.5 | 0.0054173 | 0.094912 | 0.0054173 | 0.21712 | 0.21712 | 0.019644 | 0.0011212 | 0.019644 | 0.0011212 | 0.00037744 | 0.0066127 | 0.00037744 | 0.0022611 | 0.039614 | 0.0022611 | Heater | Gas | 0 | 0.004911 | 0.004911 | 0.014733 | 0.014733
CAMPHT1 | Operations Camp Heater | Vert./no Cap | 440958.059 | 7803537.002 | 241.1576 | -95.3446 | 1.8288 | 32 | 9.7536 | 32 | 9.7536 | 257 | 398.15 | 29 | 8.8392 | 2.5 | 0.762 | 0.5 | 0.14456 | 0.14456 | 0.14456 | 0.3307 | 0.3307 | 0.02992 | 0.02992 | 0.02992 | 0.02992 | 0.010203 | 0.010203 | 0.010203 | 0.061123 | 0.061123 | 0.061123 | Heater | Gas | 0 | 0.00748 | 0.00748 | 0.02244 | 0.02244
CAMPHT2 | Operations Camp Heater | Vert./no Cap | 440961.234 | 7803523.243 | 241.1626 | -95.3578 | 1.8288 | 32 | 9.7536 | 32 | 9.7536 | 257 | 398.15 | 29 | 8.8392 | 2.5 | 0.762 | 0.5 | 0.14456 | 0.14456 | 0.14456 | 0.3307 | 0.3307 | 0.02992 | 0.02992 | 0.02992 | 0.02992 | 0.010203 | 0.010203 | 0.010203 | 0.061123 | 0.061123 | 0.061123 | Heater | Gas | 0 | 0.00748 | 0.00748 | 0.02244 | 0.02244
CAMPHT3 | Operations Camp Heater (Spare) | Vert./no Cap | 440964.409 | 7803508.691 | 241.1676 | -95.3719 | 1.8288 | 32 | 9.7536 | 32 | 9.7536 | 257 | 398.15 | 29 | 8.8392 | 2.5 | 0.762 | 0.5
Total Emissions (Without Maximum Flare) | [18 empty] | 63.2371 | 69.2683 | 53.3931 | 83.7985 | 83.7985 | 8.7327 | 7.5725 | 8.7054 | 7.571 | 3.288 | 3.308 | 2.8495 | 19.6948 | 19.7774 | 17.0678
Total Emissions (With Maximum Flare) | [18 empty] | 107.5375 | 85.438 | 97.6936 | 1852.9518 | 304.9427 | 15.4431 | 25.9573 | 15.4159 | 25.9557 | 5.6074 | 10.0806 | 5.1688 | 33.5893 | 60.3493 | 30.9623
NOTES
500 | hours Intermittent Diesel Equipment has been modeled with an annual value based on operating only 500 hours/year.
500 | hours Maximum Flaring Events have been modeled with an annual value based on operating only 500 hours/year.
8760 | hours Annual hours
0.5 | hours Per day maximum flare operation
1 | Supplemental Firing emissions have been included in the total emissions from the turbine source. To be conservative, the additional supplemental firing flow rate and velocity have not been included in the stack parameter selection
2 | Intermittent equipment 1-hr NOx and SO2 emissions can be annualized

## GTP Potential to Emit
PTE SUMMARY
Model ID | Source Description | Annual Operating Hours | Potential to Emit (PTE) Emission Rates
|  |  | NOx |  | CO |  |  | VOC |  | PM10 |  |  | PM2.5 |  |  | SO2 @ 16 ppmvd |  |  | SO2 @ 96 ppmvd1 |  |  |  | CO2 |  | CH4 |  | N2O |  | CO2e | HAPs (Formaldehyde) |  | HAPs (Total)
|  |  | lb/hr | tpy | lb/hr | lb/8-hr | tpy | lb/hr | tpy | lb/hr | lb/day | tpy | lb/hr | lb/day | tpy | lb/hr | lb/day | tpy | lb/hr | lb/day | tpy | lb/hr | tonnes/yr | lb/hr | tonnes/yr | lb/hr | tonnes/yr | lb/hr | tonnes/yr | lb/hr | tpy | lb/hr | tpy
1A | Train 1a Treated Gas Compressor Turbine Primary Stack (includes SF WHR) | 8760 | 38.4352 | 133.3556 | 44.4439 | 355.5512 | 159.1029 | 5.1964 | 16.1677 | 4.3361 | 104.0675 | 15.9217 | 4.3361 | 104.0675 | 15.9217 | 1.7654 | 42.37 | 6.3158 | 10.5759 | 253.8227 | 37.8355 | 82191.5687 | 267274.603 | 1.549 | 5.0372 | 0.1549 | 0.50372 | 82276.4556 | 267550.6424 | 0.39618 | 1.7353 | 0.57325 | 2.5108
1B | Train 1b Treated Gas Compressor Turbine Primary Stack (includes SF WHR) | 8760 | 38.4352 | 133.3556 | 44.4439 | 355.5512 | 159.1029 | 5.1964 | 16.1677 | 4.3361 | 104.0675 | 15.9217 | 4.3361 | 104.0675 | 15.9217 | 1.7654 | 42.37 | 6.3158 | 10.5759 | 253.8227 | 37.8355 | 82191.5687 | 267274.603 | 1.549 | 5.0372 | 0.1549 | 0.50372 | 82276.4556 | 267550.6424 | 0.39618 | 1.7353 | 0.57325 | 2.5108
2A | Train 2a Treated Gas Compressor Turbine Primary Stack (includes SF WHR) | 8760 | 38.4352 | 133.3556 | 44.4439 | 355.5512 | 159.1029 | 5.1964 | 16.1677 | 4.3361 | 104.0675 | 15.9217 | 4.3361 | 104.0675 | 15.9217 | 1.7654 | 42.37 | 6.3158 | 10.5759 | 253.8227 | 37.8355 | 82191.5687 | 267274.603 | 1.549 | 5.0372 | 0.1549 | 0.50372 | 82276.4556 | 267550.6424 | 0.39618 | 1.7353 | 0.57325 | 2.5108
2B | Train 2b Treated Gas Compressor Turbine Primary Stack (includes SF WHR) | 8760 | 38.4352 | 133.3556 | 44.4439 | 355.5512 | 159.1029 | 5.1964 | 16.1677 | 4.3361 | 104.0675 | 15.9217 | 4.3361 | 104.0675 | 15.9217 | 1.7654 | 42.37 | 6.3158 | 10.5759 | 253.8227 | 37.8355 | 82191.5687 | 267274.603 | 1.549 | 5.0372 | 0.1549 | 0.50372 | 82276.4556 | 267550.6424 | 0.39618 | 1.7353 | 0.57325 | 2.5108
3A | Train 3a Treated Gas Compressor Turbine Primary Stack (includes SF WHR) | 8760 | 38.4352 | 133.3556 | 44.4439 | 355.5512 | 159.1029 | 5.1964 | 16.1677 | 4.3361 | 104.0675 | 15.9217 | 4.3361 | 104.0675 | 15.9217 | 1.7654 | 42.37 | 6.3158 | 10.5759 | 253.8227 | 37.8355 | 82191.5687 | 267274.603 | 1.549 | 5.0372 | 0.1549 | 0.50372 | 82276.4556 | 267550.6424 | 0.39618 | 1.7353 | 0.57325 | 2.5108
3B | Train3b Treated Gas Compressor Turbine Primary Stack (includes SF WHR) | 8760 | 38.4352 | 133.3556 | 44.4439 | 355.5512 | 159.1029 | 5.1964 | 16.1677 | 4.3361 | 104.0675 | 15.9217 | 4.3361 | 104.0675 | 15.9217 | 1.7654 | 42.37 | 6.3158 | 10.5759 | 253.8227 | 37.8355 | 82191.5687 | 267274.603 | 1.549 | 5.0372 | 0.1549 | 0.50372 | 82276.4556 | 267550.6424 | 0.39618 | 1.7353 | 0.57325 | 2.5108
4A | Train 1a CO2 Compressor Turbine Primary Stack (includes SF WHR) | 8760 | 27.8007 | 100.9416 | 32.5967 | 260.7733 | 120.6069 | 3.5579 | 12.1404 | 3.1234 | 74.962 | 11.9871 | 3.1234 | 74.962 | 11.9871 | 1.2599 | 30.2376 | 4.7582 | 7.5476 | 181.1421 | 28.5043 | 58748.0114 | 201153.1606 | 1.1072 | 3.7911 | 0.11072 | 0.37911 | 58808.6859 | 201360.9102 | 0.2982 | 1.3061 | 0.43148 | 1.8899
4B | Train 1b CO2 Compressor Turbine Primary Stack (includes SF WHR) | 8760 | 27.8007 | 100.9416 | 32.5967 | 260.7733 | 120.6069 | 3.5579 | 12.1404 | 3.1234 | 74.962 | 11.9871 | 3.1234 | 74.962 | 11.9871 | 1.2599 | 30.2376 | 4.7582 | 7.5476 | 181.1421 | 28.5043 | 58748.0114 | 201153.1606 | 1.1072 | 3.7911 | 0.11072 | 0.37911 | 58808.6859 | 201360.9102 | 0.2982 | 1.3061 | 0.43148 | 1.8899
5A | Train 2a CO2 Compressor Turbine Primary Stack (includes SF WHR) | 8760 | 27.8007 | 100.9416 | 32.5967 | 260.7733 | 120.6069 | 3.5579 | 12.1404 | 3.1234 | 74.962 | 11.9871 | 3.1234 | 74.962 | 11.9871 | 1.2599 | 30.2376 | 4.7582 | 7.5476 | 181.1421 | 28.5043 | 58748.0114 | 201153.1606 | 1.1072 | 3.7911 | 0.11072 | 0.37911 | 58808.6859 | 201360.9102 | 0.2982 | 1.3061 | 0.43148 | 1.8899
5B | Train 2b CO2 Compressor Turbine Primary Stack (includes SF WHR) | 8760 | 27.8007 | 100.9416 | 32.5967 | 260.7733 | 120.6069 | 3.5579 | 12.1404 | 3.1234 | 74.962 | 11.9871 | 3.1234 | 74.962 | 11.9871 | 1.2599 | 30.2376 | 4.7582 | 7.5476 | 181.1421 | 28.5043 | 58748.0114 | 201153.1606 | 1.1072 | 3.7911 | 0.11072 | 0.37911 | 58808.6859 | 201360.9102 | 0.2982 | 1.3061 | 0.43148 | 1.8899
6A | Train 3a CO2 Compressor Turbine Primary Stack (includes SF WHR) | 8760 | 27.8007 | 100.9416 | 32.5967 | 260.7733 | 120.6069 | 3.5579 | 12.1404 | 3.1234 | 74.962 | 11.9871 | 3.1234 | 74.962 | 11.9871 | 1.2599 | 30.2376 | 4.7582 | 7.5476 | 181.1421 | 28.5043 | 58748.0114 | 201153.1606 | 1.1072 | 3.7911 | 0.11072 | 0.37911 | 58808.6859 | 201360.9102 | 0.2982 | 1.3061 | 0.43148 | 1.8899
6B | Train 3b CO2 Compressor Turbine Primary Stack (includes SF WHR) | 8760 | 27.8007 | 100.9416 | 32.5967 | 260.7733 | 120.6069 | 3.5579 | 12.1404 | 3.1234 | 74.962 | 11.9871 | 3.1234 | 74.962 | 11.9871 | 1.2599 | 30.2376 | 4.7582 | 7.5476 | 181.1421 | 28.5043 | 58748.0114 | 201153.1606 | 1.1072 | 3.7911 | 0.11072 | 0.37911 | 58808.6859 | 201360.9102 | 0.2982 | 1.3061 | 0.43148 | 1.8899
7A_1A | Power Generation Turbines | 8760 | 12.8163 | 54.9175 | 21.673 | 173.3844 | 92.8687 | 0.92685 | 3.7488 | 2.913 | 69.9112 | 11.7821 | 2.913 | 69.9112 | 11.7821 | 1.0497 | 25.1918 | 4.2338 | 6.2881 | 150.9145 | 25.3633 | 48895.9998 | 179414.9616 | 0.92152 | 3.3814 | 0.092152 | 0.33814 | 48946.4992 | 179600.2601 | 0.27406 | 1.2004 | 0.39655 | 1.7369
7A_1B | Power Generation Turbines | 8760 | 12.8163 | 54.9175 | 21.673 | 173.3844 | 92.8687 | 0.92685 | 3.7488 | 2.913 | 69.9112 | 11.7821 | 2.913 | 69.9112 | 11.7821 | 1.0497 | 25.1918 | 4.2338 | 6.2881 | 150.9145 | 25.3633 | 48895.9998 | 179414.9616 | 0.92152 | 3.3814 | 0.092152 | 0.33814 | 48946.4992 | 179600.2601 | 0.27406 | 1.2004 | 0.39655 | 1.7369
7A_2A | Power Generation Turbines | 8760 | 12.8163 | 54.9175 | 21.673 | 173.3844 | 92.8687 | 0.92685 | 3.7488 | 2.913 | 69.9112 | 11.7821 | 2.913 | 69.9112 | 11.7821 | 1.0497 | 25.1918 | 4.2338 | 6.2881 | 150.9145 | 25.3633 | 48895.9998 | 179414.9616 | 0.92152 | 3.3814 | 0.092152 | 0.33814 | 48946.4992 | 179600.2601 | 0.27406 | 1.2004 | 0.39655 | 1.7369
7A_2B | Power Generation Turbines | 8760 | 12.8163 | 54.9175 | 21.673 | 173.3844 | 92.8687 | 0.92685 | 3.7488 | 2.913 | 69.9112 | 11.7821 | 2.913 | 69.9112 | 11.7821 | 1.0497 | 25.1918 | 4.2338 | 6.2881 | 150.9145 | 25.3633 | 48895.9998 | 179414.9616 | 0.92152 | 3.3814 | 0.092152 | 0.33814 | 48946.4992 | 179600.2601 | 0.27406 | 1.2004 | 0.39655 | 1.7369
7A_3A | Power Generation Turbines | 8760 | 12.8163 | 54.9175 | 21.673 | 173.3844 | 92.8687 | 0.92685 | 3.7488 | 2.913 | 69.9112 | 11.7821 | 2.913 | 69.9112 | 11.7821 | 1.0497 | 25.1918 | 4.2338 | 6.2881 | 150.9145 | 25.3633 | 48895.9998 | 179414.9616 | 0.92152 | 3.3814 | 0.092152 | 0.33814 | 48946.4992 | 179600.2601 | 0.27406 | 1.2004 | 0.39655 | 1.7369
7A_3B | Power Generation Turbines | 8760 | 12.8163 | 54.9175 | 21.673 | 173.3844 | 92.8687 | 0.92685 | 3.7488 | 2.913 | 69.9112 | 11.7821 | 2.913 | 69.9112 | 11.7821 | 1.0497 | 25.1918 | 4.2338 | 6.2881 | 150.9145 | 25.3633 | 48895.9998 | 179414.9616 | 0.92152 | 3.3814 | 0.092152 | 0.33814 | 48946.4992 | 179600.2601 | 0.27406 | 1.2004 | 0.39655 | 1.7369
9_1 | Black Start Diesel Generator (2500 kW) | 500 | 36.5018 | 9.1255 | 36.5018 | 292.0147 | 9.1255 | 1.9815 | 0.49538 | 0.41716 | 10.0119 | 0.10429 | 0.33373 | 8.0095 | 0.083433 | 0.03757 | 0.90167 | 0.0093924 |  |  |  | 4633.944 | 1050.9716 | 1.2341 | 0.04263 | 0 | 0.008526 | 4664.7974 | 1054.5781 | 0.0022423 | 0.00056058 | 0.050744 | 0.012686
31A | Main Diesel Firewater Pump (250 hp) | 500 | 2.4544 | 0.61359 | 2.2391 | 17.9127 | 0.55977 | 0.12918 | 0.032294 | 0.12918 | 3.1003 | 0.032294 | 0.10334 | 2.4802 | 0.025836 | 0.0029127 | 0.069904 | 0.00072817 |  |  |  | 285.3414 | 64.715 | 0.095679 | 0.002625 | 0 | 0.000525 | 287.7334 | 64.9371 | 0.002065 | 0.00051625 | 0.0070733 | 0.0017683
31B | Main Diesel Firewater Pump (250 hp) | 500 | 2.4544 | 0.61359 | 2.2391 | 17.9127 | 0.55977 | 0.12918 | 0.032294 | 0.12918 | 3.1003 | 0.032294 | 0.10334 | 2.4802 | 0.025836 | 0.0029127 | 0.069904 | 0.00072817 |  |  |  | 285.3414 | 64.715 | 0.095679 | 0.002625 | 0 | 0.000525 | 287.7334 | 64.9371 | 0.002065 | 0.00051625 | 0.0070733 | 0.0017683
31C | Main Diesel Firewater Pump (250 hp) | 500 | 2.4544 | 0.61359 | 2.2391 | 17.9127 | 0.55977 | 0.12918 | 0.032294 | 0.12918 | 3.1003 | 0.032294 | 0.10334 | 2.4802 | 0.025836 | 0.0029127 | 0.069904 | 0.00072817 |  |  |  | 285.3414 | 64.715 | 0.095679 | 0.002625 | 0 | 0.000525 | 287.7334 | 64.9371 | 0.002065 | 0.00051625 | 0.0070733 | 0.0017683
33 | Dormitory Emergency Diesel Generator (250 kW) | 500 | 3.2725 | 0.81813 | 3.0141 | 24.1132 | 0.75354 | 0.17224 | 0.043059 | 0.17224 | 4.1337 | 0.043059 | 0.13779 | 3.307 | 0.034447 | 0.0039059 | 0.093743 | 0.00097649 |  |  |  | 382.649 | 86.7842 | 0.12831 | 0.0035202 | 0 | 0.00070404 | 385.8567 | 87.082 | 0.0027692 | 0.0006923 | 0.0094854 | 0.0023713
36 | Communications Tower (150 kW) | 500 | 1.9635 | 0.49088 | 1.8085 | 14.4679 | 0.45212 | 0.10334 | 0.025836 | 0.10334 | 2.4802 | 0.025836 | 0.082674 | 1.9842 | 0.020668 | 0.0023436 | 0.056246 | 0.00058589 |  |  |  | 229.5894 | 52.0705 | 0.076985 | 0.0021121 | 0 | 0.00042242 | 231.514 | 52.2492 | 0.0016615 | 0.00041538 | 0.0056912 | 0.0014228
10E_1 | LP CO2 Flare East Pilot/Purge (3 Flares) | 8760 | 0.46446 | 2.0343 | 2.1174 | 16.9391 | 9.2741 | 3.8933 | 17.0524 | 0.19275 | 4.626 | 0.84425 | 0.19275 | 4.626 | 0.84425 | 0.017131 | 0.41115 | 0.075035 | 0.10263 | 2.4631 | 0.44951 | 798.9774 | 3174.7448 | 0.015058 | 0.059833 | 0.0015058 | 0.0059833 | 799.8026 | 3178.0237 | 0.007828 | 0.034287 | 0.019788 | 0.08667
10W_1 | LP CO2 Flare West Pilot/Purge (3 Flares) | 8760 | 0.46446 | 2.0343 | 2.1174 | 16.9391 | 9.2741 | 3.8933 | 17.0524 | 0.19275 | 4.626 | 0.84425 | 0.19275 | 4.626 | 0.84425 | 0.017131 | 0.41115 | 0.075035 | 0.10263 | 2.4631 | 0.44951 | 798.9774 | 3174.7448 | 0.015058 | 0.059833 | 0.0015058 | 0.0059833 | 799.8026 | 3178.0237 | 0.007828 | 0.034287 | 0.019788 | 0.08667
11E | HP CO2 Flare East Pilot/Purge | 8760 | 0.20153 | 0.8827 | 0.91874 | 7.3499 | 4.0241 | 1.6893 | 7.3991 | 0.083636 | 2.0073 | 0.36632 | 0.083636 | 2.0073 | 0.36632 | 0.0074334 | 0.1784 | 0.032558 | 0.044531 | 1.0687 | 0.19504 | 346.6805 | 1377.5382 | 0.0065337 | 0.025962 | 0.00065337 | 0.0025962 | 347.0385 | 1378.9609 | 0.0033966 | 0.014877 | 0.008586 | 0.037607
11W | HP CO2 Flare West Pilot/Purge | 8760 | 0.20153 | 0.8827 | 0.91874 | 7.3499 | 4.0241 | 1.6893 | 7.3991 | 0.083636 | 2.0073 | 0.36632 | 0.083636 | 2.0073 | 0.36632 | 0.0074334 | 0.1784 | 0.032558 | 0.044531 | 1.0687 | 0.19504 | 346.6805 | 1377.5382 | 0.0065337 | 0.025962 | 0.00065337 | 0.0025962 | 347.0385 | 1378.9609 | 0.0033966 | 0.014877 | 0.008586 | 0.037607
12E | HP Hydrocarbon Flare East Pilot/Purge | 8760 | 0.5337 | 2.3376 | 2.433 | 19.4644 | 10.6567 | 4.4737 | 19.5947 | 0.22149 | 5.3157 | 0.97011 | 0.22149 | 5.3157 | 0.97011 | 0.019685 | 0.47245 | 0.086222 | 0.11793 | 2.8303 | 0.51652 | 918.0912 | 3648.0445 | 0.017303 | 0.068753 | 0.0017303 | 0.0068753 | 919.0394 | 3651.8122 | 0.008995 | 0.039398 | 0.022738 | 0.099591
12W | HP Hydrocarbon Flare West Pilot/Purge | 8760 | 0.5337 | 2.3376 | 2.433 | 19.4644 | 10.6567 | 4.4737 | 19.5947 | 0.22149 | 5.3157 | 0.97011 | 0.22149 | 5.3157 | 0.97011 | 0.019685 | 0.47245 | 0.086222 | 0.11793 | 2.8303 | 0.51652 | 918.0912 | 3648.0445 | 0.017303 | 0.068753 | 0.0017303 | 0.0068753 | 919.0394 | 3651.8122 | 0.008995 | 0.039398 | 0.022738 | 0.099591
13E | LP Hydrocarbon Flare East Pilot/Purge | 8760 | 0.097728 | 0.42805 | 0.44552 | 3.5642 | 1.9514 | 0.81919 | 3.588 | 0.040557 | 0.97337 | 0.17764 | 0.040557 | 0.97337 | 0.17764 | 0.0036046 | 0.086511 | 0.015788 | 0.021594 | 0.51826 | 0.094582 | 168.1146 | 668.005 | 0.0031684 | 0.01259 | 0.00031684 | 0.001259 | 168.2882 | 668.6949 | 0.0016471 | 0.0072143 | 0.0041636 | 0.018236
13W | LP Hydrocarbon Flare West Pilot/Purge | 8760 | 0.097728 | 0.42805 | 0.44552 | 3.5642 | 1.9514 | 0.81919 | 3.588 | 0.040557 | 0.97337 | 0.17764 | 0.040557 | 0.97337 | 0.17764 | 0.0036046 | 0.086511 | 0.015788 | 0.021594 | 0.51826 | 0.094582 | 168.1146 | 668.005 | 0.0031684 | 0.01259 | 0.00031684 | 0.001259 | 168.2882 | 668.6949 | 0.0016471 | 0.0072143 | 0.0041636 | 0.018236
10E_M | LP CO2 Flare East MAX (3 Flares) | 500 | 327.4203 | 163.7102 | 1492.6514 | 1492.6514 | 746.3257 | 2744.5525 | 1372.2763 | 135.8799 | 135.8799 | 67.94 | 135.8799 | 135.8799 | 67.94 | 39.4393 | 39.4393 | 19.7196 | 236.266 | 236.266 | 118.133 | 563240.324 | 255484.135 | 10.6152 | 4.815 | 1.0615 | 0.4815 | 563822.0347 | 255747.9973 | 5.5184 | 2.7592 | 13.9494 | 6.9747
11E_M | HP CO2 Flare East MAX | 500 | 107.2531 | 53.6265 | 488.9478 | 488.9478 | 244.4739 | 899.033 | 449.5165 | 44.5102 | 44.5102 | 22.2551 | 44.5102 | 44.5102 | 22.2551 | 12.9207 | 12.9207 | 6.4604 | 77.4033 | 77.4033 | 38.7017 | 184500.6149 | 83688.9299 | 3.4772 | 1.5773 | 0.34772 | 0.15773 | 184691.1658 | 83775.3633 | 1.8077 | 0.90383 | 4.5694 | 2.2847
12E_M | HP Hydrocarbon Flare East MAX | 500 | 2492.4501 | 1246.2251 | 11362.6404 | 11362.6404 | 5681.3202 | 20892.5968 | 10446.2984 | 1034.3708 | 1034.3708 | 517.1854 | 1034.3708 | 1034.3708 | 517.1854 | 103.2531 | 103.2531 | 51.6265 | 618.5505 | 618.5505 | 309.2753 | 4287603.4933 | 1944844.1864 | 80.8067 | 36.6537 | 8.0807 | 3.6654 | 4292031.7005 | 1946852.808 | 42.008 | 21.004 | 106.1883 | 53.0941
13E_M | LP Hydrocarbon Flare East MAX | 500 | 152.8836 | 76.4418 | 696.9692 | 696.9692 | 348.4846 | 1281.5241 | 640.762 | 63.4469 | 63.4469 | 31.7235 | 63.4469 | 63.4469 | 31.7235 | 5.6422 | 5.6422 | 2.8211 | 33.8006 | 33.8006 | 16.9003 | 262995.8873 | 119294.1519 | 4.9566 | 2.2483 | 0.49566 | 0.22483 | 263267.5076 | 119417.3581 | 2.5767 | 1.2884 | 6.5134 | 3.2567
14_1 | Building Heat Medium Heater | 8760 | 9.8908 | 43.3218 | 1.9232 | 15.3857 | 8.4237 | 1.6485 | 7.2203 | 2.0471 | 49.1309 | 8.9664 | 2.0471 | 49.1309 | 8.9664 | 0.68884 | 16.5321 | 3.0171 | 4.1266 | 99.0376 | 18.0744 | 32138.5801 | 127702.9671 | 0.6057 | 2.4068 | 0.06057 | 0.24068 | 32171.7726 | 127834.8579 | 0.020202 | 0.088484 | 0.50685 | 2.22
14_2 | Building Heat Medium Heater | 8760 | 9.8908 | 43.3218 | 1.9232 | 15.3857 | 8.4237 | 1.6485 | 7.2203 | 2.0471 | 49.1309 | 8.9664 | 2.0471 | 49.1309 | 8.9664 | 0.68884 | 16.5321 | 3.0171 | 4.1266 | 99.0376 | 18.0744 | 32138.5801 | 127702.9671 | 0.6057 | 2.4068 | 0.06057 | 0.24068 | 32171.7726 | 127834.8579 | 0.020202 | 0.088484 | 0.50685 | 2.22
14_3 | Building Heat Medium Heater (spare) | 0
21A | Buyback Gas Bath Heater Primary Heater Standby | 8760 | 0.0055389 | 0.02426 | 0.012671 | 0.10136 | 0.055497 | 0.00092314 | 0.0040434 | 0.0011464 | 0.027513 | 0.0050212 | 0.0011464 | 0.027513 | 0.0050212 | 0.00041002 | 0.0098405 | 0.0017959 | 0.0024563 | 0.058951 | 0.010759 | 17.9976 | 71.5137 | 0.00033919 | 0.0013478 | 3.3919e-05 | 0.00013478 | 18.0162 | 71.5875 | 1.1313e-05 | 4.9551e-05 | 0.00028384 | 0.0012432
21B | Buyback Gas Bath Heater Secondary Heater Standby | 8760 | 0.0055389 | 0.02426 | 0.012671 | 0.10136 | 0.055497 | 0.00092314 | 0.0040434 | 0.0011464 | 0.027513 | 0.0050212 | 0.0011464 | 0.027513 | 0.0050212 | 0.00041002 | 0.0098405 | 0.0017959 | 0.0024563 | 0.058951 | 0.010759 | 17.9976 | 71.5137 | 0.00033919 | 0.0013478 | 3.3919e-05 | 0.00013478 | 18.0162 | 71.5875 | 1.1313e-05 | 4.9551e-05 | 0.00028384 | 0.0012432
21A_M | Buyback Gas Bath Heater Primary Heater MAX | 500 | 0.91154 | 0.22788 | 2.0852 | 16.6817 | 0.5213 | 0.15192 | 0.037981 | 0.18866 | 4.5279 | 0.047166 | 0.18866 | 4.5279 | 0.047166 | 0.063553 | 1.5253 | 0.015888 | 0.38073 | 9.1374 | 0.095181 | 2961.8915 | 671.7526 | 0.055822 | 0.01266 | 0.0055822 | 0.001266 | 2964.9506 | 672.4464 | 0.0018618 | 0.00046545 | 0.046711 | 0.011678
21B_M | Buyback Gas Bath Heater Secondary Heater MAX | 500 | 0.75328 | 0.18832 | 1.7232 | 13.7856 | 0.4308 | 0.12555 | 0.031387 | 0.15591 | 3.7418 | 0.038977 | 0.15591 | 3.7418 | 0.038977 | 0.052483 | 1.2596 | 0.013121 | 0.31441 | 7.5457 | 0.078601 | 2447.6743 | 555.1289 | 0.04613 | 0.010462 | 0.004613 | 0.0010462 | 2450.2022 | 555.7022 | 0.0015386 | 0.00038464 | 0.038602 | 0.0096504
CAMPHT1 | Operations Camp Heater | 8760 | 1.1473 | 5.0253 | 2.6246 | 20.997 | 11.4958 | 0.19122 | 0.83755 | 0.23747 | 5.6992 | 1.0401 | 0.23747 | 5.6992 | 1.0401 | 0.080979 | 1.9435 | 0.35469 | 0.48512 | 11.6428 | 2.1248 | 3728.0753 | 14813.5442 | 0.070262 | 0.27918 | 0.0070262 | 0.027918 | 3731.9256 | 14828.8435 | 0.0023434 | 0.010264 | 0.058795 | 0.25752
CAMPHT2 | Operations Camp Heater | 8760 | 1.1473 | 5.0253 | 2.6246 | 20.997 | 11.4958 | 0.19122 | 0.83755 | 0.23747 | 5.6992 | 1.0401 | 0.23747 | 5.6992 | 1.0401 | 0.080979 | 1.9435 | 0.35469 | 0.48512 | 11.6428 | 2.1248 | 3728.0753 | 14813.5442 | 0.070262 | 0.27918 | 0.0070262 | 0.027918 | 3731.9256 | 14828.8435 | 0.0023434 | 0.010264 | 0.058795 | 0.25752
CAMPHT3 | Operations Camp Heater (spare) | 0
| Tank Emissions | 8760 | [5 empty] | 0.13284 | 0.58184
| Fugitive Emissions | 8760 | [5 empty] | 10.8025 | 47.3151 | [14 empty] | 27.9984 | 111.252 |  |  | 699.9605 | 2781.3
| Mobile Equipment Emissions (Normal Operation) | 8760 |  | 3.259 |  |  | 3.2583 |  | 0.33304 |  |  | 0.19328 |  |  | 0.16899 |  |  | 0.018136 |  |  |  |  | 2159.6627 |  | 0.12735 |  | 0.0087667 |  | 2165.459 |  |  |  | 0.06986
| Non-Road/Portable Equipment Emissions (Normal Operation) | 8760 |  | 7.5904 |  |  | 3.2176 |  | 2.4298 |  |  | 0.69429 |  |  | 0.69429
Total Emissions (Without Maximum Flare) |  |  | 549.7607 | 1866.9379 | 665.0822 | 5320.6574 | 2346.6724 | 97.3766 | 355.1244 | 69.3084 | 1663.4006 | 264.1282 | 69.0923 | 1658.2153 | 264.0499 | 26.2546 | 630.1104 | 99.0733 | 156.9666 | 3767.1987 | 593.3235 | 1226758.2847 | 4194739.582 | 52.7301 | 190.4252 | 2.3005 | 7.919 | 1228762.0919 | 4201860.0656 | 5.9158 | 25.8438 | 9.8225 | 42.3803
Total Emissions (With Maximum Flare) |  |  | 3629.7677 | 3406.9414 | 14706.2909 | 19361.8661 | 9367.2768 | 25915.083 | 13263.9775 | 1347.5162 | 2941.6084 | 903.2321 | 1347.3001 | 2936.4231 | 903.1538 | 187.51 | 791.3658 | 179.701 | 1122.987 | 4733.2191 | 1076.3337 | 6525098.6043 | 6598050.9853 | 152.5857 | 235.7195 | 12.2861 | 12.4484 | 6532574.5007 | 6607653.5922 | 57.8265 | 51.7992 | 141.043 | 107.9906
8 | CO Standard Requirement
24 | Intermittent unit hours/day operation
24 | Non-intermittent unit hours/day operation
0.5 | Flare hours/day operation
Notes:
1 | Commissioning Only Raw Gas

## GTP Tanks
Alaska LNG
GTP Tank Emissions | [10 empty] | Original
[5 empty] | Current Estimate | [5 empty] | GTP Cookbook Estimate
Source | Stream | Uncontrolled VOC Emissions (lb/yr) |  |  | Uncontrolled VOC Emissions (tpy) | [5 empty] | VOC Emissions
|  | (Working) | (Standing) | (Total) | (Working) | (Standing) | (Total) |  |  |  | lb/hr | lb/year
Tank 53 | ULSD | 4.8827 | 0.34886 | 5.2315 | 0.0024413 | 0.00017443 | 0.0026158 |  |  |  | 0.00058 | 5.0808
Tank 54 | ULSD | 0.16872 | 0.0218 | 0.19052 | 8.436e-05 | 1.09e-05 | 9.526e-05 |  |  |  | 2e-05 | 0.1752
Tank 55 | ULSD | 0.006 | 0.01451 | 0.02051 | 3e-06 | 7.255e-06 | 1.0255e-05 |  |  |  | 0 | 0
Tank 56 | ULSD | 0.20952 | 0.34972 | 0.55924 | 0.00010476 | 0.00017486 | 0.00027962 |  |  |  | 4e-05 | 0.3504
Tank 57 | ULSD | 0.12684 | 0.01573 | 0.14257 | 6.342e-05 | 7.865e-06 | 7.1285e-05 |  |  |  | 2e-05 | 0.1752
Tank 58 | ULSD | 0.12684 | 0.01573 | 0.14257 | 6.342e-05 | 7.865e-06 | 7.1285e-05 |  |  |  | 2e-05 | 0.1752
Tank 59 | ULSD | 0.12684 | 0.01573 | 0.14257 | 6.342e-05 | 7.865e-06 | 7.1285e-05 |  |  |  | 2e-05 | 0.1752
Tank 60 | ULSD | 0.24324 | 0.11654 | 0.35978 | 0.00012162 | 5.827e-05 | 0.00017989 |  |  |  |  | 0
Tank 61 | RUL | 986.4968 | 170.3963 | 1156.8931 | 0.49325 | 0.085198 | 0.57845 |  |  |  |  | 0
Tank Totals |  | 992.3875 | 171.2949 | 1163.6824 | 0.49619 | 0.085647 | 0.58184 |  |  |  | 0.0007 | 6.132
Total Facility Emissions |  |  |  | 1163.6824 |  |  | 0.58184 |  |  |  | 0.0007 | 6.132
|  | Tank 53 | Tank 54 | Tank 55 | Tank 56 | Tank 57 | Tank 58 | Tank 59 | Tank 60 | Tank 61 | Facility Totals
|  | ULSD | ULSD | ULSD | ULSD | ULSD | ULSD | ULSD | ULSD | RUL | VOC
|  | lb/yr | lb/yr | lb/yr | lb/yr | lb/yr | lb/yr | lb/yr | lb/yr | lb/yr | lb/yr | tpy
VOC |  | 5.2315 | 0.19052 | 0.02051 | 0.55924 | 0.14257 | 0.14257 | 0.14257 | 0.35978 | 1156.8931 | 1163.6824 | 0.58184
| CAS | [9 empty] | HAPs
Conrolled HAP Emissions | Number | [9 empty] | lb/yr | tpy
Benzene | 71432 | 0.00492 | 0.000146 | 2.0309e-05 | 0.00048021 | 0.00011756 | 0.00011756 | 0.00011756 | 0.00027842 | 4.6249 | 4.6311 | 0.0023155
Cyclohexane | 110827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66234 | 0.66234 | 0.00033117
Ethylbenzene | 100414 | 0.00514 | 0.0001636 | 2.1224e-05 | 0.00048959 | 0.00011508 | 0.00011508 | 0.00011508 | 0.0002968 | 0.23033 | 0.23679 | 0.00011839
Hexane (-n) | 110543 | 0.001073 | 4.1403e-05 | 4.5563e-06 | 0.00012329 | 3.0975e-05 | 3.0975e-05 | 3.0975e-05 | 7.8626e-05 | 4.6161 | 4.6175 | 0.0023087
Isopropyl benzene | 98828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03356 | 0.03356 | 1.678e-05
Toluene | 108883 | 0.04767 | 0.0016621 | 0.00016885 | 0.00492 | 0.0012074 | 0.0012074 | 0.0012074 | 0.0032 | 4.2571 | 4.3183 | 0.0021592
1,2,4-Trimethylbenzene | 95636 | 0.05773 | 0.0020327 | 0.000214 | 0.00606 | 0.0015005 | 0.0015005 | 0.0015005 | 0.0039 | 0.05889 | 0.13333 | 6.6664e-05
Isooctane | 540841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4245 | 8.4245 | 0.0042122
Xylene (-m) | 1330207 | 0.09591 | 0.00341 | 0.00033133 | 0.01026 | 0.0024996 | 0.0024996 | 0.0024996 | 0.00657 | 0.9444 | 1.0684 | 0.00053419
Total HAPs (lbs/yr) |  | 0.21244 | 0.0074558 | 0.00076027 | 0.022333 | 0.0054712 | 0.0054712 | 0.0054712 | 0.014324 | 23.852 | 24.1257
Total HAPs (tpy) |  | 0.00010622 | 3.7279e-06 | 3.8013e-07 | 1.1167e-05 | 2.7356e-06 | 2.7356e-06 | 2.7356e-06 | 7.1619e-06 | 0.011926 |  | 0.012063
Total HAPs (Standing) (tpy) |  | 7.2215e-06 | 4.1707e-07 | 2.665e-07 | 7.1309e-06 | 2.7162e-07 | 2.7162e-07 | 2.7162e-07 | 2.3506e-06 | 0.0017557
Total HAPs (Working) (tpy) |  | 9.9e-05 | 3.3108e-06 | 1.1364e-07 | 4.0356e-06 | 2.464e-06 | 2.464e-06 | 2.464e-06 | 4.8113e-06 | 0.01017

## GTP Fuel
GTP Fuel Gas Specification
| Component | % By Volume | MW |  | Conversion of 1 grain/100 scf of H2S to Sulfur
| Hydrogen | 0 |  |  | GPSA Calculation:
| Methane | 91.11
| Ethane | 5.76
| Ethylene | 0 |  |  | 32 | Sulfur Molecular Weight
| Propane | 1.97 |  |  | 34.08 | H2S Molecular Weight
| Propylene | 0 |  |  | 1.065
| Butane | 0.3
| Butylene | 0 |  |  | 90 | ppm H2S of Rich Gas
| Butadiene | 0 |  |  | 95.85 | ppm S equivalent
| Pentane | 0.07
| Cyclopentane | 0
| Hexane | 0.0074
| Heptane | 0.0045
| CO | 0
| CO2 | 0.005
| Nitrogen | 0.77 | 28.013
| Water | 0 | 18.02
| Oxygen | 0 | 32
| Lean Gas - S (Note 1) | 0.0016 | 64.066
| Rich Gas - S (Note 1) | 0.009585 | 64.066
| Ammonia | 0
| Argon | 0
Properties
| Temp | 82
| MW | 17.67
Fuel Heating Value at 82ºF:
| Net (Btu/lbm) | 21040
| Net (Btu/scf) | 980
| Gross (Btu/lbm) | 23129
| Gross (Btu/scf) | 1077
scf defined at 14.676 psia, 60F
REFERENCE GTP COOKBOOK USAG-EC-PRZZ-00-000003_EMISSIONS DATA REV 1
Notes:
1 | Normal maximum sulfur based on 16 ppmv for total sulfur being equal to the pipeline specification of 1 grain/100 scf. This assumes all H2S and other mercaptans are included in Sulfur value
GTP Diesel Fuel Specification
| Sulfur Content (H2S) | 15 | ppm | Assume ULSD required
| Specific Gravity | 0.855 |  | average value at 60oF
| Density | 7.1307 | lb/gal
| LHV | 0.13113 | MMBtu/gal
| LHV | 18390 | Btu/lb
| HHV | 0.14425 | MMBtu/gal | Assumed 10% higher than LHV
| HHV | 20229 | Btu/lb
| lb SO2/gal Fuel | 0.00020134

## GTP Turbines
GTP Fuel Gas-Driven Turbines |  |  |  | Reference: GTP COOKBOOK USAG-EC-PRZZ-00-000003_EMISSIONS DATA REV 1
| EMISSION FACTORS | Standard Factors |  | Special/Vendor
|  | AP42 Table 3.1-1 and 3.1-2a | 40 CFR Part 98 (Natural Gas) |  |  | Ambient Temp Basis (F) | Load % Basis | Treated Gas/CO2 CompressorTurbine Vendor | Ambient Temp Basis (F) | Load % Basis | Power Gen Turbine |  | Supplemental Firing Vendor
| NOx (lb/MMBtu) | 0.33788 |  | Short-Term ppmvd @ 15% NOx |  | -40 | 100% | 11 | -40 | 100% | 9 | NOx (lb/MMBtu) | 0.08
| CO (lb/MMBtu) | 0.086582 |  | Short-Term ppmvd @ 15% CO |  | -40 | 100% | 25 | -40 | 85% | 25 | CO (lb/MMBtu) | 0.08
| VOC (lb/MMBtu) | 0.0022174 |  | Annual ppmvd @ 15% NOx |  | 10 | 100% | 11 | 10 | 100% | 9 | VOC (lb/MMBtu) | 0.015
| PM10 (lb/MMBtu) | 0.0069688 |  | Annual ppmvd @ 15% CO |  | 10 | 100% | 25 | 10 | 100% | 25 | PM10 (lb/MMBtu) | 0.005
| PM2.5 (lb/MMBtu) | 0.0069688 | [9 empty] | PM2.5 (lb/MMBtu) | 0.005
| CO2 (kg CO2/MMBtu) |  | 53.06
| CH4 (kg CH4/MMBtu) |  | 0.001
| N2O (kg N2O/MMBtu) |  | 0.0001
Notes:
1.) AP42 Section 3.1 Emission Factors have been convert to AlaskaLNG fuel gas HHV by ratio of project fuel gas/1020 (btu/scf)
| EMISSIONS CALCULATIONS | Treated Gas Compressor Turbines |  | CO2 Compressor Turbines |  | Main Power Generation Turbines |  | References/ Comments
| Turbine Parameters | Short-Term | Annual | Short-Term | Annual | Short-Term | Annual
| Total Installed | 6 | 6 | 6 | 6 | 6 | 6 | From GTP Cookbook
| Ambient Temperature Basis (F) | -40 | 10 | -40 | 10 | -40 | 10
| Load % Basis | 100% | 100% | 100% | 100% | 100% | 100%
| Operation (hr/yr) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
| Device Power (hp) | 61094.2738 | 56196.862 | 37339.4126 | 34457.5567 | 59089.4462 | 54264.4495
| Device Power (kW) | 45558 | 41906 | 27844 | 25695 | 44063 | 40465 | From GTP Cookbook - Inlet Power
| Turbine Heat Input HHV (MMBtu/hr) | 418 | 386 | 311 | 291 | 418 | 386 | From GTP Cookbook
| Fuel Flow Rate (lbmol/hr) | 1024 | 943 | 760 | 712 | 1024 | 943 | From GTP Cookbook
| Exhaust Flow MW (lb/lbmol) | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | From GTP Cookbook
| Exhaust Flow Rate WET (lb/hr) | 1042433 | 968343 | 724483 | 684305 | 1042433 | 968343 | From GTP Cookbook
| Exhaust Flow Rate (lbmol/hr) | 36448.7063 | 33858.1469 | 25331.5734 | 23926.7483 | 36448.7063 | 33858.1469
| Exhaust H2O Concentration | 6.18% | 5.78% | 6.29% | 6.36% | 6.18% | 5.78% | From GTP Cookbook
| Exhaust Flow Rate DRY (lbmol/hr) | 34196.1762 | 31901.146 | 23738.2175 | 22405.0071 | 34196.1762 | 31901.146
| Exhaust O2 Concentration DRY | 15.56% | 15.3% | 14.76% | 14.81% | 15.56% | 15.3% | From Vendor Info
| Exhaust Flow Rate (acfh) | 23152716.2576 | 21507157.5047 | 16090961.5606 | 15198597.4146 | 35420994.6424 | 32903478.8951
| Turbine Emission Factors | Short-Term | Annual | Short-Term | Annual | Short-Term | Annual
| NOx (ppmvd @15% O2) | 11 | 11 | 11 | 11 | 9 | 9 | Adjusted to Actual O2 Amount
| CO (ppmvd @15% O2) | 25 | 25 | 25 | 25 | 25 | 25 | Adjusted to Actual O2 Amount
| VOC (lb/MMBtu) | 0.0022174 | 0.0022174 | 0.0022174 | 0.0022174 | 0.0022174 | 0.0022174 |  |  |  | Conversion Table
| PM10 (lb/MMBtu) | 0.0069688 | 0.0069688 | 0.0069688 | 0.0069688 | 0.0069688 | 0.0069688 |  |  |  | 1 lb = | 453.59 | g
| PM2.5 (lb/MMBtu) | 0.0069688 | 0.0069688 | 0.0069688 | 0.0069688 | 0.0069688 | 0.0069688 |  |  |  | 1 lbmol = | 378.49 | scf
| SO2 | No Emission Factor | No Emission Factor | No Emission Factor | No Emission Factor | No Emission Factor | No Emission Factor | Based on Mass Balance of Sulfur |  |  | 1 MMBtu= | 1000000 | Btu
| CO2 (kg CO2/MMBtu) | 53.06 | 53.06 | 53.06 | 53.06 | 53.06 | 53.06 |  |  |  | 1 hr = | 60 | min
| CH4 (kg CH4/MMBtu) | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 |  |  |  | 1 ft3 = | 0.028317 | m3
| N2O (kg N2O/MMBtu) | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 |  |  |  | 1 min = | 60 | sec
| Turbine Emission Calculations (Maximum 1-hour) | [9 empty] | 1 kJ = | 0.94782 | MMBtu
| NOx (lb/hr) | 15.6643 | 15.3245 | 12.5029 | 11.7046 | 12.8163 | 12.5383 |  |  |  | 1 scf = | 28.32 | L
| CO (lb/hr) | 21.673 | 21.2029 | 17.2989 | 16.1943 | 21.673 | 21.2029 |  |  |  | 1 g = | 1000000 | ug
| VOC (lb/hr) | 0.92685 | 0.8559 | 0.6896 | 0.64525 | 0.92685 | 0.8559 |  |  |  | 1 ton = | 2000 | lb
| PM10 (lb/hr) | 2.913 | 2.69 | 2.1673 | 2.0279 | 2.913 | 2.69 |  |  |  | 1 hp = | 0.7457 | kW
| PM2.5 (lb/hr) | 2.913 | 2.69 | 2.1673 | 2.0279 | 2.913 | 2.69 |  |  |  | 1 kg = | 2.2046 | lb
| SO2 @ 16 ppm (lb/hr) | 1.0497 | 0.96663 | 0.77904 | 0.72984 | 1.0497 | 0.96663 |  |  |  | 1 mol = | 1000000 | ppm
| SO2 @ 96 ppm (lb/hr) | 6.2881 | 5.7907 | 4.667 | 4.3722 | 6.2881 | 5.7907 |  |  |  | 1 tonnes = | 1000 | kg
| CO2 (lb/hr) | 48895.9998 | 45152.7653 | 36379.5596 | 34040.0381 | 48895.9998 | 45152.7653
| CH4 (lb/hr) | 0.92152 | 0.85098 | 0.68563 | 0.64154 | 0.92152 | 0.85098 |  |  |  | Heat Release Equivalents
| N2O (lb/hr) | 0.092152 | 0.085098 | 0.068563 | 0.064154 | 0.092152 | 0.085098 |  |  |  | 1 | CO2
| CO2e (lb/hr) | 48946.4992 | 45199.3988 | 36417.1322 | 34075.1944 | 48946.4992 | 45199.3988 |  |  |  | 25 | CH4
| Supplemental Firing Parameters | [9 empty] | 298 | N2O
| Ambient Temp Basis (F) | -40 | 10 | -40 | 10
| Load % Basis | 100% | 85% | 80% | 85% | [5 empty] | Molecular Weight
| Operation (hr/yr) | 8760 | 8760 | 8760 | 8760 | [5 empty] | NO2 | 46.01
| Heat Input LHV (MMBtu/hr) | 259 | 172 | 174 | 129 |  |  | From GTP Cookbook |  |  | CO | 28.01
| Heat Input HHV (MMBtu/hr) | 284.6357 | 189.0245 | 191.2224 | 141.7684
| Fuel Flow Rate (lbmol/hr) | 698.2634 | 463.7116 | 469.1036 | 347.7837 |  |  | Based on HHV
Supplemental Firing Emission Factors
| NOx (lb/MMBtu) | 0.08 | 0.08 | 0.08 | 0.08
| CO (lb/MMBtu) | 0.08 | 0.08 | 0.08 | 0.08
| VOC (lb/MMBtu) | 0.015 | 0.015 | 0.015 | 0.015
| PM10 (lb/MMBtu) | 0.005 | 0.005 | 0.005 | 0.005
| PM2.5 (lb/MMBtu) | 0.005 | 0.005 | 0.005 | 0.005
| SO2 | No Emission Factor | No Emission Factor | No Emission Factor | No Emission Factor |  |  | Based on Mass Balance of Sulfur
| CO2 (kg CO2/MMBtu) | 53.06 | 53.06 | 53.06 | 53.06
| CH4 (kg CH4/MMBtu) | 0.001 | 0.001 | 0.001 | 0.001
| N2O (kg N2O/MMBtu) | 0.0001 | 0.0001 | 0.0001 | 0.0001
Supplemental Firing Emission Calculations (Maximum 1-hour)
| NOx (lb/hr) | 22.7709 | 15.122 | 15.2978 | 11.3415
| CO (lb/hr) | 22.7709 | 15.122 | 15.2978 | 11.3415
| VOC (lb/hr) | 4.2695 | 2.8354 | 2.8683 | 2.1265
| PM10 (lb/hr) | 1.4232 | 0.94512 | 0.95611 | 0.70884
| PM2.5 (lb/hr) | 1.4232 | 0.94512 | 0.95611 | 0.70884
| SO2 @ 16 ppm (lb/hr) | 0.71576 | 0.47533 | 0.48086 | 0.3565
| SO2 @ 96 ppm (lb/hr) | 4.2878 | 2.8475 | 2.8806 | 2.1356
| CO2 (lb/hr) | 33295.5689 | 22111.3431 | 22368.4517 | 16583.5073
| CH4 (lb/hr) | 0.62751 | 0.41672 | 0.42157 | 0.31254
| N2O (lb/hr) | 0.062751 | 0.041672 | 0.042157 | 0.031254
| CO2e (lb/hr) | 33329.9564 | 22134.1795 | 22391.5537 | 16600.6346
Total Emission Calculations (Maximum 1-hour)
| NOx (lb/hr) | 38.4352 | 30.4465 | 27.8007 | 23.046 | 12.8163 | 12.5383
| CO (lb/hr) | 44.4439 | 36.3249 | 32.5967 | 27.5358 | 21.673 | 21.2029
| VOC (lb/hr) | 5.1964 | 3.6913 | 3.5579 | 2.7718 | 0.92685 | 0.8559
| PM10 (lb/hr) | 4.3361 | 3.6351 | 3.1234 | 2.7368 | 2.913 | 2.69
| PM2.5 (lb/hr) | 4.3361 | 3.6351 | 3.1234 | 2.7368 | 2.913 | 2.69
| SO2 @ 16 ppm (lb/hr) | 1.7654 | 1.442 | 1.2599 | 1.0863 | 1.0497 | 0.96663
| SO2 @ 96 ppm (lb/hr) | 10.5759 | 8.6382 | 7.5476 | 6.5078 | 6.2881 | 5.7907
| CO2 (lb/hr) | 82191.5687 | 67264.1084 | 58748.0114 | 50623.5454 | 48895.9998 | 45152.7653
| CH4 (lb/hr) | 1.549 | 1.2677 | 1.1072 | 0.95408 | 0.92152 | 0.85098
| N2O (lb/hr) | 0.1549 | 0.12677 | 0.11072 | 0.095408 | 0.092152 | 0.085098
| CO2e (lb/hr) | 82276.4556 | 67333.5783 | 58808.6859 | 50675.8291 | 48946.4992 | 45199.3988
Total Emission Calculations (Annual)
| NOx (tpy) | 168.3461 | 133.3556 | 121.7669 | 100.9416 | 56.1352 | 54.9175
| CO (tpy) | 194.6643 | 159.1029 | 142.7734 | 120.6069 | 94.9279 | 92.8687
| VOC (tpy) | 22.7602 | 16.1677 | 15.5837 | 12.1404 | 4.0596 | 3.7488
| PM10 (tpy) | 18.9923 | 15.9217 | 13.6806 | 11.9871 | 12.7588 | 11.7821
| PM2.5 (tpy) | 18.9923 | 15.9217 | 13.6806 | 11.9871 | 12.7588 | 11.7821
| SO2 @ 16 ppm (tpy) | 7.7325 | 6.3158 | 5.5184 | 4.7582 | 4.5975 | 4.2338
| SO2 @ 96 ppm (tpy) | 46.3227 | 37.8355 | 33.0584 | 28.5043 | 27.5419 | 25.3633
| CO2 (tonnes/yr) | 326589.0148 | 267274.603 | 233435.8067 | 201153.1606 | 194288.7408 | 179414.9616
| CH4 (tonnes/yr) | 6.1551 | 5.0372 | 4.3995 | 3.7911 | 3.6617 | 3.3814
| N2O (tonnes/yr) | 0.61551 | 0.50372 | 0.43995 | 0.37911 | 0.36617 | 0.33814
| CO2e (tonnes/yr) | 326926.3136 | 267550.6424 | 233676.8976 | 201360.9102 | 194489.4009 | 179600.2601
Stack Parameters
| Stack Height (ft) | 240 | 240 | 240 | 240 | 240 | 240 | From GTP Cookbook
| Exhaust Temp Ambient Temp Basis (F) | -- | -- | -- | -- | -40 | -40
| Exhaust Temp Load % Basis | -- | -- | -- | -- | 60% | 60%
| Exhaust Temperature (F) | 410 | 410 | 410 | 410 | 871 | 871 | From GTP Cookbook
| Exhaust Velocity Ambient Temp Basis (F) | 70 | 70 | 70 | 70 | 70 | 70
| Exhaust Velocity Load % Basis | 60% | 85% | 60% | 85% | 60% | 60%
| Exhaust Velocity (ft/s) | 52 | 63 | 41 | 48 | 83 | 83 | From GTP Cookbook (Calculated without SF for the Treated Gas and CO2 Turbines)
| Stack Diameter (ft) | 10 | 10 | 10 | 10 | 10 | 10 | From GTP Cookbook
| NO2/NOx Ratio | 0.4 | 0.4 | 0.2 | 0.2 | 0.4 | 0.4 | From GTP Cookbook

## GTP Diesel Equip
GTP Diesel-Driven Intermittent Equipment |  |  |  | Reference: GTP COOKBOOK USAG-EC-PRZZ-00-000003_EMISSIONS DATA REV 1
|  | Emergency |  |  |  | Non-Emergency
| EMISSION FACTORS | Standard Factors
|  | 40 CFR Part 89.112 Tier 3 130<kW<225 | 40 CFR Part 89.112 Tier 3 225<kW<450 | 40 CFR Part 60 Subpart IIII 175<hp<300 | 40 CFR Part 60 Subpart IIII 300<hp<600 | 40 CFR 1039 Subpart B Tier 4 130<kW<560 | 40 CFR 1039 Subpart B Tier 4 kW>560 | 40 CFR Part 98 (Petroleum)
| NOx (g/hp-hr) (95% of NOx+NMHC) | 2.8337 | 2.8337 | 2.85 | 2.85 | 0.29828 | 2.6099
| CO (g/hp-hr) | 2.6099 | 2.6099 | 2.6 | 2.6 | 2.6099 | 2.6099
| VOC (g/hp-hr) (5% of NOx+NMHC) | 0.14914 | 0.14914 | 0.15 | 0.15 | 0.14168 | 0.14168
| PM10 (g/hp-hr) | 0.14914 | 0.14914 | 0.15 | 0.15 | 0.014914 | 0.029828
| PM2.5 (g/hp-hr) | 0.14914 | 0.14914 | 0.15 | 0.15 | 0.014914 | 0.029828
| CO2 (kg CO2/MMBtu) | [6 empty] | 73.96
| CH4 (kg CH4/MMBtu) | [6 empty] | 0.003
| N2O (kg N2O/MMBtu) | [6 empty] | 0.0006
| EMISSIONS CALCULATIONS | Black Start Diesel Generator | Main Diesel Firewater Pump | Dormitory Emergency Diesel Generator | Communications Tower Diesel Generator | References/ Comments
| Total Installed | 1 | 3 | 1 | 1 | From GTP Cookbook |  |  | Conversion Table
| Load % Basis | 100% | 100% | 100% | 100% | Ambient Temp does not affect emissions |  |  | 1 lb = | 453.59 | g
| Operation (hr/yr) | 500 | 500 | 500 | 500 | Intermittent Assumption |  |  | 1 lbmol = | 378.49 | scf
| Rated Power (hp) | 4060 | 250 | 335.2555 | 201.1533 |  |  |  | 1 MMBtu= | 1000000 | Btu
| Rated Power (kW) | 2500 | 186.425 | 250 | 150 | From GTP Cookbook |  |  | 1 hr = | 60 | min
| BSFC (Btu/hp-hr) | 7000 | 7000 | 7000 | 7000 | AP42 Table 3.3-1 |  |  | 1 ft3 = | 0.028317 | m3
| Rated Duty (MMBtu/hr) | 28.42 | 1.75 | 2.3468 | 1.4081 | For HAPs calculation and CO2e |  |  | 1 min = | 60 | sec
| Fuel Flow Rate (gal/hr) | 186.6 | 14.4666 | 19.4 | 11.64 | Ratio Assumed for FWP and Com Tower Gen |  |  | 1 kJ = | 0.94782 | MMBtu
| Exhaust Flow Rate (acfm) | 20134 | 1674.8422 | 2246 | 1347.6 | Ratio Assumed for FWP and Com Tower Gen |  |  | 1 scf = | 28.32 | L
| Emission Factors | [7 empty] | 1 g = | 1000000 | ug
| Not-to-Exceed Factor | 25% | 25% | 25% | 25% |  |  |  | 1 ton = | 2000 | lb
| NOx (g/hp-hr) | 3.2624 | 3.5625 | 3.5421 | 3.5421 |  |  |  | 1 hp = | 0.7457 | kW
| CO (g/hp-hr) | 3.2624 | 3.25 | 3.2624 | 3.2624 |  |  |  | 1 kg = | 2.2046 | lb
| VOC (g/hp-hr) | 0.1771 | 0.1875 | 0.18643 | 0.18643 |  |  |  | 1 mol = | 1000000 | ppm
| PM10 (g/hp-hr) | 0.037285 | 0.1875 | 0.18643 | 0.18643 |  |  |  | 1 tonnes = | 1000 | kg
| PM2.5 (g/hp-hr) | 0.029828 | 0.15 | 0.14914 | 0.14914
| SO2 | No Emission Factor | No Emission Factor | No Emission Factor | No Emission Factor | Based on Mass Balance of Sulfur |  |  | Heat Release Equivalents
| CO2 (kg CO2/MMBtu) | 73.96 | 73.96 | 73.96 | 73.96 |  |  |  | 1 | CO2
| CH4 (kg CH4/MMBtu) | 0.003 | 0.003 | 0.003 | 0.003 |  |  |  | 25 | CH4
| N2O (kg N2O/MMBtu) | 0.0006 | 0.0006 | 0.0006 | 0.0006 |  |  |  | 298 | N2O
Emission Calculations (Maximum 1-hour)
| NOx (lb/hr) | 36.5018 | 2.4544 | 3.2725 | 1.9635
| CO (lb/hr) | 36.5018 | 2.2391 | 3.0141 | 1.8085
| VOC (lb/hr) | 1.9815 | 0.12918 | 0.17224 | 0.10334
| PM10 (lb/hr) | 0.41716 | 0.12918 | 0.17224 | 0.10334
| PM2.5 (lb/hr) | 0.33373 | 0.10334 | 0.13779 | 0.082674
| SO2 (lb/hr) | 0.03757 | 0.0029127 | 0.0039059 | 0.0023436
| CO2 (lb/hr) | 4633.944 | 285.3414 | 382.649 | 229.5894
| CH4 (lb/hr) | 1.2341 | 0.095679 | 0.12831 | 0.076985
| N2O (lb/hr) | 0 | 0 | 0 | 0
| CO2e (lb/hr) | 4664.7974 | 287.7334 | 385.8567 | 231.514
Emission Calculations (Annual)
| NOx (tpy) | 9.1255 | 0.61359 | 0.81813 | 0.49088
| CO (tpy) | 9.1255 | 0.55977 | 0.75354 | 0.45212
| VOC (tpy) | 0.49538 | 0.032294 | 0.043059 | 0.025836
| PM10 (tpy) | 0.10429 | 0.032294 | 0.043059 | 0.025836
| PM2.5 (tpy) | 0.083433 | 0.025836 | 0.034447 | 0.020668
| SO2 (tpy) | 0.0093924 | 0.00072817 | 0.00097649 | 0.00058589
| CO2 (tonnes/yr) | 1050.9716 | 64.715 | 86.7842 | 52.0705
| CH4 (tonnes/yr) | 0.04263 | 0.002625 | 0.0035202 | 0.0021121
| N2O (tonnes/yr) | 0.008526 | 0.000525 | 0.00070404 | 0.00042242
| CO2e (tonnes/yr) | 1054.5781 | 64.9371 | 87.082 | 52.2492
Stack Parameters
| Stack Height (ft) | 115 | 76 | 76 | 29 | From GTP Cookbook (FWP and Com Gen Assumed)
| Exhaust Temperature (F) | 879 | 850 | 852 | 850 | From GTP Cookbook (FWP and Com Gen Assumed)
| Exhaust Velocity (ft/s) | 68 | 35.5413 | 48 | 28.597 | From GTP Cookbook (FWP and Com Gen Assumed)
| Stack Diameter (ft) | 2.5 | 1 | 1 | 1 | From GTP Cookbook (FWP and Com Gen Assumed)
| NO2/NOx Ratio | 0.5 | 0.5 | 0.5 | 0.5 | EPA's ISR Guidance (Date: 3-1-2011)

## GTP Flares
GTP Flares |  |  |  | Reference: GTP COOKBOOK USAG-EC-PRZZ-00-000003_EMISSIONS DATA REV 1
| EMISSION FACTORS | Standard Factors
|  | AP42 Tables 13.5-1 and 13.5-2 | 40 CFR Part 98 (Natural Gas)
| NOx (lb/MMBtu) | 0.068
| CO (lb/MMBtu) | 0.31
| VOC (lb/MMBtu) | 0.57
| PM10 (µg/L Exhaust) | 40
| PM2.5 (µg/L Exhaust) | 40
| CO2 (kg CO2/MMBtu) |  | 53.06
| CH4 (kg CH4/MMBtu) |  | 0.001
| N2O (kg N2O/MMBtu) |  | 0.0001
| MODELING PARAMETERS CALCULATION | LP CO2 East/West Purge Pilot | HP CO2 East/West Purge Pilot | HP HC East/West Purge Pilot | LP HC East/West Purge Pilot | LP CO2 East/West Maximum | HP CO2 East/West Maximum | HP HC East/West Maximum | LP HC East/West Maximum | References/ Comments
Exhaust Flow Calculation
| Fuel Flow Rate (scfh) | 6325.5526 | 2744.69 | 7268.5835 | 1330.9734 | 29125000 | 9541666.6667 | 76250000 | 4166666.6667 | From GTP Cookbook
| Fuel Flow Rate (lbmol/hr) | 16.7126 | 7.2517 | 19.2042 | 3.5165 | 76950.5139 | 25209.825 | 201458.4269 | 11008.6572
| Fuel MW(lb/lbmol) | 17.67 | 17.67 | 17.67 | 17.67 | 35.64 | 35.92 | 20.57 | 17.66 | Purge/Pilot based on Fuel Gas, Maximum Case from GTP Cookbook
| Fuel Flow Rate (lb/hr) | 295.3117 | 128.1373 | 339.3376 | 62.1372 | 2742516.3148 | 905536.9142 | 4143999.8415 | 194412.8863
| Fuel HHV (Btu/lb) | 23129 | 23129 | 23129 | 23129 | 3511.3771 | 3483.5705 | 17690 | 23129 | Purge/Pilot based on Fuel Gas, Maximum Case from GTP Cookbook
| Fuel Flow HHV (MMBtu/hr) | 6.8303 | 2.9637 | 7.8485 | 1.4372 | 9630.0089 | 3154.5017 | 73307.3572 | 4496.5756
| Fd Factor (dscf/MMBtu) | 8710 | 8710 | 8710 | 8710 | 8710 | 8710 | 8710 | 8710 | Method 19 for gas fuel
| Exhaust O2 Concentration | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | Assumed Dry Oxygen Concentration
| Exhaust Flow (dscfh) (@HHV) | 69462.2551 | 30140.0323 | 79817.88 | 14615.705 | 97935038.1319 | 32080577.2986 | 745519441.1479 | 45729169.5095
| Exhaust Water Concentration | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | Assumed Water Content
| Exhaust Flow (scfh) (@HHV) | 77180.2834 | 33488.9248 | 88686.5333 | 16239.6722 | 108816709.0355 | 35645085.8874 | 828354934.6088 | 50810188.3439
| Ratio of Exhaust to Fuel | 12.2014 | 12.2014 | 12.2014 | 12.2014 | 3.7362 | 3.7357 | 10.8637 | 12.1944
| Exhaust Flow (L/h) (@HHV) | 2185745.626 | 948406.351 | 2511602.6227 | 459907.5161 | 3081689199.8847 | 1009468832.3307 | 23459011748.1213 | 1438944533.8996
Effective Height and Diameter Calculation
| Fuel LHV (Btu/lb) | 21040 | 21040 | 21040 | 21040 | 3194 | 3169 | 16100 | 21040 | Purge/Pilot based on Fuel Gas, Maximum Case from GTP Cookbook
| Heat Release Rate (MMBtu/hr) | 6.2134 | 2.696 | 7.1397 | 1.3074 | 8759.5971 | 2869.6465 | 66718.3974 | 4090.4471 | Based on LHV
| Buoyancy flux | 7.2199 | 3.1328 | 8.2963 | 1.5192 | 10178.6518 | 3334.5292 | 77526.7778 | 4753.0996 | SCREEN3 Model User's Guide
| Actual Stack Height (m) | 67.056 | 67.056 | 67.056 | 67.056 | 67.056 | 67.056 | 67.056 | 67.056 | From GTP Cookbook converted to m
| GEP stack height (m) | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | EPA GEP Stack Height Guideline
| Effective Stack Height (m) | 67.2604 | 66.5165 | 67.4156 | 66.073 | 137.3568 | 107.4438 | 255.9683 | 115.2804 | SCREEN3 Model User's Guide
| Effective Stack Diameter (m) | 0.43746 | 0.28816 | 0.46894 | 0.20067 | 16.4255 | 9.4014 | 45.3315 | 11.2244 | SCREEN3 Model User's Guide
Note:
1.) Method 19 used to develop Exhaust Flow Rate for PM calculation. Assumed typical Boiler Exhaust parameters of 3% O2 and 10% H2O
| EMISSIONS CALCULATIONS | LP CO2 East/West Purge Pilot | HP CO2 East/West Purge Pilot | HP HC East/West Purge Pilot | LP HC East/West Purge Pilot | LP CO2 East/West Maximum | HP CO2 East/West Maximum | HP HC East/West Maximum | LP HC East/West Maximum | References/ Comments
| Total Installed | 6 (2 x 3 flare tips) | 2 | 2 | 2 | 3 | 1 | 1 | 1 | From GTP Cookbook | Conversion Table
| Load | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | Ambient Temp does not affect emissions | 1 lb = | 453.59 | g
| Operation (hr/yr) | 8760 | 8760 | 8760 | 8760 | 500 | 500 | 500 | 500 | Maximum Case Intermittent | 1 lbmol = | 378.49 | scf
| Rated Duty HHV (MMBtu/hr) | 6.8303 | 2.9637 | 7.8485 | 1.4372 | 9630.0089 | 3154.5017 | 73307.3572 | 4496.5756 | For HAPs Calculation | 1 MMBtu= | 1000000 | Btu
| Emission Factors | [9 empty] | 1 hr = | 60 | min
| NOx (lb/MMBtu) | 0.068 | 0.068 | 0.068 | 0.068 | 0.068 | 0.068 | 0.068 | 0.068 | Based on HHV | 1 ft3 = | 0.028317 | m3
| CO (lb/MMBtu) | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | Based on HHV | 1 min = | 60 | sec
| VOC (lb/MMBtu) | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | Based on HHV | 1 kJ = | 0.94782 | MMBtu
| PM10 (µg/L Exhaust) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 1 scf = | 28.32 | L
| PM2.5 (µg/L Exhaust) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 1 g = | 1000000 | ug
| SO2 | No Emission Factor | No Emission Factor | No Emission Factor | No Emission Factor | No Emission Factor | No Emission Factor | No Emission Factor | No Emission Factor | Based on Mass Balance of Sulfur | 1 ton = | 2000 | lb
| CO2 (kg CO2/MMBtu) | 53.06 | 53.06 | 53.06 | 53.06 | 53.06 | 53.06 | 53.06 | 53.06 | Based on HHV | 1 hp = | 0.7457 | kW
| CH4 (kg CH4/MMBtu) | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | Based on HHV | 1 kg = | 2.2046 | lb
| N2O (kg N2O/MMBtu) | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | Based on HHV | 1 m = | 0.3048 | ft
| Emission Calculations (Maximum 1-hour) | [9 empty] | 1 mol = | 1000000 | ppm
| NOx (lb/hr) | 0.46446 | 0.20153 | 0.5337 | 0.097728 | 654.8406 | 214.5061 | 4984.9003 | 305.7671 |  | 1 tonnes = | 1000 | kg
| CO (lb/hr) | 2.1174 | 0.91874 | 2.433 | 0.44552 | 2985.3027 | 977.8955 | 22725.2807 | 1393.9385
| VOC (lb/hr) | 3.8933 | 1.6893 | 4.4737 | 0.81919 | 5489.105 | 1798.066 | 41785.1936 | 2563.0481 |  | Heat Release Equivalents
| PM10 (lb/hr) | 0.19275 | 0.083636 | 0.22149 | 0.040557 | 271.7599 | 89.0204 | 2068.7415 | 126.8938 |  | 1 | CO2
| PM2.5 (lb/hr) | 0.19275 | 0.083636 | 0.22149 | 0.040557 | 271.7599 | 89.0204 | 2068.7415 | 126.8938 |  | 25 | CH4
| SO2 @ 16 ppm (lb/hr) | 0.017131 | 0.0074334 | 0.019685 | 0.0036046 | 78.8786 | 25.8415 | 206.5062 | 11.2845 |  | 298 | N2O
| SO2 @ 96 ppm (lb/hr) | 0.10263 | 0.044531 | 0.11793 | 0.021594 | 472.532 | 154.8066 | 1237.101 | 67.6011
| CO2 (lb/hr) | 798.9774 | 346.6805 | 918.0912 | 168.1146 | 1126480.6481 | 369001.2298 | 8575206.9867 | 525991.7746
| CH4 (lb/hr) | 0.015058 | 0.0065337 | 0.017303 | 0.0031684 | 21.2303 | 6.9544 | 161.6134 | 9.9132
| N2O (lb/hr) | 0.0015058 | 0.00065337 | 0.0017303 | 0.00031684 | 2.123 | 0.69544 | 16.1613 | 0.99132
| CO2e (lb/hr) | 799.8026 | 347.0385 | 919.0394 | 168.2882 | 1127644.0695 | 369382.3317 | 8584063.401 | 526535.0153
Emission Calculations (Annual)
| NOx (tpy) | 2.0343 | 0.8827 | 2.3376 | 0.42805 | 163.7102 | 53.6265 | 1246.2251 | 76.4418
| CO (tpy) | 9.2741 | 4.0241 | 10.6567 | 1.9514 | 746.3257 | 244.4739 | 5681.3202 | 348.4846
| VOC (tpy) | 17.0524 | 7.3991 | 19.5947 | 3.588 | 1372.2763 | 449.5165 | 10446.2984 | 640.762
| PM10 (tpy) | 0.84425 | 0.36632 | 0.97011 | 0.17764 | 67.94 | 22.2551 | 517.1854 | 31.7235
| PM2.5 (tpy) | 0.84425 | 0.36632 | 0.97011 | 0.17764 | 67.94 | 22.2551 | 517.1854 | 31.7235
| SO2 @ 16 ppm (tpy) | 0.075035 | 0.032558 | 0.086222 | 0.015788 | 19.7196 | 6.4604 | 51.6265 | 2.8211
| SO2 @ 96 ppm (tpy) | 0.44951 | 0.19504 | 0.51652 | 0.094582 | 118.133 | 38.7017 | 309.2753 | 16.9003
| CO2 (tonnes/yr) | 3174.7448 | 1377.5382 | 3648.0445 | 668.005 | 255484.135 | 83688.9299 | 1944844.1864 | 119294.1519
| CH4 (tonnes/yr) | 0.059833 | 0.025962 | 0.068753 | 0.01259 | 4.815 | 1.5773 | 36.6537 | 2.2483
| N2O (tonnes/yr) | 0.0059833 | 0.0025962 | 0.0068753 | 0.001259 | 0.4815 | 0.15773 | 3.6654 | 0.22483
| CO2e (tonnes/yr) | 3178.0237 | 1378.9609 | 3651.8122 | 668.6949 | 255747.9973 | 83775.3633 | 1946852.808 | 119417.3581
Stack Parameters
| Stack Height (m) | 67.2604 | 66.5165 | 67.4156 | 66.073 | 137.3568 | 107.4438 | 255.9683 | 115.2804
| Exhaust Temperature (K) | 1273 | 1273 | 1273 | 1273 | 1273 | 1273 | 1273 | 1273
| Exhaust Velocity (m/s) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
| Stack Diameter (m) | 0.43746 | 0.28816 | 0.46894 | 0.20067 | 16.4255 | 9.4014 | 45.3315 | 11.2244
| NO2/NOx Ratio | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | EPA's ISR Guidance (Date: 3-1-2011)

## GTP Heaters
GTP Fuel Gas Heaters |  |  |  | Reference: GTP COOKBOOK USAG-EC-PRZZ-00-000003_EMISSIONS DATA REV 1
| EMISSION FACTORS | Standard Factors
|  | AP42 Tables 1.4-1 and 1.4-2 Large Controlled (Low NOx Burners) |  |  | 40 CFR Part 98 (Natural Gas) | Average Emission Factors from Currently Operating Facilities (Low NOx Burners) | Proposed Emission Factors | Emission Factor Assumption
| NOx (lb/MMSCF) | 147.8235 | NOx (lb/MMBtu) | 0.13725 |  | 0.08 | 0.036 | Low NOx Burners
| CO (lb/MMSCF) | 88.6941 | CO (lb/MMBtu) | 0.082353 |  | 0.06 | 0.007 | Oxidation Catalyst
| VOC (lb/MMSCF) | 5.8074 | VOC (lb/MMBtu) | 0.0053922 |  | 0.006
| PM10 (lb/MMSCF) | 8.0247 | PM10 (lb/MMBtu) | 0.007451 |  | 0.007
| PM2.5 (lb/MMSCF) | 8.0247 | PM2.5 (lb/MMBtu) | 0.007451 |  | 0.007
| CO2 (kg CO2/MMBtu) |  |  |  | 53.06
| CH4 (kg CH4/MMBtu) |  |  |  | 0.001
| N2O (kg N2O/MMBtu) |  |  |  | 0.0001
Notes:
1.) Emission Factors have been convert to AlaskaLNG fuel gas HHV by ratio of project fuel gas/1020 (btu/scf)
| EMISSIONS CALCULATIONS | Building Heat Medium Heater | Buyback Gas Bath Heater Primary Heater Standby | Buyback Gas Bath Heater Secondary Heater Standby | Buyback Gas Bath Heater Primary Heater Maximum | Buyback Gas Bath Heater Secondary Heater Maximum | Operations Camp Heater | References/ Comments
| Total Installed | 3 | 1 | 1 | 1 | 1 | 3 | From GTP Cookbook (2 op, 1 spare For Building Heat Medium Heater) | Conversion Table
| Load | 100% | 100% | 100% | 100% | 100% | 100% | Ambient Temp does not affect emissions | 1 lb = | 453.59 | g
| Operation (hr/yr) | 8760 | 8760 | 8760 | 500 | 500 | 8760 | Intermittent Assumption | 1 lbmol = | 378.49 | scf
| Rated Duty LHV (MMBtu/hr) | 250 | 0.14 | 0.14 | 23.04 | 19.04 | 29 | From GTP Cookbook | 1 MMBtu= | 1000000 | Btu
| Rated Duty HHV (MMBtu/hr) | 274.7449 | 0.15386 | 0.15386 | 25.3205 | 20.9246 | 31.8704 |  | 1 hr = | 60 | min
| Fuel Flow Rate (lbmol/hr) | 672 | 0.4 | 0.4 | 62 | 51.2 | 79 | From GTP Cookbook | 1 ft3 = | 0.028317 | m3
| Fuel Flow Rate (MMSCF/hr) | 0.25435 | 0.0001514 | 0.0001514 | 0.023466 | 0.019379 | 0.029901 |  | 1 min = | 60 | sec
| Emission Factors | [7 empty] | 1 kJ = | 0.94782 | MMBtu
| NOx (lb/MMBtu) | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | Assuming 30 ppmv at 15% O2 | 1 scf = | 28.32 | L
| CO (lb/MMBtu) | 0.007 | 0.082353 | 0.082353 | 0.082353 | 0.082353 | 0.082353 | Based on HHV | 1 g = | 1000000 | ug
| VOC (lb/MMBtu) | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | Based on HHV | 1 ton = | 2000 | lb
| PM10 (lb/MMBtu) | 0.007451 | 0.007451 | 0.007451 | 0.007451 | 0.007451 | 0.007451 | Based on HHV | 1 hp = | 0.7457 | kW
| PM2.5 (lb/MMBtu) | 0.007451 | 0.007451 | 0.007451 | 0.007451 | 0.007451 | 0.007451 | Based on HHV | 1 kg = | 2.2046 | lb
| SO2 | No Emission Factor | No Emission Factor | No Emission Factor | No Emission Factor | No Emission Factor | No Emission Factor | Based on Mass Balance of Sulfur | 1 mol = | 1000000 | ppm
| CO2 (kg CO2/MMBtu) | 53.06 | 53.06 | 53.06 | 53.06 | 53.06 | 53.06 | Based on HHV | 1 tonnes = | 1000 | kg
| CH4 (kg CH4/MMBtu) | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | Based on HHV
| N2O (kg N2O/MMBtu) | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | Based on HHV | Heat Release Equivalents
| Emission Calculations (Maximum 1-hour) | [7 empty] | 1 | CO2
| NOx (lb/hr) | 9.8908 | 0.0055389 | 0.0055389 | 0.91154 | 0.75328 | 1.1473 |  | 25 | CH4
| CO (lb/hr) | 1.9232 | 0.012671 | 0.012671 | 2.0852 | 1.7232 | 2.6246 |  | 298 | N2O
| VOC (lb/hr) | 1.6485 | 0.00092314 | 0.00092314 | 0.15192 | 0.12555 | 0.19122
| PM10 (lb/hr) | 2.0471 | 0.0011464 | 0.0011464 | 0.18866 | 0.15591 | 0.23747
| PM2.5 (lb/hr) | 2.0471 | 0.0011464 | 0.0011464 | 0.18866 | 0.15591 | 0.23747
| SO2 @ 16 ppm (lb/hr) | 0.68884 | 0.00041002 | 0.00041002 | 0.063553 | 0.052483 | 0.080979
| SO2 @ 96 ppm (lb/hr) | 4.1266 | 0.0024563 | 0.0024563 | 0.38073 | 0.31441 | 0.48512
| CO2 (lb/hr) | 32138.5801 | 17.9976 | 17.9976 | 2961.8915 | 2447.6743 | 3728.0753
| CH4 (lb/hr) | 0.6057 | 0.00033919 | 0.00033919 | 0.055822 | 0.04613 | 0.070262
| N2O (lb/hr) | 0.06057 | 3.3919e-05 | 3.3919e-05 | 0.0055822 | 0.004613 | 0.0070262
| CO2e (lb/hr) | 32171.7726 | 18.0162 | 18.0162 | 2964.9506 | 2450.2022 | 3731.9256
Emission Calculations (Annual)
| NOx (tpy) | 43.3218 | 0.02426 | 0.02426 | 0.22788 | 0.18832 | 5.0253
| CO (tpy) | 8.4237 | 0.055497 | 0.055497 | 0.5213 | 0.4308 | 11.4958
| VOC (tpy) | 7.2203 | 0.0040434 | 0.0040434 | 0.037981 | 0.031387 | 0.83755
| PM10 (tpy) | 8.9664 | 0.0050212 | 0.0050212 | 0.047166 | 0.038977 | 1.0401
| PM2.5 (tpy) | 8.9664 | 0.0050212 | 0.0050212 | 0.047166 | 0.038977 | 1.0401
| SO2 @ 16 ppm (tpy) | 3.0171 | 0.0017959 | 0.0017959 | 0.015888 | 0.013121 | 0.35469
| SO2 @ 96 ppm (tpy) | 18.0744 | 0.010759 | 0.010759 | 0.095181 | 0.078601 | 2.1248
| CO2 (tonnes/yr) | 127702.9671 | 71.5137 | 71.5137 | 671.7526 | 555.1289 | 14813.5442
| CH4 (tonnes/yr) | 2.4068 | 0.0013478 | 0.0013478 | 0.01266 | 0.010462 | 0.27918
| N2O (tonnes/yr) | 0.24068 | 0.00013478 | 0.00013478 | 0.001266 | 0.0010462 | 0.027918
| CO2e (tonnes/yr) | 127834.8579 | 71.5875 | 71.5875 | 672.4464 | 555.7022 | 14828.8435
Stack Parameters
| Stack Height (ft) | 232 | 20 | 20 | 20 | 20 | 32 | From GTP Cookbook
| Exhaust Temperature (F) | 370 | 601 | 887 | 601 | 887 | 257 | From GTP Cookbook
| Exhaust Velocity (ft/s) | 26 | 0.33 | 0.41 | 54.79 | 57.49 | 29 | From GTP Cookbook
| Stack Diameter (ft) | 9 | 2 | 2 | 2 | 2 | 2.5 | From GTP Cookbook
| NO2/NOx Ratio | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | EPA's ISR Guidance (Date: 3-1-2011)

## GTP Misc
GTP Miscellaneous Emissions |  |  |  | Reference: GTP COOKBOOK USAG-EC-PRZZ-00-000003_EMISSIONS DATA REV 1
| EMISSIONS CALCULATIONS | Tank | Fugitive | References/ Comments
| Methane (lb/hr) |  | 27.9984 | From GTP Cookbook
| NMHC (lb/hr) | 0.0089 | 10.8025 | From GTP Cookbook
| CO2e (lb/hr) |  | 699.9605
| Emissions Calculation (Annual) |  |  |  | Conversion Table
| Operation (hr/yr) | 8760 | 8760 | From GTP Cookbook | 1 lb = | 453.59 | g
| Methane (tonnes/yr) |  | 111.252 |  | 1 lbmol = | 378.49 | scf
| CO2e (tonnes/yr) |  | 2781.3 |  | 1 MMBtu= | 1000000 | Btu
| NMHC (tpy) | 0.038982 | 47.3151 |  | 1 hr = | 60 | min
[5 empty] | 1 ft3 = | 0.028317 | m3
[5 empty] | 1 min = | 60 | sec
[5 empty] | 1 kJ = | 0.94782 | MMBtu
[5 empty] | 1 scf = | 28.32 | L
[5 empty] | 1 g = | 1000000 | ug
[5 empty] | 1 ton = | 2000 | lb
[5 empty] | 1 hp = | 0.7457 | kW
[5 empty] | 1 kg = | 2.2046 | lb
[5 empty] | 1 mol = | 1000000 | ppm
[5 empty] | 1 tonnes = | 1000 | kg
Heat Release Equivalents
[5 empty] | 1 | CO2
[5 empty] | 25 | CH4
[5 empty] | 298 | N2O

## GTP HAP Emission Unit Inventory
Emission Unit ID | Emission Unit Tag No. | Description | Source Category | Turbine ISO Power | Turbine ISO Heat Rate | Turbine 10o F MMBtu/hr (HHV) | Load Basis for CT EF | Fuel/Service | Control Type | CE% | hrs/yr | Load Basis for Calc
1A |  | Train 1a Treated Gas Compressor Turbine Primary Stack (includes SF WHR) | CT |  |  | 558 | >80% | NG |  |  | 8760 | 100% load
1B |  | Train 1b Treated Gas Compressor Turbine Primary Stack (includes SF WHR) | CT |  |  | 558 | >80% | NG |  |  | 8760 | 100% load
2A |  | Train 2a Treated Gas Compressor Turbine Primary Stack (includes SF WHR) | CT |  |  | 558 | >80% | NG |  |  | 8760 | 100% load
2B |  | Train 2b Treated Gas Compressor Turbine Primary Stack (includes SF WHR) | CT |  |  | 558 | >80% | NG |  |  | 8760 | 100% load
3A |  | Train 3a Treated Gas Compressor Turbine Primary Stack (includes SF WHR) | CT |  |  | 558 | >80% | NG |  |  | 8760 | 100% load
3B |  | Train 3b Treated Gas Compressor Turbine Primary Stack (includes SF WHR) | CT |  |  | 558 | >80% | NG |  |  | 8760 | 100% load
4A |  | Train 1a CO2 Compressor Turbine Primary Stack (includes SF WHR) | CT |  |  | 420 | >80% | NG |  |  | 8760 | 100% load
4B |  | Train 1b CO2 Compressor Turbine Primary Stack (includes SF WHR) | CT |  |  | 420 | >80% | NG |  |  | 8760 | 100% load
5A |  | Train 2a CO2 Compressor Turbine Primary Stack (includes SF WHR) | CT |  |  | 420 | >80% | NG |  |  | 8760 | 100% load
5B |  | Train 2b CO2 Compressor Turbine Primary Stack (includes SF WHR) | CT |  |  | 420 | >80% | NG |  |  | 8760 | 100% load
6A |  | Train 3a CO2 Compressor Turbine Primary Stack (includes SF WHR) | CT |  |  | 420 | >80% | NG |  |  | 8760 | 100% load
6B |  | Train 3b CO2 Compressor Turbine Primary Stack (includes SF WHR) | CT |  |  | 420 | >80% | NG |  |  | 8760 | 100% load
7A_1A |  | Power Generator Turbines | CT |  |  | 386 | >80% | NG |  |  | 8760 | 100% load
7A_1B |  | Power Generator Turbines | CT |  |  | 386 | >80% | NG |  |  | 8760 | 100% load
7A_2A |  | Power Generator Turbines | CT |  |  | 386 | >80% | NG |  |  | 8760 | 100% load
7A_2B |  | Power Generator Turbines | CT |  |  | 386 | >80% | NG |  |  | 8760 | 100% load
7A_3A |  | Power Generator Turbines | CT |  |  | 386 | >80% | NG |  |  | 8760 | 100% load
7A_3B |  | Power Generator Turbines | CT |  |  | 386 | >80% | NG |  |  | 8760 | 100% load
9_1 |  | Black Start Diesel Generator (2500 kW) | ICE |  |  | 28.42 | >600hp | D |  |  | 500 | 100% load
31A |  | Main Diesel Firewater Pump (250 hp) | ICE |  |  | 1.75 | <600hp | D |  |  | 500 | 100% load
31B |  | Main Diesel Firewater Pump (250 hp) | ICE |  |  | 1.75 | <600hp | D |  |  | 500 | 100% load
31C |  | Main Diesel Firewater Pump (250 hp) | ICE |  |  | 1.75 | <600hp | D |  |  | 500 | 100% load
33 |  | Dormitory Emergency Diesel Generator (250 kW) | ICE |  |  | 2.3468 | <600hp | D |  |  | 500 | 100% load
36 |  | Communications Tower (150 kW) | ICE |  |  | 1.4081 | <600hp | D |  |  | 500 | 100% load
10E |  | LP CO2 Flare East Pilot/Purge (3 Flares) | Flare |  |  | 6.8303 | 0 | NG |  |  | 8760 | 100% load
10W |  | LP CO2 Flare West Pilot/Purge (3 Flares) | Flare |  |  | 6.8303 | 0 | NG |  |  | 8760 | 100% load
11E |  | HP CO2 Flare East Pilot/Purge | Flare |  |  | 2.9637 | 0 | NG |  |  | 8760 | 100% load
11W |  | HP CO2 Flare West Pilot/Purge | Flare |  |  | 2.9637 | 0 | NG |  |  | 8760 | 100% load
12E |  | HP Hydrocarbon Flare East Pilot/Purge | Flare |  |  | 7.8485 | 0 | NG |  |  | 8760 | 100% load
12W |  | HP Hydrocarbon Flare West Pilot/Purge | Flare |  |  | 7.8485 | 0 | NG |  |  | 8760 | 100% load
13E |  | LP Hydrocarbon Flare East Pilot/Purge | Flare |  |  | 1.4372 | 0 | NG |  |  | 8760 | 100% load
13W |  | LP Hydrocarbon Flare West Pilot/Purge | Flare |  |  | 1.4372 | 0 | NG |  |  | 8760 | 100% load
10E_M |  | LP CO2 Flare East MAX | Flare |  |  | 9630.0089 | 0 | NG |  |  | 500 | 100% load
11E_M |  | HP CO2 Flare East MAX | Flare |  |  | 3154.5017 | 0 | NG |  |  | 500 | 100% load
12E_M |  | HP Hydrocarbon Flare East MAX | Flare |  |  | 73307.3572 | 0 | NG |  |  | 500 | 100% load
13E_M |  | LP Hydrocarbon Flare East MAX | Flare |  |  | 4496.5756 | 0 | NG |  |  | 500 | 100% load
14_1 |  | Building Heat Medium Heater | Heater |  |  | 274.7449 | 0 | NG |  |  | 8760 | 100% load
14_2 |  | Building Heat Medium Heater | Heater |  |  | 274.7449 | 0 | NG |  |  | 8760 | 100% load
14_3 |  | Building Heat Medium Heater (spare) | Heater |  |  | 274.7449 | 0 | NG |  |  | 0 | 100% load
21A |  | Buyback Gas Bath Heater Pre-Let Down Heater Standby | Heater |  |  | 0.15386 | 0 | NG |  |  | 8760 | 100% load
21B |  | Buyback Gas Bath Heater Post-Let Down Heater Standby | Heater |  |  | 0.15386 | 0 | NG |  |  | 8760 | 100% load
21A_M |  | Buyback Gas Bath Heater Pre-Let Down Heater MAX | Heater |  |  | 25.3205 | 0 | NG |  |  | 500 | 100% load
21B_M |  | Buyback Gas Bath Heater Post-Let Down Heater MAX | Heater |  |  | 20.9246 | 0 | NG |  |  | 500 | 100% load
CAMPHT1 |  | Operations Camp Heater | Heater |  |  | 31.8704 | 0 | NG |  |  | 8760 | 100% load
CAMPHT2 |  | Operations Camp Heater | Heater |  |  | 31.8704 | 0 | NG |  |  | 8760 | 100% load
CAMPHT3 |  | Operations Camp Heater (spare) | Heater |  |  | 31.8704 | 0 | NG |  |  | 0 | 100% load
Note on K1: kmalmquist: Control Efficiency

## GTP HAPs Calc
| Emission Unit Tag No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Total
| Emission Unit ID | 1A | 1B | 2A | 2B | 3A | 3B | 4A | 4B | 5A | 5B | 6A | 6B | 7A_1A | 7A_1B | 7A_2A | 7A_2B | 7A_3A | 7A_3B | 9_1 | 31A | 31B | 31C | 33 | 36 | 10E | 10W | 11E | 11W | 12E | 12W | 13E | 13W | 10E_M | 11E_M | 12E_M | 13E_M | 14_1 | 14_2 | 14_3 | 21A | 21B | 21A_M | 21B_M | CAMPHT1 | CAMPHT2 | CAMPHT3
| CT Mfg / Model | Train 1a Treated Gas Compressor Turbine Primary Stack (includes SF WHR) | Train 1b Treated Gas Compressor Turbine Primary Stack (includes SF WHR) | Train 2a Treated Gas Compressor Turbine Primary Stack (includes SF WHR) | Train 2b Treated Gas Compressor Turbine Primary Stack (includes SF WHR) | Train 3a Treated Gas Compressor Turbine Primary Stack (includes SF WHR) | Train 3b Treated Gas Compressor Turbine Primary Stack (includes SF WHR) | Train 1a CO2 Compressor Turbine Primary Stack (includes SF WHR) | Train 1b CO2 Compressor Turbine Primary Stack (includes SF WHR) | Train 2a CO2 Compressor Turbine Primary Stack (includes SF WHR) | Train 2b CO2 Compressor Turbine Primary Stack (includes SF WHR) | Train 3a CO2 Compressor Turbine Primary Stack (includes SF WHR) | Train 3b CO2 Compressor Turbine Primary Stack (includes SF WHR) | Power Generator Turbines | Power Generator Turbines | Power Generator Turbines | Power Generator Turbines | Power Generator Turbines | Power Generator Turbines | Black Start Diesel Generator (2500 kW) | Main Diesel Firewater Pump (250 hp) | Main Diesel Firewater Pump (250 hp) | Main Diesel Firewater Pump (250 hp) | Dormitory Emergency Diesel Generator (250 kW) | Communications Tower (150 kW) | LP CO2 Flare East Pilot/Purge (3 Flares) | LP CO2 Flare West Pilot/Purge (3 Flares) | HP CO2 Flare East Pilot/Purge | HP CO2 Flare West Pilot/Purge | HP Hydrocarbon Flare East Pilot/Purge | HP Hydrocarbon Flare West Pilot/Purge | LP Hydrocarbon Flare East Pilot/Purge | LP Hydrocarbon Flare West Pilot/Purge | LP CO2 Flare East MAX | HP CO2 Flare East MAX | HP Hydrocarbon Flare East MAX | LP Hydrocarbon Flare East MAX | Building Heat Medium Heater | Building Heat Medium Heater | Building Heat Medium Heater (spare) | Buyback Gas Bath Heater Pre-Let Down Heater Standby | Buyback Gas Bath Heater Post-Let Down Heater Standby | Buyback Gas Bath Heater Pre-Let Down Heater MAX | Buyback Gas Bath Heater Post-Let Down Heater MAX | Operations Camp Heater | Operations Camp Heater | Operations Camp Heater (spare)
| Source Category | CT | CT | CT | CT | CT | CT | CT | CT | CT | CT | CT | CT | CT | CT | CT | CT | CT | CT | ICE | ICE | ICE | ICE | ICE | ICE | Flare | Flare | Flare | Flare | Flare | Flare | Flare | Flare | Flare | Flare | Flare | Flare | Heater | Heater | Heater | Heater | Heater | Heater | Heater | Heater | Heater | Heater
| ISO Power (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ISO Heat Rate (MMBtu/hr) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10oF Heat Consumption (MMBtu/hr) | 558 | 558 | 558 | 558 | 558 | 558 | 420 | 420 | 420 | 420 | 420 | 420 | 386 | 386 | 386 | 386 | 386 | 386 | 28.42 | 1.75 | 1.75 | 1.75 | 2.3468 | 1.4081 | 6.8303 | 6.8303 | 2.9637 | 2.9637 | 7.8485 | 7.8485 | 1.4372 | 1.4372 | 9630.0089 | 3154.5017 | 73307.3572 | 4496.5756 | 274.7449 | 274.7449 | 274.7449 | 0.15386 | 0.15386 | 25.3205 | 20.9246 | 31.8704 | 31.8704 | 31.8704
| Load Basis for CT EF | >80% | >80% | >80% | >80% | >80% | >80% | >80% | >80% | >80% | >80% | >80% | >80% | >80% | >80% | >80% | >80% | >80% | >80% | >600hp | <600hp | <600hp | <600hp | <600hp | <600hp | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fuel | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | D | D | D | D | D | D | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG
| hrs/yr | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 500 | 500 | 500 | 500 | 500 | 500 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 500 | 500 | 500 | 500 | 8760 | 8760 | 0 | 8760 | 8760 | 500 | 500 | 8760 | 8760 | 0
2 | 1,1,2,2-Tetrachloroethane | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1,1,2-Trichloroethane | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1,3-Butadiene | 0.0010509 | 0.0010509 | 0.0010509 | 0.0010509 | 0.0010509 | 0.0010509 | 0.00079103 | 0.00079103 | 0.00079103 | 0.00079103 | 0.00079103 | 0.00079103 | 0.00072699 | 0.00072699 | 0.00072699 | 0.00072699 | 0.00072699 | 0.00072699 | 0 | 1.7106e-05 | 1.7106e-05 | 1.7106e-05 | 2.294e-05 | 1.3764e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015502
5 | 1,3-Dichloropropene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1,4-Dichlorobenzene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2,2,4-Trimethylpentane | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | Acetaldehyde | 0.097762 | 0.097762 | 0.097762 | 0.097762 | 0.097762 | 0.097762 | 0.073584 | 0.073584 | 0.073584 | 0.073584 | 0.073584 | 0.073584 | 0.067627 | 0.067627 | 0.067627 | 0.067627 | 0.067627 | 0.067627 | 0.00017905 | 0.00033556 | 0.00033556 | 0.00033556 | 0.00045 | 0.00027 | 0.0012612 | 0.0012612 | 0.00054724 | 0.00054724 | 0.0014492 | 0.0014492 | 0.00026537 | 0.00026537 | 0.10149 | 0.033246 | 0.7726 | 0.04739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3975
9 | Acrolein | 0.015642 | 0.015642 | 0.015642 | 0.015642 | 0.015642 | 0.015642 | 0.011773 | 0.011773 | 0.011773 | 0.011773 | 0.011773 | 0.011773 | 0.01082 | 0.01082 | 0.01082 | 0.01082 | 0.01082 | 0.01082 | 5.5987e-05 | 4.0469e-05 | 4.0469e-05 | 4.0469e-05 | 5.4269e-05 | 3.2562e-05 | 0.0002933 | 0.0002933 | 0.00012726 | 0.00012726 | 0.00033703 | 0.00033703 | 6.1714e-05 | 6.1714e-05 | 0.023603 | 0.0077316 | 0.17967 | 0.011021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45335
10 | Antimony | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | Arsenic | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | Benzene | 0.029328 | 0.029328 | 0.029328 | 0.029328 | 0.029328 | 0.029328 | 0.022075 | 0.022075 | 0.022075 | 0.022075 | 0.022075 | 0.022075 | 0.020288 | 0.020288 | 0.020288 | 0.020288 | 0.020288 | 0.020288 | 0.0055135 | 0.00040819 | 0.00040819 | 0.00040819 | 0.00054739 | 0.00032843 | 0.0046635 | 0.0046635 | 0.0020235 | 0.0020235 | 0.0053587 | 0.0053587 | 0.00098125 | 0.00098125 | 0.37529 | 0.12293 | 2.8568 | 0.17523 | 0.0024775 | 0.0024775 | 0 | 1.3874e-06 | 1.3874e-06 | 1.3032e-05 | 1.077e-05 | 0.00028739 | 0.00028739 | 0 | 3.9997
13 | Beryllium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | Biphenyl | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Cadmium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | Carbon Tetrachloride | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | Chlorobenzene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | Chloroform | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | Chromium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | Cobalt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | Dibutylphthalate | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | Ethylbenzene | 0.078209 | 0.078209 | 0.078209 | 0.078209 | 0.078209 | 0.078209 | 0.058867 | 0.058867 | 0.058867 | 0.058867 | 0.058867 | 0.058867 | 0.054102 | 0.054102 | 0.054102 | 0.054102 | 0.054102 | 0.054102 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042352 | 0.042352 | 0.018377 | 0.018377 | 0.048666 | 0.048666 | 0.0089115 | 0.0089115 | 3.4083 | 1.1164 | 25.9451 | 1.5914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.4449
23 | Ethylene Dibromide | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | Ethylene Dichloride | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | Formaldehyde | 1.7353 | 1.7353 | 1.7353 | 1.7353 | 1.7353 | 1.7353 | 1.3061 | 1.3061 | 1.3061 | 1.3061 | 1.3061 | 1.3061 | 1.2004 | 1.2004 | 1.2004 | 1.2004 | 1.2004 | 1.2004 | 0.00056058 | 0.00051625 | 0.00051625 | 0.00051625 | 0.0006923 | 0.00041538 | 0.034287 | 0.034287 | 0.014877 | 0.014877 | 0.039398 | 0.039398 | 0.0072143 | 0.0072143 | 2.7592 | 0.90383 | 21.004 | 1.2884 | 0.088484 | 0.088484 | 0 | 4.9551e-05 | 4.9551e-05 | 0.00046545 | 0.00038464 | 0.010264 | 0.010264 | 0 | 51.7992
26 | HCl | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | Lead | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0005899 | 0.0005899 | 0 | 3.3034e-07 | 3.3034e-07 | 3.103e-06 | 2.5643e-06 | 6.8428e-05 | 6.8428e-05 | 0 | 0.001323
28 | Manganese | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | Mercury | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | Methanol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | Methylene Chloride | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | n-Hexane | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00085057 | 0.00085057 | 0.00036907 | 0.00036907 | 0.00097737 | 0.00097737 | 0.00017897 | 0.00017897 | 0.068449 | 0.022422 | 0.52106 | 0.031961 | 2.1236 | 2.1236 | 0 | 0.0011892 | 0.0011892 | 0.011171 | 0.0092314 | 0.24634 | 0.24634 | 0 | 5.4113
33 | Nickel | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | PAHs | 0.0053769 | 0.0053769 | 0.0053769 | 0.0053769 | 0.0053769 | 0.0053769 | 0.0040471 | 0.0040471 | 0.0040471 | 0.0040471 | 0.0040471 | 0.0040471 | 0.0037195 | 0.0037195 | 0.0037195 | 0.0037195 | 0.0037195 | 0.0037195 | 0.0015063 | 7.35e-05 | 7.35e-05 | 7.35e-05 | 9.8565e-05 | 5.9139e-05 | 0.00041062 | 0.00041062 | 0.00017817 | 0.00017817 | 0.00047184 | 0.00047184 | 8.6399e-05 | 8.6399e-05 | 0.033044 | 0.010824 | 0.25154 | 0.015429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39388
35 | Phenol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | Phosphorus | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | POM (Total) | 0.0031773 | 0.0031773 | 0.0031773 | 0.0031773 | 0.0031773 | 0.0031773 | 0.0023915 | 0.0023915 | 0.0023915 | 0.0023915 | 0.0023915 | 0.0023915 | 0.0021979 | 0.0021979 | 0.0021979 | 0.0021979 | 0.0021979 | 0.0021979 | 0.0015029 | 7.3615e-05 | 7.3615e-05 | 7.3615e-05 | 9.8719e-05 | 5.9231e-05 | 3.163e-07 | 3.163e-07 | 1.3725e-07 | 1.3725e-07 | 3.6346e-07 | 3.6346e-07 | 6.6554e-08 | 6.6554e-08 | 2.5454e-05 | 8.338e-06 | 0.00019377 | 1.1885e-05 | 0.00082408 | 0.00082408 | 0 | 4.6148e-07 | 4.6148e-07 | 4.3349e-06 | 3.5823e-06 | 9.5593e-05 | 9.5593e-05 | 0 | 0.050571
38 | POM 2-Methylnaphthalene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8279e-05 | 2.8279e-05 | 0 | 1.5837e-08 | 1.5837e-08 | 1.4876e-07 | 1.2293e-07 | 3.2804e-06 | 3.2804e-06 | 0 | 6.3423e-05
39 | POM 3-Methylcholanthrene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1661e-06 | 2.1661e-06 | 0 | 1.213e-09 | 1.213e-09 | 1.1394e-08 | 9.4161e-09 | 2.5127e-07 | 2.5127e-07 | 0 | 4.8579e-06
40 | POM 7,12-Dimethylbenz(a)anthracene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8893e-05 | 1.8893e-05 | 0 | 1.058e-08 | 1.058e-08 | 9.9383e-08 | 8.2129e-08 | 2.1916e-06 | 2.1916e-06 | 0 | 4.2372e-05
41 | POM Acenaphthene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3251e-05 | 6.2125e-07 | 6.2125e-07 | 6.2125e-07 | 8.3311e-07 | 4.9987e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1661e-06 | 2.1661e-06 | 0 | 1.213e-09 | 1.213e-09 | 1.1394e-08 | 9.4161e-09 | 2.5127e-07 | 2.5127e-07 | 0 | 4.1306e-05
42 | POM Acenaphthylene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5579e-05 | 2.2137e-06 | 2.2137e-06 | 2.2137e-06 | 2.9687e-06 | 1.7812e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1661e-06 | 2.1661e-06 | 0 | 1.213e-09 | 1.213e-09 | 1.1394e-08 | 9.4161e-09 | 2.5127e-07 | 2.5127e-07 | 0 | 8.1828e-05
43 | POM Anthracene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7392e-06 | 8.1813e-07 | 8.1813e-07 | 8.1813e-07 | 1.0971e-06 | 6.5827e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8881e-06 | 2.8881e-06 | 0 | 1.6173e-09 | 1.6173e-09 | 1.5192e-08 | 1.2555e-08 | 3.3502e-07 | 3.3502e-07 | 0 | 1.9426e-05
44 | POM Benz(a)anthracene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4193e-06 | 7.35e-07 | 7.35e-07 | 7.35e-07 | 9.8565e-07 | 5.9139e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1661e-06 | 2.1661e-06 | 0 | 1.213e-09 | 1.213e-09 | 1.1394e-08 | 9.4161e-09 | 2.5127e-07 | 2.5127e-07 | 0 | 1.3059e-05
45 | POM Benzo(a)pyrene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.826e-06 | 8.225e-08 | 8.225e-08 | 8.225e-08 | 1.103e-07 | 6.6179e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4441e-06 | 1.4441e-06 | 0 | 8.0867e-10 | 8.0867e-10 | 7.5961e-09 | 6.2774e-09 | 1.6751e-07 | 1.6751e-07 | 0 | 5.4878e-06
46 | POM Benzo(b)fluoranthene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.8865e-06 | 4.3356e-08 | 4.3356e-08 | 4.3356e-08 | 5.8142e-08 | 3.4885e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1661e-06 | 2.1661e-06 | 0 | 1.213e-09 | 1.213e-09 | 1.1394e-08 | 9.4161e-09 | 2.5127e-07 | 2.5127e-07 | 0 | 1.2968e-05
47 | POM Benzo(g,h,i)perylene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9504e-06 | 2.1394e-07 | 2.1394e-07 | 2.1394e-07 | 2.8689e-07 | 1.7214e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4441e-06 | 1.4441e-06 | 0 | 8.0867e-10 | 8.0867e-10 | 7.5961e-09 | 6.2774e-09 | 1.6751e-07 | 1.6751e-07 | 0 | 8.2899e-06
48 | POM Benzo(k)fluoranthene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5489e-06 | 6.7812e-08 | 6.7812e-08 | 6.7812e-08 | 9.0938e-08 | 5.4563e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1661e-06 | 2.1661e-06 | 0 | 1.213e-09 | 1.213e-09 | 1.1394e-08 | 9.4161e-09 | 2.5127e-07 | 2.5127e-07 | 0 | 6.7558e-06
49 | POM Chrysene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0871e-05 | 1.5444e-07 | 1.5444e-07 | 1.5444e-07 | 2.071e-07 | 1.2426e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1661e-06 | 2.1661e-06 | 0 | 1.213e-09 | 1.213e-09 | 1.1394e-08 | 9.4161e-09 | 2.5127e-07 | 2.5127e-07 | 0 | 1.6523e-05
50 | POM Dibenz(a,h)anthracene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4583e-06 | 2.5506e-07 | 2.5506e-07 | 2.5506e-07 | 3.4204e-07 | 2.0523e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4441e-06 | 1.4441e-06 | 0 | 8.0867e-10 | 8.0867e-10 | 7.5961e-09 | 6.2774e-09 | 1.6751e-07 | 1.6751e-07 | 0 | 7.0094e-06
51 | POM Fluoranthene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8633e-05 | 3.3294e-06 | 3.3294e-06 | 3.3294e-06 | 4.4648e-06 | 2.6789e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4898e-06 | 3.4898e-06 | 0 | 1.9543e-09 | 1.9543e-09 | 1.8357e-08 | 1.517e-08 | 4.0482e-07 | 4.0482e-07 | 0 | 5.3592e-05
52 | POM Fluorene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0944e-05 | 1.2862e-05 | 1.2862e-05 | 1.2862e-05 | 1.7249e-05 | 1.0349e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2491e-06 | 3.2491e-06 | 0 | 1.8195e-09 | 1.8195e-09 | 1.7091e-08 | 1.4124e-08 | 3.769e-07 | 3.769e-07 | 0 | 0.00016442
53 | POM Indeno(1,2,3-c,d)pyrene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9415e-06 | 1.6406e-07 | 1.6406e-07 | 1.6406e-07 | 2.2001e-07 | 1.3201e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1661e-06 | 2.1661e-06 | 0 | 1.213e-09 | 1.213e-09 | 1.1394e-08 | 9.4161e-09 | 2.5127e-07 | 2.5127e-07 | 0 | 8.6436e-06
54 | POM Naphthalene | 0.0031773 | 0.0031773 | 0.0031773 | 0.0031773 | 0.0031773 | 0.0031773 | 0.0023915 | 0.0023915 | 0.0023915 | 0.0023915 | 0.0023915 | 0.0023915 | 0.0021979 | 0.0021979 | 0.0021979 | 0.0021979 | 0.0021979 | 0.0021979 | 0.00092365 | 3.71e-05 | 3.71e-05 | 3.71e-05 | 4.9752e-05 | 2.9851e-05 | 0.00032263 | 0.00032263 | 0.00013999 | 0.00013999 | 0.00037073 | 0.00037073 | 6.7885e-05 | 6.7885e-05 | 0.025963 | 0.0085048 | 0.19764 | 0.012123 | 0.00071962 | 0.00071962 | 0 | 4.0299e-07 | 4.0299e-07 | 3.7854e-06 | 3.1282e-06 | 8.3476e-05 | 8.3476e-05 | 0 | 0.29536
55 | POM Phenanthrene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00028988 | 1.2862e-05 | 1.2862e-05 | 1.2862e-05 | 1.7249e-05 | 1.0349e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0096e-05 | 2.0096e-05 | 0 | 1.1254e-08 | 1.1254e-08 | 1.0571e-07 | 8.736e-08 | 2.3312e-06 | 2.3312e-06 | 0 | 0.00040114
56 | POM Pyrene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.636e-05 | 2.0913e-06 | 2.0913e-06 | 2.0913e-06 | 2.8044e-06 | 1.6826e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8966e-06 | 5.8966e-06 | 0 | 3.3021e-09 | 3.3021e-09 | 3.1018e-08 | 2.5633e-08 | 6.84e-07 | 6.84e-07 | 0 | 5.0345e-05
57 | Propional[dehyde] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | Propylene Oxide | 0.070877 | 0.070877 | 0.070877 | 0.070877 | 0.070877 | 0.070877 | 0.053348 | 0.053348 | 0.053348 | 0.053348 | 0.053348 | 0.053348 | 0.04903 | 0.04903 | 0.04903 | 0.04903 | 0.04903 | 0.04903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0395
59 | Selenium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60 | Styrene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | Tetrachloroethylene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | Toluene | 0.31773 | 0.31773 | 0.31773 | 0.31773 | 0.31773 | 0.31773 | 0.23915 | 0.23915 | 0.23915 | 0.23915 | 0.23915 | 0.23915 | 0.21979 | 0.21979 | 0.21979 | 0.21979 | 0.21979 | 0.21979 | 0.0019965 | 0.00017894 | 0.00017894 | 0.00017894 | 0.00023996 | 0.00014398 | 0.0017011 | 0.0017011 | 0.00073813 | 0.00073813 | 0.0019547 | 0.0019547 | 0.00035794 | 0.00035794 | 0.1369 | 0.044843 | 1.0421 | 0.063922 | 0.0040112 | 0.0040112 | 0 | 2.2463e-06 | 2.2463e-06 | 2.11e-05 | 1.7437e-05 | 0.0004653 | 0.0004653 | 0 | 5.9692
63 | Trichloroethylene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64 | Vinyl Chloride | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65 | Vinylidene Chloride | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66 | Xylenes(m,p,o) | 0.15642 | 0.15642 | 0.15642 | 0.15642 | 0.15642 | 0.15642 | 0.11773 | 0.11773 | 0.11773 | 0.11773 | 0.11773 | 0.11773 | 0.1082 | 0.1082 | 0.1082 | 0.1082 | 0.1082 | 0.1082 | 0.0013713 | 0.00012469 | 0.00012469 | 0.00012469 | 0.00016721 | 0.00010033 | 0.00085057 | 0.00085057 | 0.00036907 | 0.00036907 | 0.00097737 | 0.00097737 | 0.00017897 | 0.00017897 | 0.068449 | 0.022422 | 0.52106 | 0.031961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9448
67 | CDD/CDF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SOURCE TOTAL (tpy) | 2.5108 | 2.5108 | 2.5108 | 2.5108 | 2.5108 | 2.5108 | 1.8899 | 1.8899 | 1.8899 | 1.8899 | 1.8899 | 1.8899 | 1.7369 | 1.7369 | 1.7369 | 1.7369 | 1.7369 | 1.7369 | 0.012686 | 0.0017683 | 0.0017683 | 0.0017683 | 0.0023713 | 0.0014228 | 0.08667 | 0.08667 | 0.037607 | 0.037607 | 0.099591 | 0.099591 | 0.018236 | 0.018236 | 6.9747 | 2.2847 | 53.0941 | 3.2567 | 2.22 | 2.22 | 0 | 0.0012432 | 0.0012432 | 0.011678 | 0.0096504 | 0.25752 | 0.25752 | 0 | 107.9207
|  |  | FACILITY TOTAL | 107.9207
|  |  | CT TOTAL (All Fuels) | 36.8256
|  |  | HEATER TOTAL (All Fuels) | 4.9789
|  |  | ICE TOTAL (All fuels) | 0.021785
|  |  | SUM CTs & ICE (All Fuels) | 36.8256
|  |  | FLARE TOTAL | 66.0945
|  |  | INCINERATOR TOTAL | 0
|  |  | BURNER TOTAL | 0
|  |  | TANK TOTAL | 0
|  |  | FUGITIVE TOTAL | 0

## GTP Emission Factor Summary
| Short-Term Maximum |  | Annual |  | Short-Term Maximum |  | Annual |  |  |  | Short-Term Maximum |  | Annual
| Treated Gas Compressor Turbine Primary Stack |  | Treated Gas Compressor Turbine Primary Stack |  | CO2 Compressor Turbine Primary Stack |  | CO2 Compressor Turbine Primary Stack |  | Turbine Supplemental Firing |  | Power Generator Turbine |  | Power Generator Turbine |  | Black Start Diesel Generator |  | Main Diesel Firewater Pump |  | Dormitory Emergency Diesel Generator |  | Communications Tower |  | Flares |  | Common Utility Heater |  | Buyback Gas Bath Heater |  | Operations Camp Heater
Pollutant | Emission Factor | Units | Emission Factor | Units | Emission Factor | Units | Emission Factor | Units | Emission Factor | Units | Emission Factor | Units | Emission Factor | Units | Emission Factor | Units | Emission Factor | Units | Emission Factor | Units | Emission Factor | Units | Emission Factor | Units | Emission Factor | Units | Emission Factor | Units | Emission Factor | Units
NOx | 15 | ppmvd @15% O2 | 12 | ppmvd @15% O2 | 15 | ppmvd @15% O2 | 15 | ppmvd @15% O2 | 0.08 | lb/MMBtu | 15 | ppmvd @15% O2 | 12 | ppmvd @15% O2 | 3.2624 | g/hp-hr | 3.5625 | g/hp-hr | 3.5421 | g/hp-hr | 3.5421 | g/hp-hr | 0.068 | lb/MMBtu | 0.08 | lb/MMBtu | 0.08 | lb/MMBtu | 0.08 | lb/MMBtu
CO | 15 | ppmvd @15% O2 | 15 | ppmvd @15% O2 | 67 | ppmvd @15% O2 | 25 | ppmvd @15% O2 | 0.08 | lb/MMBtu | 15 | ppmvd @15% O2 | 15 | ppmvd @15% O2 | 3.2624 | g/hp-hr | 3.25 | g/hp-hr | 3.2624 | g/hp-hr | 3.2624 | g/hp-hr | 0.31 | lb/MMBtu | 0.082353 | lb/MMBtu | 0.082353 | lb/MMBtu | 0.082353 | lb/MMBtu
VOC | 0.0022174 | lb/MMBtu | 0.0022174 | lb/MMBtu | 0.0022174 | lb/MMBtu | 0.0022174 | lb/MMBtu | 0.015 | lb/MMBtu | 0.0022174 | lb/MMBtu | 0.0022174 | lb/MMBtu | 0.1771 | g/hp-hr | 0.1875 | g/hp-hr | 0.18643 | g/hp-hr | 0.18643 | g/hp-hr | 0.57 | lb/MMBtu | 0.006 | lb/MMBtu | 0.006 | lb/MMBtu | 0.006 | lb/MMBtu
PM10 | 0.0069688 | lb/MMBtu | 0.0069688 | lb/MMBtu | 0.0069688 | lb/MMBtu | 0.0069688 | lb/MMBtu | 0.005 | lb/MMBtu | 0.0069688 | lb/MMBtu | 0.0069688 | lb/MMBtu | 0.037285 | g/hp-hr | 0.1875 | g/hp-hr | 0.18643 | g/hp-hr | 0.18643 | g/hp-hr | 40 | µg/L | 0.007451 | lb/MMBtu | 0.007451 | lb/MMBtu | 0.007451 | lb/MMBtu
PM2.5 | 0.0069688 | lb/MMBtu | 0.0069688 | lb/MMBtu | 0.0069688 | lb/MMBtu | 0.0069688 | lb/MMBtu | 0.005 | lb/MMBtu | 0.0069688 | lb/MMBtu | 0.0069688 | lb/MMBtu | 0.037285 | g/hp-hr | 0.1875 | g/hp-hr | 0.18643 | g/hp-hr | 0.18643 | g/hp-hr | 40 | µg/L | 0.007451 | lb/MMBtu | 0.007451 | lb/MMBtu | 0.007451 | lb/MMBtu
Fuel Sulfur Normal Operation | 16 | ppmv | 16 | ppmv | 16 | ppmv | 16 | ppmv | 16 | ppmv | 16 | ppmv | 16 | ppmv | 15 | ppmv | 15 | ppmv | 15 | ppmv | 15 | ppmv | 16 | ppmv | 16 | ppmv | 16 | ppmv | 16 | ppmv
Fuel Sulfur Maximum | 96 | ppmv | 96 | ppmv | 96 | ppmv | 96 | ppmv | 96 | ppmv | 96 | ppmv | 96 | ppmv | [8 empty] | 96 | ppmv | 96 | ppmv | 96 | ppmv | 96 | ppmv
CO2 | 53.06 | kg/MMBtu | 53.06 | kg/MMBtu | 53.06 | kg/MMBtu | 53.06 | kg/MMBtu | 53.06 | kg/MMBtu | 53.06 | kg/MMBtu | 53.06 | kg/MMBtu | 73.96 | kg/MMBtu | 73.96 | kg/MMBtu | 73.96 | kg/MMBtu | 73.96 | kg/MMBtu | 53.06 | kg/MMBtu | 53.06 | kg/MMBtu | 53.06 | kg/MMBtu | 53.06 | kg/MMBtu
CH4 | 0.001 | kg/MMBtu | 0.001 | kg/MMBtu | 0.001 | kg/MMBtu | 0.001 | kg/MMBtu | 0.001 | kg/MMBtu | 0.001 | kg/MMBtu | 0.001 | kg/MMBtu | 0.003 | kg/MMBtu | 0.003 | kg/MMBtu | 0.003 | kg/MMBtu | 0.003 | kg/MMBtu | 0.001 | kg/MMBtu | 0.001 | kg/MMBtu | 0.001 | kg/MMBtu | 0.001 | kg/MMBtu
N2O | 0.0001 | kg/MMBtu | 0.0001 | kg/MMBtu | 0.0001 | kg/MMBtu | 0.0001 | kg/MMBtu | 0.0001 | kg/MMBtu | 0.0001 | kg/MMBtu | 0.0001 | kg/MMBtu | 0.0006 | kg/MMBtu | 0.0006 | kg/MMBtu | 0.0006 | kg/MMBtu | 0.0006 | kg/MMBtu | 0.0001 | kg/MMBtu | 0.0001 | kg/MMBtu | 0.0001 | kg/MMBtu | 0.0001 | kg/MMBtu
1,1,2,2-Tetrachloroethane
1,1,2-Trichloroethane
1,3-Butadiene | 4.3e-07 | lb/MMBtu | 4.3e-07 | lb/MMBtu | 4.3e-07 | lb/MMBtu | 4.3e-07 | lb/MMBtu | 4.3e-07 | lb/MMBtu | 4.3e-07 | lb/MMBtu | 4.3e-07 | lb/MMBtu |  |  | 3.91e-05 | lb/MMBtu | 3.91e-05 | lb/MMBtu | 3.91e-05 | lb/MMBtu
1,3-Dichloropropene
1,4-Dichlorobenzene
2,2,4-Trimethylpentane
Acetaldehyde | 4e-05 | lb/MMBtu | 4e-05 | lb/MMBtu | 4e-05 | lb/MMBtu | 4e-05 | lb/MMBtu | 4e-05 | lb/MMBtu | 4e-05 | lb/MMBtu | 4e-05 | lb/MMBtu | 2.52e-05 | lb/MMBtu | 0.000767 | lb/MMBtu | 0.000767 | lb/MMBtu | 0.000767 | lb/MMBtu | 4.2157e-05 | lb/MMBtu
Acrolein | 6.4e-06 | lb/MMBtu | 6.4e-06 | lb/MMBtu | 6.4e-06 | lb/MMBtu | 6.4e-06 | lb/MMBtu | 6.4e-06 | lb/MMBtu | 6.4e-06 | lb/MMBtu | 6.4e-06 | lb/MMBtu | 7.88e-06 | lb/MMBtu | 9.25e-05 | lb/MMBtu | 9.25e-05 | lb/MMBtu | 9.25e-05 | lb/MMBtu | 9.8039e-06 | lb/MMBtu
Antimony
Arsenic
Benzene | 1.2e-05 | lb/MMBtu | 1.2e-05 | lb/MMBtu | 1.2e-05 | lb/MMBtu | 1.2e-05 | lb/MMBtu | 1.2e-05 | lb/MMBtu | 1.2e-05 | lb/MMBtu | 1.2e-05 | lb/MMBtu | 0.000776 | lb/MMBtu | 0.000933 | lb/MMBtu | 0.000933 | lb/MMBtu | 0.000933 | lb/MMBtu | 0.00015588 | lb/MMBtu | 2.0588e-06 | lb/MMBtu | 2.0588e-06 | lb/MMBtu | 2.0588e-06 | lb/MMBtu
Beryllium
Biphenyl
Cadmium
Carbon Tetrachloride
Chlorobenzene
Chloroform
Chromium
Cobalt
Dibutylphthalate
Ethylbenzene | 3.2e-05 | lb/MMBtu | 3.2e-05 | lb/MMBtu | 3.2e-05 | lb/MMBtu | 3.2e-05 | lb/MMBtu | 3.2e-05 | lb/MMBtu | 3.2e-05 | lb/MMBtu | 3.2e-05 | lb/MMBtu | [8 empty] | 0.0014157 | lb/MMBtu
Ethylene Dibromide
Ethylene Dichloride
Formaldehyde | 0.00071 | lb/MMBtu | 0.00071 | lb/MMBtu | 0.00071 | lb/MMBtu | 0.00071 | lb/MMBtu | 0.00071 | lb/MMBtu | 0.00071 | lb/MMBtu | 0.00071 | lb/MMBtu | 7.89e-05 | lb/MMBtu | 0.00118 | lb/MMBtu | 0.00118 | lb/MMBtu | 0.00118 | lb/MMBtu | 0.0011461 | lb/MMBtu | 7.3529e-05 | lb/MMBtu | 7.3529e-05 | lb/MMBtu | 7.3529e-05 | lb/MMBtu
HCl
Lead | [24 empty] | 4.902e-07 | lb/MMBtu | 4.902e-07 | lb/MMBtu | 4.902e-07 | lb/MMBtu
Manganese
Mercury
Methanol
Methylene Chloride
n-Hexane | [22 empty] | 2.8431e-05 | lb/MMBtu | 0.0017647 | lb/MMBtu | 0.0017647 | lb/MMBtu | 0.0017647 | lb/MMBtu
Nickel
PAHs | 2.2e-06 | lb/MMBtu | 2.2e-06 | lb/MMBtu | 2.2e-06 | lb/MMBtu | 2.2e-06 | lb/MMBtu | 2.2e-06 | lb/MMBtu | 2.2e-06 | lb/MMBtu | 2.2e-06 | lb/MMBtu | 0.000212 | lb/MMBtu | 0.000168 | lb/MMBtu | 0.000168 | lb/MMBtu | 0.000168 | lb/MMBtu | 1.3725e-05 | lb/MMBtu
Phenol
Phosphorus
POM 2-Methylnaphthalene | [24 empty] | 2.35e-08 | lb/MMBtu | 2.35e-08 | lb/MMBtu | 2.35e-08 | lb/MMBtu
POM 3-Methylcholanthrene | [24 empty] | 1.8e-09 | lb/MMBtu | 1.8e-09 | lb/MMBtu | 1.8e-09 | lb/MMBtu
POM 7,12-Dimethylbenz(a)anthracene | [24 empty] | 1.57e-08 | lb/MMBtu | 1.57e-08 | lb/MMBtu | 1.57e-08 | lb/MMBtu
POM Acenaphthene | [14 empty] | 4.68e-06 | lb/MMBtu | 1.42e-06 | lb/MMBtu | 1.42e-06 | lb/MMBtu | 1.42e-06 | lb/MMBtu |  |  | 1.8e-09 | lb/MMBtu | 1.8e-09 | lb/MMBtu | 1.8e-09 | lb/MMBtu
POM Acenaphthylene | [14 empty] | 9.23e-06 | lb/MMBtu | 5.06e-06 | lb/MMBtu | 5.06e-06 | lb/MMBtu | 5.06e-06 | lb/MMBtu |  |  | 1.8e-09 | lb/MMBtu | 1.8e-09 | lb/MMBtu | 1.8e-09 | lb/MMBtu
POM Anthracene | [14 empty] | 1.23e-06 | lb/MMBtu | 1.87e-06 | lb/MMBtu | 1.87e-06 | lb/MMBtu | 1.87e-06 | lb/MMBtu |  |  | 2.4e-09 | lb/MMBtu | 2.4e-09 | lb/MMBtu | 2.4e-09 | lb/MMBtu
POM Benz(a)anthracene | [14 empty] | 6.22e-07 | lb/MMBtu | 1.68e-06 | lb/MMBtu | 1.68e-06 | lb/MMBtu | 1.68e-06 | lb/MMBtu |  |  | 1.8e-09 | lb/MMBtu | 1.8e-09 | lb/MMBtu | 1.8e-09 | lb/MMBtu
POM Benzo(a)pyrene | [14 empty] | 2.57e-07 | lb/MMBtu | 1.88e-07 | lb/MMBtu | 1.88e-07 | lb/MMBtu | 1.88e-07 | lb/MMBtu |  |  | 1.2e-09 | lb/MMBtu | 1.2e-09 | lb/MMBtu | 1.2e-09 | lb/MMBtu
POM Benzo(b)fluoranthene | [14 empty] | 1.11e-06 | lb/MMBtu | 9.91e-08 | lb/MMBtu | 9.91e-08 | lb/MMBtu | 9.91e-08 | lb/MMBtu |  |  | 1.8e-09 | lb/MMBtu | 1.8e-09 | lb/MMBtu | 1.8e-09 | lb/MMBtu
POM Benzo(g,h,i)perylene | [14 empty] | 5.56e-07 | lb/MMBtu | 4.89e-07 | lb/MMBtu | 4.89e-07 | lb/MMBtu | 4.89e-07 | lb/MMBtu |  |  | 1.2e-09 | lb/MMBtu | 1.2e-09 | lb/MMBtu | 1.2e-09 | lb/MMBtu
POM Benzo(k)fluoranthene | [14 empty] | 2.18e-07 | lb/MMBtu | 1.55e-07 | lb/MMBtu | 1.55e-07 | lb/MMBtu | 1.55e-07 | lb/MMBtu |  |  | 1.8e-09 | lb/MMBtu | 1.8e-09 | lb/MMBtu | 1.8e-09 | lb/MMBtu
POM Chrysene | [14 empty] | 1.53e-06 | lb/MMBtu | 3.53e-07 | lb/MMBtu | 3.53e-07 | lb/MMBtu | 3.53e-07 | lb/MMBtu |  |  | 1.8e-09 | lb/MMBtu | 1.8e-09 | lb/MMBtu | 1.8e-09 | lb/MMBtu
POM Dibenz(a,h)anthracene | [14 empty] | 3.46e-07 | lb/MMBtu | 5.83e-07 | lb/MMBtu | 5.83e-07 | lb/MMBtu | 5.83e-07 | lb/MMBtu |  |  | 1.2e-09 | lb/MMBtu | 1.2e-09 | lb/MMBtu | 1.2e-09 | lb/MMBtu
POM Fluoranthene | [14 empty] | 4.03e-06 | lb/MMBtu | 7.61e-06 | lb/MMBtu | 7.61e-06 | lb/MMBtu | 7.61e-06 | lb/MMBtu |  |  | 2.9e-09 | lb/MMBtu | 2.9e-09 | lb/MMBtu | 2.9e-09 | lb/MMBtu
POM Fluorene | [14 empty] | 1.28e-05 | lb/MMBtu | 2.94e-05 | lb/MMBtu | 2.94e-05 | lb/MMBtu | 2.94e-05 | lb/MMBtu |  |  | 2.7e-09 | lb/MMBtu | 2.7e-09 | lb/MMBtu | 2.7e-09 | lb/MMBtu
POM Indeno(1,2,3-c,d)pyrene | [14 empty] | 4.14e-07 | lb/MMBtu | 3.75e-07 | lb/MMBtu | 3.75e-07 | lb/MMBtu | 3.75e-07 | lb/MMBtu |  |  | 1.8e-09 | lb/MMBtu | 1.8e-09 | lb/MMBtu | 1.8e-09 | lb/MMBtu
POM Naphthalene | 1.3e-06 | lb/MMBtu | 1.3e-06 | lb/MMBtu | 1.3e-06 | lb/MMBtu | 1.3e-06 | lb/MMBtu | 1.3e-06 | lb/MMBtu | 1.3e-06 | lb/MMBtu | 1.3e-06 | lb/MMBtu | 0.00013 | lb/MMBtu | 8.48e-05 | lb/MMBtu | 8.48e-05 | lb/MMBtu | 8.48e-05 | lb/MMBtu | 1.0784e-05 | lb/MMBtu | 5.98e-07 | lb/MMBtu | 5.98e-07 | lb/MMBtu | 5.98e-07 | lb/MMBtu
POM Phenanthrene | [14 empty] | 4.08e-05 | lb/MMBtu | 2.94e-05 | lb/MMBtu | 2.94e-05 | lb/MMBtu | 2.94e-05 | lb/MMBtu |  |  | 1.67e-08 | lb/MMBtu | 1.67e-08 | lb/MMBtu | 1.67e-08 | lb/MMBtu
POM Pyrene | [14 empty] | 3.71e-06 | lb/MMBtu | 4.78e-06 | lb/MMBtu | 4.78e-06 | lb/MMBtu | 4.78e-06 | lb/MMBtu |  |  | 4.9e-09 | lb/MMBtu | 4.9e-09 | lb/MMBtu | 4.9e-09 | lb/MMBtu
Propional[dehyde]
Propylene Oxide | 2.9e-05 | lb/MMBtu | 2.9e-05 | lb/MMBtu | 2.9e-05 | lb/MMBtu | 2.9e-05 | lb/MMBtu | 2.9e-05 | lb/MMBtu | 2.9e-05 | lb/MMBtu | 2.9e-05 | lb/MMBtu
Selenium
Styrene
Tetrachloroethylene
Toluene | 0.00013 | lb/MMBtu | 0.00013 | lb/MMBtu | 0.00013 | lb/MMBtu | 0.00013 | lb/MMBtu | 0.00013 | lb/MMBtu | 0.00013 | lb/MMBtu | 0.00013 | lb/MMBtu | 0.000281 | lb/MMBtu | 0.000409 | lb/MMBtu | 0.000409 | lb/MMBtu | 0.000409 | lb/MMBtu | 5.6863e-05 | lb/MMBtu | 3.3333e-06 | lb/MMBtu | 3.3333e-06 | lb/MMBtu | 3.3333e-06 | lb/MMBtu
Trichloroethylene
Vinyl Chloride
Vinylidene Chloride
Xylenes(m,p,o) | 6.4e-05 | lb/MMBtu | 6.4e-05 | lb/MMBtu | 6.4e-05 | lb/MMBtu | 6.4e-05 | lb/MMBtu | 6.4e-05 | lb/MMBtu | 6.4e-05 | lb/MMBtu | 6.4e-05 | lb/MMBtu | 0.000193 | lb/MMBtu | 0.000285 | lb/MMBtu | 0.000285 | lb/MMBtu | 0.000285 | lb/MMBtu | 2.8431e-05 | lb/MMBtu
CDD/CDF

## GTP Annual Fuel Consumption
Gas-Fired Equipment (Fuel Gas Users) | Rated Duty (HHV) | Daily Average Fuel Flow
| MMBtu/hr | MMSCFD | GTP Fuel
Train 1a Treated Gas Compressor Turbine | 386 | 8.6017 | Gross (Btu/lbm) | 23129
Supplemental Firing | 189.0245 | 4.2122 | Gross (Btu/scf) | 1077
Train 1b Treated Gas Compressor Turbine | 386 | 8.6017 | Gross (MMBtu/gal) | 0.14425
Supplemental Firing | 189.0245 | 4.2122 | Gross (Btu/lb) | 20229
Train 2a Treated Gas Compressor Turbine | 386 | 8.6017
Supplemental Firing | 189.0245 | 4.2122 | Heat Release Equivalents
Train 2b Treated Gas Compressor Turbine | 386 | 8.6017 | 1 | CO2
Supplemental Firing | 189.0245 | 4.2122 | 25 | CH4
Train 3a Treated Gas Compressor Turbine | 386 | 8.6017 | 298 | N2O
Supplemental Firing | 189.0245 | 4.2122
Train3b Treated Gas Compressor Turbine | 386 | 8.6017 | GHG Emissions from 40 CFR 98
Supplemental Firing | 189.0245 | 4.2122 |  | Gas | Diesel
Train 1a CO2 Compressor Turbine | 291 | 6.4847 | CO2 | 53.06 | 73.96 | kg/MMBtu
Supplemental Firing | 141.7684 | 3.1592 | CH4 | 0.001 | 0.003 | kg/MMBtu
Train 1b CO2 Compressor Turbine | 291 | 6.4847 | N2O | 0.0001 | 0.0006 | kg/MMBtu
Supplemental Firing | 141.7684 | 3.1592
Train 2a CO2 Compressor Turbine | 291 | 6.4847 | Conversion Table
Supplemental Firing | 141.7684 | 3.1592 | 1 tonnes = | 1000 | kg
Train 2b CO2 Compressor Turbine | 291 | 6.4847 | 1 yr = | 8760 | hr
Supplemental Firing | 141.7684 | 3.1592 | 1 yr = | 500 | hr
Train 3a CO2 Compressor Turbine | 291 | 6.4847
Supplemental Firing | 141.7684 | 3.1592
Train 3b CO2 Compressor Turbine | 291 | 6.4847
Supplemental Firing | 141.7684 | 3.1592
Power Generation Turbines | 386 | 8.6017
Power Generation Turbines | 386 | 8.6017
Power Generation Turbines | 386 | 8.6017
Power Generation Turbines | 386 | 8.6017
Power Generation Turbines | 386 | 8.6017
Power Generation Turbines | 386 | 8.6017
LP CO2 Flare East Pilot/Purge (3 Flares) | 6.8303 | 0.15221
LP CO2 Flare West Pilot/Purge (3 Flares) | 6.8303 | 0.15221
HP CO2 Flare East Pilot/Purge | 2.9637 | 0.066043
HP CO2 Flare West Pilot/Purge | 2.9637 | 0.066043
HP Hydrocarbon Flare East Pilot/Purge | 7.8485 | 0.1749
HP Hydrocarbon Flare West Pilot/Purge | 7.8485 | 0.1749
LP Hydrocarbon Flare East Pilot/Purge | 1.4372 | 0.032026
LP Hydrocarbon Flare West Pilot/Purge | 1.4372 | 0.032026
LP CO2 Flare East Assist Gas (For Max Case) | 9558.375 | 213
HP CO2 Flare East Assist Gas (For Max Case) | 3141.25 | 70
Building Heat Medium Heater | 274.7449 | 6.1224
Building Heat Medium Heater | 274.7449 | 6.1224
Building Heat Medium Heater (spare) | 0 | 0
Buyback Gas Bath Heater Pre-Let Down Heater Standby | 0.15386 | 0.0034286
Buyback Gas Bath Heater Post-Let Down Heater Standby | 0.15386 | 0.0034286
Buyback Gas Bath Heater Pre-Let Down Heater MAX | 25.3205 | 0.56424
Buyback Gas Bath Heater Post-Let Down Heater MAX | 20.9246 | 0.46629
Operations Camp Heater | 31.8704 | 0.7102
Operations Camp Heater | 31.8704 | 0.7102
Operations Camp Heater (spare) | 0 | 0
Total Fuel Gas Consumption | 21760.3248 | 484.9097
Liquid-Driven Equipment (Diesel Users) | Rated Duty (HHV) | Daily Average Diesel Flow
| MMBtu/hr | gal/day
Black Start Diesel Generator (2500 kW) | 28.42 | 4728.5582
Main Diesel Firewater Pump (250 hp) | 1.75 | 291.1674
Main Diesel Firewater Pump (250 hp) | 1.75 | 291.1674
Main Diesel Firewater Pump (250 hp) | 1.75 | 291.1674
Dormitory Emergency Diesel Generator (250 kW) | 2.3468 | 390.4618
Communications Tower (150 kW) | 1.4081 | 234.2771
Mobile Equipment Emissions (Normal Operation) | 6.531 | 1086.6411
Non-Road/Portable Equipment Emissions (Normal Operation) | 27.324 | 4546.2042
Total Diesel Consumption | 71.2799 | 11859.6445
Additional GHG Emission Sources not from Fuel Gas or Diesel Consumption
LP CO2 Flare East (Max Case CO2)
HP CO2 Flare East (Max Case CO2)
HP Hydrocarbon Flare East (Max Case)
LP Hydrocarbon Flare East (Max Case)
Tank Emissions
Fugitive Emissions

## AQRV Speciation
AQRV Speciation Table
Equipment and Fuel Type | PMF Ratio | EC % Filterable |  | SOA % Condensable |  | Reference
|  | PM2.5 | PM10 | PM2.5 | PM10
Mobile Source ¦ Diesel | 0 | 9.98% | 10.85% | 90.02% | 89.15% | EPA-420-R-15-022 Speciation of Total Organic Gas and Particulate Matter Emissions from On-road Vehicles in MOVES2014 Table C-10 and Table D-1
Turbine¦Gas | 0 | 28.79% | 28.79% | 71.21% | 71.21% | AP42 Table 3.1-2a
Turbine¦Diesel | 0 | 37.39% | 37.39% | 62.61% | 62.61% | AP42 Table 3.1-2a
Generator¦Gas | 0 | 48.94% | 48.94% | 51.06% | 51.06% | AP42 Table 3.2-3
Generator¦Diesel | 0 | 86.15% | 86.56% | 13.85% | 13.44% | AP42 Table 3.4-2
Compressor¦Gas | 0 | 48.94% | 48.94% | 51.06% | 51.06% | AP42 Table 3.2-3
Compressor¦Diesel | 0 | 86.15% | 86.56% | 13.85% | 13.44% | AP42 Table 3.4-2 (Smaller than 600 hp, but no condensable info in AP42 3.3)
Heater¦Gas | 0 | 25% | 25% | 75% | 75% | AP42 Table 1.4-2
Heater¦Diesel | 0 | 38.97% | 45.38% | 61.03% | 54.62% | AP42 Table 1.3-2 and Table 1.3-7
Boiler¦Gas | 0 | 25% | 25% | 75% | 75% | AP42 Table 1.4-2
Boiler¦Diesel | 0 | 38.97% | 45.38% | 61.03% | 54.62% | AP42 Table 1.3-2 and Table 1.3-7
Pump¦Gas | 0 | 48.94% | 48.94% | 51.06% | 51.06% | AP42 Table 3.2-3
Pump¦Diesel | 0 | 86.15% | 86.56% | 13.85% | 13.44% | AP42 Table 3.4-2 (Smaller than 600 hp, but no condensable info in AP42 3.3)
Flare¦Gas | 0 | 25% | 25% | 75% | 75% | AP42 Table 1.4-2 (pilot/purge fuel gas, assumed as external combustion source)
Cooling Tower¦N/A | 0 | 0% | 0% | 100% | 100% | The particulates from cooling towers are hygroscopic particles which are likely organic - therefore assumed 100% SOA.
Tank¦N/A | 0 | 0% | 0% | 0% | 0% | No EC, SOA or PMF Emissions assumed from tank emissions

## Mobile Equip Assumptions (hidden)
Assumptions
• During commissioning of a piece of equipment, assume only operate half of the hours in 1 month
• During maintainence of a piece of equipment, assume only operate half of the hours in 1 month
• During start-up of Trains 1&2 compressors, use CGF gas
• Power Generators use CGF gas until Trains 1&2 completely started-up
• Two Power Generators in operation after sealift 1, four after sealift 2 and commisioning of T 1&2, and six after all sealift 3.
• Each essential and emergency generator is tested for 5 hr/month.
• Essential and emergency generators start with Hookup of Sealift 1.
• First Fills for tanks occurs just before use. More specifically, this means that the TEG storage tanks and common heating/cooling medium tanks will operate on Sealift 1
as well as the diesel tanks. MeOH and Amine storage tanks come on line with sealift 2; all train tanks come online as the train is put in service
• All water tanks assumed to not have vent emissions that require recording
• Diesel Air compressors and Fire Water Pump will be tested for 5 hr/month. These items are for emergency use only, which is not reflected in these sheets.
• Auxilliary heater operates at 40% of design for the first year after sealift one. After sealift one and comissioning of Trains 1 & 2 the heater will not operate.
• Garbage and Food delivery trucks will operate daily, assuming 5hrs of operation a day
• Water delivery was asssumed to be by pipeline only; No truck delivery was assumed
• Each of the following trucks were assumed to operate 10hrs/month:
Miscelaneous Parts Delivery Truck
Electrical and Controls Delivery Truck
Azimuth and Elevation Drive Delivery Truck (i.e. communications)
Hazardous Waste Truck
• Each of the following trucks were assumed to operate 20hrs/month:
Special Maintenance Personnel Truck
Vacuum Truck (after commisioning)
• During commissioning, the vacuum truck will operate 12hr/day for 7 days a week
• Delivery Truck size was based on the maximum vehicle weight limit as defined in AAC 25.013. a Kenworth T800 was assumed to have an empty weight of 25,000 lb.
• All chemical delivery trucks were defined together. The delivery truck size was assumed to be 9000 US gal (unless noted), and first fill quantities are:
[5 empty] | Sea Lift 1 (month 48) | Sea Lift 2 (month 60) | Sea Lift 3 (month 72)
| TEG: | 363 trucks SL1 (heating/cooling medium) |  |  | 121
| TEG: | 42 trucks, sea lift 2;24 trucks SL3 |  |  |  | 14 | 8
| Amine: | 312 trucks seal lift 2, 285 trucks SL3 |  |  |  | 104 | 95
| Propane: | 60 trucks sea lift 2 |  |  |  | 20
| Liquid N2: | 4 trucks sea lift 1 (6000 gal) |  |  | 2
| Diesel: | 57 trucks sea lift 1 |  |  | 19
| Chemical Injectants: |  | 6 trucks sea lift 1 |  | 2
| Hydraulic Fluid: |  | 9 trucks sea lift 1 |  | 3
| Lube oil: | 12 trucks each sea lift |  |  | 4 | 4 | 4
[5 empty] | 151 | 142 | 107
• All chemical delivery trucks were defined together. The delivery truck size was assumed to be 9000 US gal (unless noted), and delivery quantities are:
[5 empty] | Jan | Feb | Mar | April | May | June | July | Aug | Sept | Oct | Nov | Dec
| TEG: | 6 trucks every 2 months |  |  | Jan: 6; Mar: 6; May: 6; July: 6; Sept: 6; Nov: 6
| Amine: | 15 trucks a year |  |  | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1
| Propane: | 1 trucks a year (6000 gal) | bar: Jan
| Liquid N2: | 2 trucks every 2 months (6000 gal) |  |  | Feb: 2; April: 2; June: 2; Aug: 2; Oct: 2; Dec: 2
| Diesel: | 1 truck every week |  |  | 4 | 5 | 4 | 4 | 4 | 5 | 4 | 5 | 4 | 4 | 4 | 5
| Chemical Injectants: |  | 1 trucks every other month | bar: Feb; April; June; Aug; Oct; Dec
Hydraulic Fluid:
| Lube oil: | 8 trucks every 2 months |  |  | Feb: 8; April: 8; June: 8; Aug: 8; Oct: 8; Dec: 8
[5 empty] | 12 | 18 | 11 | 17 | 11 | 18 | 11 | 17 | 11 | 16 | 11 | 17
(ABOVE quatities based on USAG-WD-PEUTL-000002 Inventory List Base Case Rev 0.xls)
Therefore, for normal operation assume 18 chemical trucks a month, at 12 hrs each (once all trains running)
| (6 after sea lift 1) |  |  | sea lift 1: | 4.3333 | 6.3333 | 3.3333 | 6 | 3.3333 | 6.3333 | 3.3333 | 6.3333 | 3.3333 | 6 | 3.3333 | 6.3333
| (12 after sea lift 2) |  |  | sea lift 2: | 8.1667 | 12.6667 | 7.1667 | 12 | 7.1667 | 12.6667 | 7.1667 | 12.1667 | 7.1667 | 11.5 | 7.1667 | 12.1667
• Flaring/venting for startup occurs 4 times a year per train, except during commissioning which was assumed to be 8 times/yr/train for the first year. Each event was assumed to take 24 hrs.
• Cooling Medium Expansion Drums and Sumps open to atmosphere were assumed to have a working volume of 50%, and to have 1 turnover a year each, to approximate actual operation.
• Truck horsepower was assumed to be 400HP as an average, if more detailed vehicle information was unavailable
• All diesel is arctic diesel
• Turbine emissions and stack parameters account for waste heat recovery and supplimental firing where applicable
• Turbine HP represents average over the year with respect to ambient temperature (derated)
AAC Vehicle weight: |  |  | http://www.legis.state.ak.us/basis/folioproxy.asp?url=http://wwwjnu01.legis.state.ak.us/cgi-bin/folioisa.dll/aac/query=[JUMP:'Title17Chap25!2C+a!2E+1']/doc/{@1}?firsthit
Description:
1998 Kenworth T800; 400 miles, empty weight 25,500 lbs, 525 hp, N14 Cummins, 18 speed, 17 aluminum east box, 20k and 40k, axles, 433 ratio, air ride, axle interlock, 240" wheel base, all aluminum wheels, all new tires, 2 steerable lift axles, new brakes, roll tarp, suspension updates, new S.S. drop visor, L.E.D. lights and S.S. trip, new bumper, paint light bar and more. Asking $67,900. Located in Eau Claire, WI. For more information, please call 715-833-0313 or 715-830-0031.
http://www.activefarming.org/node/6478

## Onsite Opper. Eqt and Vehic (hidden)
GTP
| Co-current construction and operation | Onsite Operations Equipment Projection
| Operations Equipment Description | HP | D | G | P | Sales Gas | CGF Gas | Hrs/Month | Month After Construction Start (number of equipment per month in chart)
[9 empty] | 2014 -3Q,4Q | [5 empty] | 2015 | [11 empty] | 2016 | [11 empty] | 2017 | [11 empty] | 2018 | [11 empty] | 2019 | [11 empty] | 2020 | [11 empty] | 2021 | [11 empty] | 2022
Item Number | [8 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 1-12 | 2-13 | 3-14 | 4-15 | 5-16 | 6-17 | 7-18 | 8-19 | 9-20 | 10-21 | 11-22 | 12-23 | 13-24 | 14-25 | 15-26 | 16-27 | 17-28 | 18-29 | 19-30 | 20-31 | 21-32 | 22-33 | 23-34 | 24-35 | 25-36 | 26-37 | 27-38 | 28-39 | 29-40 | 30-41 | 31-42 | 32-43 | 33-44 | 34-45 | 35-46 | 36-47 | 37-48 | 38-49 | 39-50 | 40-51 | 41-52 | 42-53 | 43-54 | 44-55 | 45-56 | 46-57 | 47-58 | 48-59 | 49-60 | 50-61 | 51-62 | 52-63 | 53-64 | 54-65 | 55-66 | 56-67 | 57-68 | 58-69 | 59-70 | 60-71 | 61-72 | 62-73 | 63-74 | 64-75 | 65-76 | 66-77 | 67-78 | 68-79 | 69-80 | 70-81 | 71-82 | 72-83 | 73-84 | 74-85 | 75-86 | 76-87 | 77-88 | 78-89 | 79-90 | 80-91 | 81-92 | 82-93 | 83-94 | 84-95 | 85-96 | 86-97 | 87-98 | 88-99 | 89-100 | 90-101 | 91-102 | 1-75 (entire construction)
| Vehicles with Onroad Engines for Emissions Estimates | [7 empty] | 2022 1-12: 0; 2022 2-13: 0; 2022 3-14: 0; 2022 4-15: 0; 2022 5-16: 0; 2022 6-17: 0; 2022 7-18: 0; 2022 8-19: 0; 2022 9-20: 0; 2022 10-21: 0; 2022 11-22: 0; 2022 12-23: 0; 2022 13-24: 0; 2022 14-25: 0; 2022 15-26: 0; 2022 16-27: 0; 2022 17-28: 0; 2022 18-29: 0; 2022 19-30: 0; 2022 20-31: 0; 2022 21-32: 0; 2022 22-33: 0; 2022 23-34: 0; 2022 24-35: 0; 2022 25-36: 0; 2022 26-37: 0; 2022 27-38: 0; 2022 28-39: 0; 2022 29-40: 0; 2022 30-41: 0; 2022 31-42: 0; 2022 32-43: 0; 2022 33-44: 0; 2022 34-45: 0; 2022 35-46: 0; 2022 36-47: 0; 2022 37-48: 0; 2022 38-49: 0; 2022 39-50: 0; 2022 40-51: 0; 2022 41-52: 0; 2022 42-53: 0; 2022 43-54: 0; 2022 44-55: 0; 2022 45-56: 0; 2022 46-57: 0; 2022 47-58: 0; 2022 48-59: 0; 2022 49-60: 0; 2022 50-61: 0; 2022 51-62: 0; 2022 52-63: 0; 2022 53-64: 0; 2022 54-65: 0; 2022 55-66: 0; 2022 56-67: 0; 2022 57-68: 0; 2022 58-69: 0; 2022 59-70: 0; 2022 60-71: 0; 2022 61-72: 0; 2022 62-73: 0; 2022 63-74: 0; 2022 64-75: 0; 2022 65-76: 0; 2022 66-77: 0; 2022 67-78: 0; 2022 68-79: 0; 2022 69-80: 0; 2022 70-81: 0; 2022 71-82: 0; 2022 72-83: 0; 2022 73-84: 0; 2022 74-85: 0; 2022 75-86: 0; 2022 76-87: 0; 2022 77-88: 0; 2022 78-89: 0; 2022 79-90: 0; 2022 80-91: 0; 2022 81-92: 0; 2022 82-93: 0; 2022 83-94: 0; 2022 84-95: 0; 2022 85-96: 0; 2022 86-97: 0; 2022 87-98: 0; 2022 88-99: 0; 2022 89-100: 0; 2022 90-101: 0; 2022 91-102: 0 | 0
21 | General Materials Delivery Truck for general construction | 400 | x |  |  |  |  | 10 | [38 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 37
22 | Delivery Truck- Food | 400 | x |  |  |  |  | 150 | [38 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 37
23 | Delivery Truck - Chemicals | 400 | x |  |  |  |  | 12 | 2017 39: 17; 2017 40: 17; 2017 41: 17; 2017 42: 17; 2018 43: 17; 2018 44: 17; 2018 45: 17; 2018 46: 17; 2018 47: 35; 2018 48: 186; 2018 49: 35; 2018 50: 35; 2018 51: 35; 2018 52: 35; 2018 53: 35; 2018 54: 35; 2019 55: 35; 2019 56: 35; 2019 57: 35; 2019 58: 35; 2019 59: 35; 2019 60: 194; 2019 61: 52; 2019 62: 52; 2019 63: 52; 2019 64: 52; 2019 65: 52; 2019 66: 52; 2020 67: 52; 2020 68: 52; 2020 69: 52; 2020 70: 52; 2020 71: 159; 2020 72: 52; 2020 73: 52; 2020 74: 52; 2020 75: 52; 2020 76: 52; 2020 77: 52; 2020 78: 52; 2021 79: 52; 2021 80: 52; 2021 81: 52; 2021 82: 52; 2021 83: 52; 2021 84: 52; 2021 85: 52; 2021 86: 52; 2021 87: 52; 2021 88: 52; 2021 89: 52; 2021 90: 52; 2022 91: 52; 2022 92: 52; 2022 93: 52; 2022 94: 52; 2022 95: 52; 2022 96: 52; 2022 97: 52; 2022 98: 52; 2022 99: 52; 2022 100: 52; 2022 101: 52; 2022 102: 52
24 | Delivery Truck - Misc. Parts | 400 | x |  |  |  |  | 10 | [38 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 37
25 | Special Maintenance Personnel Truck | 400 | x |  |  |  |  | 20 | [38 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 37
26 | Electrical and Control Systems Delivery Truck | 400 | x |  |  |  |  | 10 | [38 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 37
27 | Azimuth and Elevation Drive (Communications) Delivery Truck | 400 | x |  |  |  |  | 10 | [38 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 37
28 | Water Delivery Trucks | 400 | x |  |  |  |  | 0 | [38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29a | Vacuum Truck (commisioning) | 300 | x |  |  |  |  | 360 | bar: 2017 39 to 2020 72
29b | Vacuum Truck | 300 | x |  |  |  |  | 20 | bar: 2020 73 to 2022 102
30 | Garbage Trucks | 400 | x |  |  |  |  | 150 | bar: 2017 39 to 2022 102
31 | Hazardous Waste Trucks | 400 | x |  |  |  |  | 10 | bar: 2017 39 to 2022 102
| Total | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 44 | 195 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 203 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 168 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 12 | 18 | [61 empty] | 222
Note:
1. abbreviation:
| HP=horsepower G=gasoline D=diesel P=propane Sales Gas CGF Gas = Plant Inlet gas | [7 empty] | 2022 4-15: max =; 2022 5-16: 12
| 2. max numbers of equipment and vehicles per month = |  |  | 203
3. It is assumed the numbers of worker passenger vehicles are the numbers of workers divided by 1.5.

## Mobile Eqt and Vehic (hidden)
GTP
Mobile Equipment and Vehicle Projection for Operations
Co-current construction and operation
Onsite Mobile Equipment and Vehicles Emission Sources
Mobile Equipment Description | HP | D | G | P | Sales Gas | CGF Gas | Hrs/Month | Month After Construction Start (number of equipment operating per month in chart)
[8 empty] | 2014 -3Q,4Q | [5 empty] | 2015 | [11 empty] | 2016 | [11 empty] | 2017 | [11 empty] | 2018 | [11 empty] | 2019 | [11 empty] | 2020 | [11 empty] | 2021 | [11 empty] | 2022
[8 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 1-12 | 2-13 | 3-14 | 4-15 | 5-16 | 6-17 | 7-18 | 8-19 | 9-20 | 10-21 | 11-22 | 12-23 | 13-24 | 14-25 | 15-26 | 16-27 | 17-28 | 18-29 | 19-30 | 20-31 | 21-32 | 22-33 | 23-34 | 24-35 | 25-36 | 26-37 | 27-38 | 28-39 | 29-40 | 30-41 | 31-42 | 32-43 | 33-44 | 34-45 | 35-46 | 36-47 | 37-48 | 38-49 | 39-50 | 40-51 | 41-52 | 42-53 | 43-54 | 44-55 | 45-56 | 46-57 | 47-58 | 48-59 | 49-60 | 50-61 | 51-62 | 52-63 | 53-64 | 54-65 | 55-66 | 56-67 | 57-68 | 58-69 | 59-70 | 60-71 | 61-72 | 62-73 | 63-74 | 64-75 | 65-76 | 66-77 | 67-78 | 68-79 | 69-80 | 70-81 | 71-82 | 72-83 | 73-84 | 74-85 | 75-86 | 76-87 | 77-88 | 78-89 | 79-90 | 80-91 | 81-92 | 82-93 | 83-94 | 84-95 | 85-96 | 86-97 | 87-98 | 88-99 | 89-100 | 90-101 | 91-102 | 1-75 (entire construction)
Air Compressor -900CFM (Sullair; caterpillar C-9 ATAAC engine) | 300 | X |  |  |  |  | 120 | [36 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 4 | 6 | 8 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 24 | 78
Dump Truck - Mack B70 (10 tires, 12 gph, 6 cylinders) |  | X |  |  |  |  | 300 | 2017 41: 4; 2017 42: 4; 2018 43: 4; 2018 44: 4; 2018 45: 4; 2018 53: 4; 2018 54: 4; 2019 55: 4; 2019 56: 4; 2019 57: 4; 2019 65: 4; 2019 66: 4; 2020 67: 4; 2020 68: 4; 2020 69: 4; 2020 77: 4; 2020 78: 4; 2021 79: 4; 2021 80: 4; 2021 81: 4; 2021 89: 4; 2021 90: 4; 2022 91: 4; 2022 92: 4; 2022 93: 4; 2022 101: 4; 2022 102: 4
Motor Grader - Cat 16G (6 tires, 7gph, 6-cylinder engine) | 250 | X |  |  |  |  | 300 | bar: 2017 37 to 2022 102
Backhoe (CAT 966F) | 220 | X |  |  |  |  | 60 | [36 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 39
Crane (small) - 50/60 ton , Grove, RT700E (Cummins QSB engine) | 240 | X |  |  |  |  | 120 | [36 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 4 | 6 | 8 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 24 | 78
Crane (large) - 200 ton, Manitowoc 888 (Cummins M11 engine) | 330 | X |  |  |  |  | 60 | [36 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 39
Crane (large) - 90 ton, Grove 890E (Cummins QSB engine) | 275 | X |  |  |  |  | 60 | [36 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 39
Dozer - Cat D9, 475 HP | 475 | X |  |  |  |  | 300 | [40 empty] | 1 | 1 | 1 | 1 | 1 | [7 empty] | 1 | 1 | 1 | 1 | 1 | [7 empty] | 1 | 1 | 1 | 1 | 1 | [7 empty] | 1 | 1 | 1 | 1 | 1 | [7 empty] | 1 | 1 | 1 | 1 | 1 | [7 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 5 | 15
Boom Truck (National Crane 800D) | 350 | X |  |  |  |  | 60 | [36 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 39
Loader - Cat 988H, 501HP | 501 | X |  |  |  |  | 300 | [39 empty] | 4 | 4 | 4 | 4 | 4 | 4 | [6 empty] | 4 | 4 | 4 | 4 | 4 | 4 | [6 empty] | 4 | 4 | 4 | 4 | 4 | 4 | [6 empty] | 4 | 4 | 4 | 4 | 4 | 4 | [6 empty] | 4 | 4 | 4 | 4 | 4 | 4 | [6 empty] | 4 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 12 | 16 | 20 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 28 | 28 | 28 | 28 | 28 | 28 | 24 | 24 | 24 | 24 | 24 | 24 | 28 | 28 | 28 | 28 | 28 | 28 | 24 | 24 | 24 | 24 | 24 | 24 | 28 | 28 | 28 | 28 | 28 | 28 | 24 | 24 | 24 | 24 | 24 | 24 | 28 | 28 | 28 | 28 | 28 | 28 | 24 | 24 | 24 | 24 | 24 | 24 | 28 | 28 | 28 | 24 | 72
Groundthaw Heater (E3000) | 151 | X |  |  |  |  | 360 | 2017 40: 4; 2017 41: 4; 2017 42: 4; 2018 43: 4; 2018 44: 4; 2018 45: 4; 2018 52: 4; 2018 53: 4; 2018 54: 4; 2019 55: 4; 2019 56: 4; 2019 57: 4; 2019 64: 4; 2019 65: 4; 2019 66: 4; 2020 67: 4; 2020 68: 4; 2020 69: 4; 2020 76: 4; 2020 77: 4; 2020 78: 4; 2021 79: 4; 2021 80: 4; 2021 81: 4; 2021 88: 4; 2021 89: 4; 2021 90: 4; 2022 91: 4; 2022 92: 4; 2022 93: 4; 2022 100: 4; 2022 101: 4; 2022 102: 4; 2022 29-40: 4; 2022 88-99: 28; 2022 89-100: 28; 2022 90-101: 28
Tioga Heaters (600,000 Btu/hr heater) | 236 | X |  |  |  |  | 360 | [39 empty] | 26 | 26 | 26 | 26 | 26 | 26 | [6 empty] | 26 | 26 | 26 | 26 | 26 | 26 | [6 empty] | 26 | 26 | 26 | 26 | 26 | 26 | [6 empty] | 26 | 26 | 26 | 26 | 26 | 26 | [6 empty] | 26 | 26 | 26 | 26 | 26 | 26 | [6 empty] | 26 | 26 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 78 | 104 | 130 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 182 | 182 | 182 | 182 | 182 | 182 | 156 | 156 | 156 | 156 | 156 | 156 | 182 | 182 | 182 | 182 | 182 | 182 | 156 | 156 | 156 | 156 | 156 | 156 | 182 | 182 | 182 | 182 | 182 | 182 | 156 | 156 | 156 | 156 | 156 | 156 | 182 | 182 | 182 | 182 | 182 | 182 | 156 | 156 | 156 | 156 | 156 | 156 | 182 | 182 | 182 | 156 | 468
Light Plants (Genie TML-4000) | 15 | X |  |  |  |  | 120 | [36 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 50 | 75 | 100 | 150 | 175 | 200 | 225 | 250 | 275 | 300 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 300 | 975
Forklift - 15 Ton (Cat P30000) | 148 | X |  |  |  |  | 120 | [36 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 39
Forklift - Cat (2P5000) | 61 | X |  |  |  |  | 120 | [36 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 6 | 9 | 12 | 18 | 21 | 24 | 27 | 30 | 33 | 36 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 36 | 117
Snowblower/ Grader - 16' (Kodiak Northwest) | 500 | X |  |  |  |  | 300 | 2017 40: 4; 2017 41: 4; 2017 42: 4; 2018 43: 4; 2018 44: 4; 2018 45: 4; 2018 52: 4; 2018 53: 4; 2018 54: 4; 2019 55: 4; 2019 56: 4; 2019 57: 4; 2019 64: 4; 2019 65: 4; 2019 66: 4; 2020 67: 4; 2020 68: 4; 2020 69: 4; 2020 76: 4; 2020 77: 4; 2020 78: 4; 2021 79: 4; 2021 80: 4; 2021 81: 4; 2021 88: 4; 2021 89: 4; 2021 90: 4; 2022 91: 4; 2022 92: 4; 2022 93: 4; 2022 100: 4; 2022 101: 4; 2022 102: 4
Generator - 100 kW | 135 | X |  |  |  |  | 60 | 2017 37: 4; 2017 38: 4; 2017 39: 4; 2017 40: 4; 2017 41: 4; 2017 42: 4; 2018 43: 4; 2018 44: 4; 2018 45: 4; 2018 46: 4; 2018 47: 4; 2018 48: 4; 2018 49: 4; 2018 50: 4; 2018 51: 4; 2018 52: 4; 2018 53: 4; 2018 54: 4; 2019 55: 4; 2019 56: 4; 2019 57: 4; 2019 58: 4; 2019 59: 4; 2019 60: 4; 2019 61: 4; 2019 62: 4; 2019 63: 4; 2019 64: 4; 2019 65: 4; 2019 66: 4; 2020 67: 4; 2020 68: 4; 2020 69: 4; 2020 70: 4; 2020 71: 4; 2020 72: 4; 2020 73: 4; 2020 74: 4; 2020 75: 4; 2020 76: 4; 2020 77: 4; 2020 78: 4; 2021 79: 4; 2021 80: 4; 2021 81: 4; 2021 82: 4; 2021 83: 4; 2021 84: 4; 2021 85: 4; 2021 86: 4; 2021 87: 4; 2021 88: 4; 2021 89: 4; 2021 90: 4; 2022 91: 4; 2022 92: 4; 2022 93: 4; 2022 94: 4; 2022 95: 4; 2022 96: 4; 2022 97: 4; 2022 98: 4; 2022 99: 4; 2022 100: 4; 2022 101: 4; 2022 102: 4
Generator - 50 kW | 67 | X |  |  |  |  | 60 | 2017 37: 20; 2017 38: 20; 2017 39: 20; 2017 40: 20; 2017 41: 20; 2017 42: 20; 2018 43: 20; 2018 44: 20; 2018 45: 20; 2018 46: 20; 2018 47: 20; 2018 48: 20; 2018 49: 20; 2018 50: 20; 2018 51: 20; 2018 52: 20; 2018 53: 20; 2018 54: 20; 2019 55: 20; 2019 56: 20; 2019 57: 20; 2019 58: 20; 2019 59: 20; 2019 60: 20; 2019 61: 20; 2019 62: 20; 2019 63: 20; 2019 64: 20; 2019 65: 20; 2019 66: 20; 2020 67: 20; 2020 68: 20; 2020 69: 20; 2020 70: 20; 2020 71: 20; 2020 72: 20; 2020 73: 20; 2020 74: 20; 2020 75: 20; 2020 76: 20; 2020 77: 20; 2020 78: 20; 2021 79: 20; 2021 80: 20; 2021 81: 20; 2021 82: 20; 2021 83: 20; 2021 84: 20; 2021 85: 20; 2021 86: 20; 2021 87: 20; 2021 88: 20; 2021 89: 20; 2021 90: 20; 2022 91: 20; 2022 92: 20; 2022 93: 20; 2022 94: 20; 2022 95: 20; 2022 96: 20; 2022 97: 20; 2022 98: 20; 2022 99: 20; 2022 100: 20; 2022 101: 20; 2022 102: 20
Manlifts - 80' Gemie (Z80/60) | 78 | X |  |  |  |  | 60 | 2017 37: 2; 2017 38: 2; 2017 39: 2; 2017 40: 2; 2017 41: 2; 2017 42: 2; 2018 43: 2; 2018 44: 2; 2018 45: 2; 2018 46: 2; 2018 47: 2; 2018 48: 2; 2018 49: 2; 2018 50: 2; 2018 51: 2; 2018 52: 2; 2018 53: 2; 2018 54: 2; 2019 55: 2; 2019 56: 2; 2019 57: 2; 2019 58: 2; 2019 59: 2; 2019 60: 2; 2019 61: 2; 2019 62: 2; 2019 63: 2; 2019 64: 2; 2019 65: 2; 2019 66: 2; 2020 67: 2; 2020 68: 2; 2020 69: 2; 2020 70: 2; 2020 71: 2; 2020 72: 2; 2020 73: 2; 2020 74: 2; 2020 75: 2; 2020 76: 2; 2020 77: 2; 2020 78: 2; 2021 79: 2; 2021 80: 2; 2021 81: 2; 2021 82: 2; 2021 83: 2; 2021 84: 2; 2021 85: 2; 2021 86: 2; 2021 87: 2; 2021 88: 2; 2021 89: 2; 2021 90: 2; 2022 91: 2; 2022 92: 2; 2022 93: 2; 2022 94: 2; 2022 95: 2; 2022 96: 2; 2022 97: 2; 2022 98: 2; 2022 99: 2; 2022 100: 2; 2022 101: 2; 2022 102: 2
Manlift - 45' Genie (Z45, Perkins 404D-22 4 cylinder engine) | 51 | X |  |  |  |  | 60 | 2017 37: 4; 2017 38: 4; 2017 39: 4; 2017 40: 4; 2017 41: 4; 2017 42: 4; 2018 43: 4; 2018 44: 4; 2018 45: 4; 2018 46: 4; 2018 47: 4; 2018 48: 4; 2018 49: 4; 2018 50: 4; 2018 51: 4; 2018 52: 4; 2018 53: 4; 2018 54: 4; 2019 55: 4; 2019 56: 4; 2019 57: 4; 2019 58: 4; 2019 59: 4; 2019 60: 4; 2019 61: 4; 2019 62: 4; 2019 63: 4; 2019 64: 4; 2019 65: 4; 2019 66: 4; 2020 67: 4; 2020 68: 4; 2020 69: 4; 2020 70: 4; 2020 71: 4; 2020 72: 4; 2020 73: 4; 2020 74: 4; 2020 75: 4; 2020 76: 4; 2020 77: 4; 2020 78: 4; 2021 79: 4; 2021 80: 4; 2021 81: 4; 2021 82: 4; 2021 83: 4; 2021 84: 4; 2021 85: 4; 2021 86: 4; 2021 87: 4; 2021 88: 4; 2021 89: 4; 2021 90: 4; 2022 91: 4; 2022 92: 4; 2022 93: 4; 2022 94: 4; 2022 95: 4; 2022 96: 4; 2022 97: 4; 2022 98: 4; 2022 99: 4; 2022 100: 4; 2022 101: 4; 2022 102: 4
Zoom Boom - Telehandler (used on warehouse), GTH-1056 | 125 | X |  |  |  |  | 300 | 2017 37: 2; 2017 38: 2; 2017 39: 2; 2017 40: 2; 2017 41: 2; 2017 42: 2; 2018 43: 2; 2018 44: 2; 2018 45: 2; 2018 46: 2; 2018 47: 2; 2018 48: 2; 2018 49: 2; 2018 50: 2; 2018 51: 2; 2018 52: 2; 2018 53: 2; 2018 54: 2; 2019 55: 2; 2019 56: 2; 2019 57: 2; 2019 58: 2; 2019 59: 2; 2019 60: 2; 2019 61: 2; 2019 62: 2; 2019 63: 2; 2019 64: 2; 2019 65: 2; 2019 66: 2; 2020 67: 2; 2020 68: 2; 2020 69: 2; 2020 70: 2; 2020 71: 2; 2020 72: 2; 2020 73: 2; 2020 74: 2; 2020 75: 2; 2020 76: 2; 2020 77: 2; 2020 78: 2; 2021 79: 2; 2021 80: 2; 2021 81: 2; 2021 82: 2; 2021 83: 2; 2021 84: 2; 2021 85: 2; 2021 86: 2; 2021 87: 2; 2021 88: 2; 2021 89: 2; 2021 90: 2; 2022 91: 2; 2022 92: 2; 2022 93: 2; 2022 94: 2; 2022 95: 2; 2022 96: 2; 2022 97: 2; 2022 98: 2; 2022 99: 2; 2022 100: 2; 2022 101: 2; 2022 102: 2
Tractor Trailer |  | X |  |  |  |  | 120 | [36 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 39
Flatbed Truck (2 ton) (approx. F-450) | 385 | X |  |  |  |  | 180 | 2017 37: 1; 2017 38: 1; 2017 39: 1; 2017 40: 1; 2017 41: 1; 2017 42: 1; 2018 43: 1; 2018 44: 1; 2018 45: 1; 2018 46: 1; 2018 47: 1; 2018 48: 2; 2018 49: 2; 2018 50: 2; 2018 51: 2; 2018 52: 2; 2018 53: 2; 2018 54: 2; 2019 55: 2; 2019 56: 2; 2019 57: 2; 2019 58: 2; 2019 59: 2; 2019 60: 2; 2019 61: 2; 2019 62: 2; 2019 63: 2; 2019 64: 2; 2019 65: 2; 2019 66: 2; 2020 67: 2; 2020 68: 2; 2020 69: 2; 2020 70: 2; 2020 71: 2; 2020 72: 2; 2020 73: 2; 2020 74: 2; 2020 75: 2; 2020 76: 2; 2020 77: 2; 2020 78: 2; 2021 79: 2; 2021 80: 2; 2021 81: 2; 2021 82: 2; 2021 83: 2; 2021 84: 2; 2021 85: 2; 2021 86: 2; 2021 87: 2; 2021 88: 2; 2021 89: 2; 2021 90: 2; 2022 91: 2; 2022 92: 2; 2022 93: 2; 2022 94: 2; 2022 95: 2; 2022 96: 2; 2022 97: 2; 2022 98: 2; 2022 99: 2; 2022 100: 2; 2022 101: 2; 2022 102: 2
Fuel Truck (Kenworth T800) | 400 | X |  |  |  |  | 360 | 2017 37: 1; 2017 38: 1; 2017 39: 1; 2017 40: 1; 2017 41: 1; 2017 42: 1; 2018 43: 1; 2018 44: 1; 2018 45: 1; 2018 46: 1; 2018 47: 1; 2018 48: 1; 2018 49: 1; 2018 50: 2; 2018 51: 2; 2018 52: 2; 2018 53: 2; 2018 54: 2; 2019 55: 2; 2019 56: 2; 2019 57: 2; 2019 58: 2; 2019 59: 2; 2019 60: 2; 2019 61: 2; 2019 62: 2; 2019 63: 2; 2019 64: 2; 2019 65: 2; 2019 66: 2; 2020 67: 2; 2020 68: 2; 2020 69: 2; 2020 70: 2; 2020 71: 2; 2020 72: 2; 2020 73: 2; 2020 74: 2; 2020 75: 2; 2020 76: 2; 2020 77: 2; 2020 78: 2; 2021 79: 2; 2021 80: 2; 2021 81: 2; 2021 82: 2; 2021 83: 2; 2021 84: 2; 2021 85: 2; 2021 86: 2; 2021 87: 2; 2021 88: 2; 2021 89: 2; 2021 90: 2; 2022 91: 2; 2022 92: 2; 2022 93: 2; 2022 94: 2; 2022 95: 2; 2022 96: 2; 2022 97: 2; 2022 98: 2; 2022 99: 2; 2022 100: 2; 2022 101: 2; 2022 102: 2
Bobcat (2500 lb capacity, 75 hp, Kubota S250 ) | 75 | X |  |  |  |  | 360 | 2017 40: 4; 2017 41: 4; 2017 42: 4; 2018 43: 4; 2018 44: 4; 2018 45: 4; 2018 52: 4; 2018 53: 4; 2018 54: 4; 2019 55: 4; 2019 56: 4; 2019 57: 4; 2019 64: 4; 2019 65: 4; 2019 66: 4; 2020 67: 4; 2020 68: 4; 2020 69: 4; 2020 76: 4; 2020 77: 4; 2020 78: 4; 2021 79: 4; 2021 80: 4; 2021 81: 4; 2021 88: 4; 2021 89: 4; 2021 90: 4; 2022 91: 4; 2022 92: 4; 2022 93: 4; 2022 100: 4; 2022 101: 4; 2022 102: 4
Welding Machines (in shop) (Lincoln Electric) | 36 | X |  |  |  |  | 180 | [36 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 24 | 28 | 32 | 36 | 40 | 44 | 48 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 48 | 156
Water Truck - dust control (West Mark DST-S4000) | 350 | X |  |  |  |  | 300 | 2017 37: 2; 2017 38: 2; 2017 39: 2; 2018 46: 2; 2018 47: 2; 2018 48: 2; 2018 49: 2; 2018 50: 2; 2018 51: 2; 2019 58: 2; 2019 59: 2; 2019 60: 2; 2019 61: 2; 2019 62: 2; 2019 63: 2; 2020 70: 2; 2020 71: 2; 2020 72: 2; 2020 73: 2; 2020 74: 2; 2020 75: 2; 2021 82: 2; 2021 83: 2; 2021 84: 2; 2021 85: 2; 2021 86: 2; 2021 87: 2; 2022 94: 2; 2022 95: 2; 2022 96: 2; 2022 97: 2; 2022 98: 2; 2022 99: 2
Grey and Black Water Truck (Kenworth T800) | 400 | X |  |  |  |  | 180 | [36 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 39
Solid Waste Truck - Refuse (Kenworth T800) | 400 | X |  |  |  |  | 300 | [36 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 24 | 66
Vehicles with Onroad Engines for Emissions Estimates | [7 empty] | 2017 42: Vehicles with Onroad Engines for Emissions Estimates; 2022 91: Vehicles with Onroad Engines for Emissions Estimates; 2022 38-49: 0; 2022 39-50: 0; 2022 40-51: 0; 2022 41-52: 0; 2022 42-53: 0; 2022 43-54: 0; 2022 44-55: 0; 2022 45-56: 0; 2022 46-57: 0; 2022 47-58: 0; 2022 48-59: 0; 2022 49-60: 0; 2022 50-61: 0; 2022 51-62: 0; 2022 52-63: 0; 2022 53-64: 0; 2022 54-65: 0; 2022 55-66: 0; 2022 56-67: 0; 2022 57-68: 0; 2022 58-69: 0; 2022 59-70: 0; 2022 60-71: 0; 2022 61-72: 0; 2022 62-73: 0; 2022 63-74: 0; 2022 64-75: 0; 2022 65-76: 0; 2022 66-77: 0; 2022 67-78: 0; 2022 68-79: 0; 2022 69-80: 0; 2022 70-81: 0; 2022 71-82: 0; 2022 72-83: 0; 2022 73-84: 0; 2022 74-85: 0; 2022 75-86: 0; 2022 76-87: 0; 2022 77-88: 0; 2022 78-89: 0; 2022 79-90: 0; 2022 80-91: 0; 2022 81-92: 0; 2022 82-93: 0; 2022 83-94: 0; 2022 84-95: 0; 2022 85-96: 0; 2022 86-97: 0; 2022 87-98: 0; 2022 88-99: 0; 2022 89-100: 0; 2022 90-101: 0; 2022 91-102: 0 | 0
Passenger Van, 16 person (Ford E-350 series, or GM chevy 3500) | 320 | X |  |  |  |  | 180 | [36 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 4 | 6 | 8 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 48 | 120
Passenger Bus, 20 person (Blue Bird; 6.8 L engine) | 360 | X |  |  |  |  | 120 | [36 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 39
Staff & Security Truck (3/4 ton crew cab) | 300 | X |  |  |  |  | 360 | [36 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 4 | 6 | 8 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 24 | 78
Pickup Truck - Standard Bed (V8 engine) | 360 | X |  |  |  |  | 360 | [36 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10 | 15 | 20 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 70 | 75 | 80 | 85 | 90 | 95 | 100 | 105 | 110 | 115 | 120 | 125 | 135 | 140 | 145 | 150 | 155 | 160 | 165 | 170 | 175 | 180 | 185 | 190 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 180 | 405
Pickup Truck - Service Bed (Silverado HD2500) | 397 | X |  |  |  |  | 360 | 2017 37: 5; 2017 38: 5; 2017 39: 5; 2017 40: 5; 2017 41: 5; 2017 42: 5; 2018 43: 5; 2018 44: 5; 2018 45: 5; 2018 46: 5; 2018 47: 5; 2018 48: 5; 2018 49: 10; 2018 50: 10; 2018 51: 10; 2018 52: 10; 2018 53: 10; 2018 54: 10; 2019 55: 10; 2019 56: 10; 2019 57: 10; 2019 58: 10; 2019 59: 10; 2019 60: 10; 2019 61: 15; 2019 62: 15; 2019 63: 15; 2019 64: 15; 2019 65: 15; 2019 66: 15; 2020 67: 15; 2020 68: 15; 2020 69: 15; 2020 70: 15; 2020 71: 15; 2020 72: 15; 2020 73: 15; 2020 74: 15; 2020 75: 15; 2020 76: 15; 2020 77: 15; 2020 78: 15; 2021 79: 15; 2021 80: 15; 2021 81: 15; 2021 82: 15; 2021 83: 15; 2021 84: 15; 2021 85: 15; 2021 86: 15; 2021 87: 15; 2021 88: 15; 2021 89: 15; 2021 90: 15; 2022 91: 15; 2022 92: 15; 2022 93: 15; 2022 94: 15; 2022 95: 15; 2022 96: 15; 2022 97: 15; 2022 98: 15; 2022 99: 15; 2022 100: 15; 2022 101: 15; 2022 102: 15; 2022 26-37: 5; 2022 27-38: 10; 2022 28-39: 15; 2022 29-40: 20; 2022 30-41: 30; 2022 31-42: 35; 2022 32-43: 40; 2022 33-44: 45; 2022 34-45: 50; 2022 35-46: 55; 2022 36-47: 60; 2022 37-48: 70 | 405
Ambulence (GM ambulence) | 260 | X |  |  |  |  | 12 | [36 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 39
Total | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 22 | 22 | 22 | 27 | 27 | 27 | 27 | 27 | 22 | 22 | 22 | 32 | 32 | 32 | 32 | 37 | 37 | 37 | 37 | 37 | 32 | 32 | 32 | 42 | 42 | 42 | 42 | 47 | 47 | 47 | 47 | 47 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 47 | 47 | 47 | 47 | 47 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 47 | 47 | 47 | 47 | 47 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 47 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 63 | 84 | 128 | 150 | 172 | 194 | 215 | 236 | 257 | 288 | 223 | 228 | 233 | 239 | 244 | 249 | 254 | 259 | 263 | 268 | 273 | 283 | 288 | 293 | 298 | 304 | 309 | 314 | 319 | 324 | 328 | 333 | 338 | 343 | 343 | 343 | 343 | 344 | 344 | 344 | 344 | 344 | 343 | 343 | 343 | 343 | 343 | 343 | 343 | 344 | 344 | 344 | 344 | 344 | 343 | 343 | 343 | 343 | 343 | 343 | 343 | 344 | 344 | 317 | 1254
Note:
1. abbreviation: | [7 empty] | 2022 4-15: max =; 2022 5-16: #REF!
HP=horsepower G=gasoline D=diesel P=propane Sales Gas CGF Gas = Plant Inlet gas
2. max numbers of equipment and vehicles per month = |  |  | 47
3. It is assumed the numbers of worker passenger vehicles are the numbers of workers divided by 1.5.

## Mobile Trip Assumptions (hidden)
Vehicle Classification | Vehicle Descriptions | Total Hours per Year | Total Assumed Miles Driven
Single Unit Short-Haul Truck | General Materials Delivery Truck | 120 | 1200
| Delivery Truck- Food | 1800 | 18000
| Delivery Truck - Chemicals | 7488 | 74880
| Delivery Truck - Misc. Parts | 120 | 1200
| Electrical and Control Systems Delivery Truck | 120 | 1200
| Azimuth and Elevation Drive (Communications) Delivery Truck | 120 | 1200
| Water Delivery Trucks | 0 | 0
| Flatbed Truck (2 ton) (approx. F-450) | 4320 | 43200
| Tractor Trailer | 1440 | 14400
| Garbage Trucks | 1800 | 18000
| Hazardous Waste Trucks | 120 | 1200
| Dump Truck - Mack B70 (10 tires, 12 gph, 6 cylinders) | 6000 | 60000
| Solid Waste Truck - Refuse (Kenworth T800) | 7200 | 72000
Light Commercial Truck | Vacuum Truck | 240 | 2400
| Ambulence (GM ambulence) | 144 | 1440
| Fuel Truck (Kenworth T800) | 8640 | 86400
| Water Truck - dust control (West Mark DST-S4000) | 3600 | 36000
| Grey and Black Water Truck (Kenworth T800) | 2160 | 21600
| Snowblower/ Grader - 16' (Kodiak Northwest) | 4320 | 43200
Intercity Bus | Passenger Van, 16 person (Ford E-350 series, or GM chevy 3500) | 8640 | 86400
| Passenger Bus, 20 person (Blue Bird; 6.8 L engine) | 1440 | 14400
Passenger Truck | Special Maintenance Personnel Truck | 240 | 2400
| Staff & Security Truck (3/4 ton crew cab) | 8640 | 86400
| Pickup Truck - Standard Bed (V8 engine) | 64800 | 648000
| Pickup Truck - Service Bed (Silverado HD2500) | 64800 | 648000
|  | Total Miles | 1983120
|  | Total Gal Diesel/yr | 396624
|  | MMBtu/hr | 6.531
Notes:
Based only on 1 year of normal operation, post-construction (year 2021)
Idling assumed to be included in total operating hours
Vehicle Classification assumed based on DOT-HPMF Vehicle Classes
Fuel Consumption based on 5 miles per gallon for all vehicles
|  | Time-Weighted Average Speed= | 10 | mph
|  | Fuel Consumption Assumption= | 5 | miles/gal
|  | Gross Diesel Heat of Combustion= | 0.14425 | MMBtu/gal

## Mobile Emissions
Mobile Emissions ton/year
Moves Vehicle Class | Total Miles Per Year | MOVES | [10 empty] | Ton/year
EFs (g/mi) 1
|  | VOC | NOx | CO | SO2 | PM10 | PM2.5 | CO2 | CH4 | N2O | CO2e4 | HAPs2 | VOC | NOx | CO | SO2 | PM10 | PM2.5 | CO2 | CH4 | N2O | CO2e4 | HAPs2
Single Unit Short-Haul Truck | 306480 | 0.3842 | 3.2571 | 1.2963 | 0.013674 | 0.21706 | 0.18849 | 1624.18 | 0.10181 | 0.0041394 | 1627.9589 | 0.070461 | 0.1298 | 1.1004 | 0.43793 | 0.0046196 | 0.07333 | 0.06368 | 548.7099 | 0.034396 | 0.0013984 | 549.9866 | 0.023805
Light Commercial Truck | 191040 | 0.078998 | 0.79598 | 1.642 | 0.0061158 | 0.040517 | 0.041121 | 729.512 | 0.041815 | 0.0034016 | 731.571 | 0.020137 | 0.016636 | 0.16762 | 0.34579 | 0.0012879 | 0.0085323 | 0.0086596 | 153.6255 | 0.0088056 | 0.00071633 | 154.0591 | 0.0042407
Intercity Bus | 100800 | 0.59448 | 5.7314 | 1.8417 | 0.019521 | 0.43991 | 0.26924 | 2310.04 | 0.097527 | 0.0033102 | 2313.4646 | 0.076487 | 0.066055 | 0.63684 | 0.20463 | 0.0021691 | 0.04888 | 0.029916 | 256.6768 | 0.010837 | 0.00036781 | 257.0573 | 0.0084987
Passenger Truck | 1384800 | 0.078973 | 0.88712 | 1.4871 | 0.0065899 | 0.040966 | 0.043718 | 786.544 | 0.048027 | 0.0041167 | 788.9714 | 0.021826 | 0.12055 | 1.3542 | 2.27 | 0.010059 | 0.062534 | 0.066736 | 1200.6505 | 0.073312 | 0.0062841 | 1204.356 | 0.033316
[12 empty] | TOTAL PER POLLUTANT (tpy) | 0.33304 | 3.259 | 3.2583 | 0.018136 | 0.19328 | 0.16899 | 2159.6627 | 0.12735 | 0.0087667 | 2165.459 | 0.06986
Note 1: Emissions estimates are based on EPA's MOVES2014 motor vehicle emissions estimation program. Year 2027 is used as the base year for North Slope Borough, based on latest county-specific MOVES2014 input data available from Alaska DEC.
Note 2: HAPs are aggregated for benzene, 1,3-butadiene, formaldehyde, acetaldehyde, acrolein, toluene, and xylene
Note 3: tons/year emissions = (Average distance traveled (mi/year)) * Emission factor (g/mi) / (453.59 g/lb) * (1 / 2000)
Note 4: Greenhouse gasses (GHG) are converted to carbon dioxide equivalents (CO2e) using 100-year Global Warming Potentials values from IPCC's Fourth Assessment Report (AR4) Chapter 2, Table 2.14 of Climate Change 2007: The Physical Science Basis. Contribution of Working Group I to the Fourth Assessment Report of the IPCC
CO2 = 1, CH4 = 25, N2O = 298

## Non-Road Emissions
Non-Road/Portable Diesel Emissions - tpy
[7 empty] | Emission Factors (g/hp-hr) 2 | [8 empty] | Deterioration Factors 2 |  |  |  | Adjusted Emission Factors (g/hp-hr) 2 |  |  |  |  | Emissions (ton/year)
Engine Description | Equipment category based on NONROAD classification | SCC 1 | Fuel Type | Equipment Horsepower | Operating hrs/year | BSFC 2 | NOx | CO | PM | THC | Age Factor 3 | NOx | CO | PM | THC | NOx | CO | PM | THC | NOx | CO | PM5 | THC | Load Factor 2 | NOx | CO | PM | VOC6
[12 empty] | "A" 3 | "A" 3 | "A" 3 | "A" 3
Air Compressor -900CFM (Sullair; caterpillar C-9 ATAAC engine) | Light Commercial Air Compressor | 2270006015 | Diesel | 300 | 2880 | 0.367 | 0.276 | 0.084 | 0.0092 | 0.1314 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.27821 | 0.096684 | 0.013552 | 0.13495 | 0.43 | 0.34655 | 0.12044 | 0.016881 | 0.17701
Motor Grader - Cat 16G (6 tires, 7gph, 6-cylinder engine) | Graders | 2270002048 | Diesel | 250 | 3600 | 0.371 | 0.28 | 0.11 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.12661 | 0.013552 | 0.13351 | 0.59 | 0.402 | 0.18033 | 0.019302 | 0.20024
Backhoe (CAT 966F) | Tractors/Loaders/Backhoes | 2270002066 | Diesel | 220 | 720 | 0.433 | 0.28 | 0.19 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.21869 | 0.013552 | 0.13351 | 0.21 | 0.12591 | 0.097562 | 0.0060457 | 0.062718
Crane (small) - 50/60 ton , Grove, RT700E (Cummins QSB engine) | Crane | 2270002045 | Diesel | 240 | 2880 | 0.367 | 0.28 | 0.07 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.08057 | 0.013552 | 0.13351 | 0.43 | 0.28126 | 0.08029 | 0.013505 | 0.1401
Crane (large) - 200 ton, Manitowoc 888 (Cummins M11 engine) | Crane | 2270002045 | Diesel | 330 | 720 | 0.367 | 0.28 | 0.08 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.09208 | 0.013552 | 0.13351 | 0.43 | 0.38673 | 0.12617 | 0.018569 | 0.19264
Crane (large) - 90 ton, Grove 890E (Cummins QSB engine) | Crane | 2270002045 | Diesel | 275 | 720 | 0.367 | 0.28 | 0.07 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.08057 | 0.013552 | 0.13351 | 0.43 | 0.32228 | 0.091999 | 0.015474 | 0.16053
Dozer - Cat D9, 475 HP | Rubber Tire Dozer | 2270002063 | Diesel | 475 | 1500 | 0.371 | 0.28 | 0.13 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.14963 | 0.013552 | 0.13351 | 0.59 | 0.76379 | 0.40493 | 0.036673 | 0.38045
Boom Truck (National Crane 800D) | Crane | 2270002045 | Diesel | 350 | 720 | 0.367 | 0.28 | 0.08 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.09208 | 0.013552 | 0.13351 | 0.43 | 0.41017 | 0.13382 | 0.019694 | 0.20431
Loader - Cat 988H, 501HP | Rubber Tire Loader | 2270002060 | Diesel | 501 | 7200 | 0.371 | 0.28 | 0.13 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.14963 | 0.013552 | 0.13351 | 0.59 | 0.8056 | 0.42709 | 0.03868 | 0.40128
Light Plants (Genie TML-4000) | Light Commercial Generator Set | 2270006005 | Diesel | 15 | 36000 | 0.408 | 0.28 | 0.22 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.25322 | 0.013552 | 0.13351 | 0.43 | 0.017579 | 0.015771 | 0.00084404 | 0.0087561
Forklift - 15 Ton (Cat P30000) | Forklifts | 2270003020 | Diesel | 148 | 1440 | 0.371 | 0.28 | 0.13 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.14963 | 0.013552 | 0.13351 | 0.59 | 0.23798 | 0.12617 | 0.011427 | 0.11854
Forklift - Cat (2P5000) | Forklifts | 2270003020 | Diesel | 61 | 4320 | 0.412 | 0.28 | 0.36 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.41436 | 0.013552 | 0.13351 | 0.59 | 0.098087 | 0.144 | 0.0047096 | 0.048858
Generator - 100 kW | Light Commercial Generator Set | 2270006005 | Diesel | 135 | 2880 | 0.367 | 0.28 | 0.09 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.10359 | 0.013552 | 0.13351 | 0.43 | 0.15821 | 0.058067 | 0.0075963 | 0.078805
Generator - 50 kW | Light Commercial Generator Set | 2270006005 | Diesel | 67 | 14400 | 0.408 | 0.28 | 0.24 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.27624 | 0.013552 | 0.13351 | 0.43 | 0.078519 | 0.076849 | 0.00377 | 0.039111
Man lifts - 80' Gemie (Z80/60) | Aerial Lift | 2270003010 | Diesel | 78 | 1440 | 0.481 | 0.28 | 0.61 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.70211 | 0.013552 | 0.13351 | 0.21 | 0.044642 | 0.11105 | 0.0021435 | 0.022237
Man lift - 45' Genie (Z45, Perkins 404D-22 4 cylinder engine) | Aerial Lift | 2270003010 | Diesel | 51 | 2880 | 0.481 | 0.28 | 0.61 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.70211 | 0.013552 | 0.13351 | 0.21 | 0.029189 | 0.072611 | 0.0014015 | 0.014539
Zoom Boom - Telehandler (used on warehouse), GTH-1056 | Forklifts | 2270003020 | Diesel | 125 | 7200 | 0.371 | 0.28 | 0.13 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.14963 | 0.013552 | 0.13351 | 0.59 | 0.201 | 0.10656 | 0.0096508 | 0.10012
Bobcat (2500 lb capacity, 75 hp, Kubota S250 ) | Skid Steer Loader | 2270002072 | Diesel | 75 | 8640 | 0.481 | 0.28 | 0.61 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.70211 | 0.013552 | 0.13351 | 0.21 | 0.042925 | 0.10678 | 0.002061 | 0.021381
Welding Machines (in shop) (Lincoln Electric) | Light Commercial Welders | 2270006025 | Diesel | 36 | 8640 | 0.481 | 0.28 | 0.39 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.44889 | 0.013552 | 0.13351 | 0.21 | 0.020604 | 0.03277 | 0.00098929 | 0.010263
Heater Description | Fuel Type | Equipment MMBtu/hr | Operating hrs/year | Emission Factors (lb/MMBtu) |  |  |  | Emissions (ton/year)
|  |  |  | NOx | CO | PM | THC | NOx | CO | PM | THC
Ground thaw Heater (E3000) | Diesel | 0.6 | 8640 | 0.14493 | 0.036232 | 0.023913 | 0.0024638 | 0.37565 | 0.093913 | 0.061983 | 0.0063861
Tioga Heaters (600,000 Btu/hr heater) | Diesel | 0.6 | 56160 | 0.14493 | 0.036232 | 0.023913 | 0.0024638 | 2.4417 | 0.61043 | 0.40289 | 0.04151
| Total Non-Road/Portable Emissions | Emissions (ton/year)
|  | NOx | CO | Emission Factors (lb/MMBtu) NOx: PM; Emission Factors (lb/MMBtu) CO: THC
|  | 7.5904 | 3.2176 | Emission Factors (lb/MMBtu) NOx: 0.69429; Emission Factors (lb/MMBtu) CO: 2.4298
NOTES:
Note 1: SCC code based on Appendix A of "Median Life, Annual Activity, and Load Factor Values for Nonroad Engine Emissions Modeling", July 2010, EPA-420-R-10-018.
Note 2: Brake-specific fuel consumption, zero hour steady state emission factor (EFss; g/hp-hr), and load factor are from NMIM/NONROAD08 model factors dated April 5, 2009.
Note 3: Median life is taken from Table 1 of "Median Life, Annual Activity, and Load Factor Values for Nonroad Engine Emissions Modeling", April 2004, EPA-420-P-04-005.
EFss from NMIM/NONROAD08 have transient adjustment factors (TAFs) built in. The EFss are weighted averages based on Tier 4 engines.
Note 3: Age factor and Deterioration factors calculated using Equation 4 from "Exhaust and Crankcase Emission Factors for Nonroad Engine Modeling - Compression-Ignition", July 2010, EPA-420-R-10-018.
Age Factor = LF * cumulative hours / median life {where Age factor is capped at 1. For this calculation, age factor is assumed to be 1 for simplification purposes}.
Deterioration Factor = 1 + ( A * Age Factor^b), where b = 1 for diesel engines and A is taken from Table A6 from above mentioned source
Note 4: Adjusted Emission Factors are calculated using Equation 1 from, "Exhaust and Crankcase Emission Factors for Nonroad Engine Modeling - Compression-Ignition", July 2010, EPA-420-R-10-018.
Adjusted EF = Efss * TAF * DF (as stated in Note 2, EFss have TAFs built in)
Note 5: Adjusted Emission Factors for PM10 are calculated using Equation 2 from, "Exhaust and Crankcase Emission Factors for Nonroad Engine Modeling - Compression-Ignition", July 2010, EPA-420-R-10-018.
The correction factor SPMadj is made to account for fuel sulfur variations; inputs specific to this calculation are noted below
|  |  | 0.02247 | Emission Factors (lb/MMBtu) NOx: soxcnv (fraction of fuel sulfur converted to direct PM) for Base, T0, T1, T2, T3, T3B, T4A, T4B
|  |  | 0.3 | Emission Factors (lb/MMBtu) NOx: soxcnv (fraction of fuel sulfur converted to direct PM) for Base, T4 and T4N
|  |  | 0.03 | Emission Factors (lb/MMBtu) NOx: soxcnv (fraction of fuel sulfur converted to direct PM) for gasoline engines
|  |  | 0.0015 | Emission Factors (lb/MMBtu) NOx: soxdsl (weight percent of sulfur in diesel fuel)
|  |  | 0.0015 | Emission Factors (lb/MMBtu) NOx: soxbas (default certification fuel sulfur weight percent, 0.0015 is default for Tier 4 engines)
Note 6: Adjusted emissions from THC to VOC by 1.053 is the ratio of VOC to THC (for diesel equipment) from "Conversion Factors for Hydrocarbon Components", July 2010, EPA-420-R-10-015.

## Emission Factors
Source Type | Gas-Fired Combustion Turbines |  |  | Gas-Fired Combustion Turbines |  |  | Diesel Combustion Turbines |  |  | Diesel Combustion Turbines |  |  | Gas-Fired Heaters/Boilers |  |  | Diesel-Fired Heaters |  |  |  |  | Gas-Fired ICEs 2-stroke, Lean-Burn |  |  | Gas-Fired ICEs 4-stroke, Rich-Burn |  |  | Diesel-Fired ICEs <600 hp |  |  | Diesel-Fired ICEs >600 hp |  |  | Flares |  |  | Refuse Incinerators (MOD/SA) |  |  | Used Oil (Atomizing) Burner
| Loads >80% (GRI-HAPCalc v.3.01) |  |  | All Loads |  |  | All Loads |  |  | >80% Load Only
HAP | EF | units | Factor Set | EF | units | Factor Set | EF | units | Factor Set | EF | units | Factor Set | EF | units | Factor Set | EF | units | EF | units | Factor Set | EF | units | Factor Set | EF | units | Factor Set | EF | units | Factor Set | EF | units | Factor Set | EF | units | Factor Set | EF | units | Factor Set | EF | units | Factor Set
1,1,2,2-Tetrachloroethane | [20 empty] | 6.63e-05 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 2.53e-05 | lb/MMBtu | AP-42 Table 3.2-3 (8/00)
1,1,2-Trichloroethane | [20 empty] | 5.27e-05 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 1.53e-05 | lb/MMBtu | AP-42 Table 3.2-3 (8/00)
1,3-Butadiene | 4.3e-07 | lb/MMBtu | EPA AP-42 Table 3.1-3 (4/00) | 4.29e-07 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 1.65e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 1.6e-05 | lb/MMBtu | AP-42 Table 3.1-4 (4/00) | [8 empty] | 0.00082 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 0.000663 | lb/MMBtu | AP-42 Table 3.2-3 (8/00) | 3.91e-05 | lb/MMBtu | AP-42 Table 3.3-2 (10/96)
1,3-Dichloropropene | [20 empty] | 4.38e-05 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 1.27e-05 | lb/MMBtu | AP-42 Table 3.2-3 (8/00)
1,4-Dichlorobenzene | [6 empty] | 2.97e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00)
2,2,4-Trimethylpentane | [20 empty] | 0.000846 | lb/MMBtu | AP-42 Table 3.2-1 (8/00)
Acetaldehyde | 4e-05 | lb/MMBtu | EPA AP-42 Table 3.1-3 (4/00) | 4.45e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 3.03e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | [11 empty] | 0.00776 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 0.00279 | lb/MMBtu | AP-42 Table 3.2-3 (8/00) | 0.000767 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 2.52e-05 | lb/MMBtu | AP-42 Table 3.4-3 (10/96) | 4.2157e-05 | lb/MMBtu | VCAPCD (5/172001)
Acrolein | 6.4e-06 | lb/MMBtu | EPA AP-42 Table 3.1-3 (4/00) | 8.31e-06 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | [14 empty] | 0.00778 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 0.00263 | lb/MMBtu | AP-42 Table 3.2-3 (8/00) | 9.25e-05 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 7.88e-06 | lb/MMBtu | AP-42 Table 3.4-3 (10/96) | 9.8039e-06 | lb/MMBtu | VCAPCD (5/172001)
Antimony | [38 empty] | 0.0045 | lb/1000 gal. | AP-42 Table 1.11-4 (10/96)
Arsenic | [6 empty] | 1.1e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 1.1e-05 | lb/MMBtu | AP-42 Table 3.1-5 (4/00) |  |  |  | 4 | lb/TBtu | 4000000 | lb/MMBtu | AP-42 Table 1.3-10 (9/98) | [15 empty] | 0.000669 | lb/ton | AP-42 Table 2.1-9 (10/96) | 0.06 | lb/1000 gal. | AP-42 Table 1.11-4 (10/96)
Benzene | 1.2e-05 | lb/MMBtu | EPA AP-42 Table 3.1-3 (4/00) | 0.000103 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 5.48e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 5.5e-05 | lb/MMBtu | AP-42 Table 3.1-4 (4/00) | 2.0588e-06 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 0.00194 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 0.00158 | lb/MMBtu | AP-42 Table 3.2-3 (8/00) | 0.000933 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 0.000776 | lb/MMBtu | AP-42 Table 3.4-3 (10/96) | 0.00015588 | lb/MMBtu | VCAPCD (5/172001)
Beryllium | [6 empty] | 3.07e-07 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 3.1e-07 | lb/MMBtu | AP-42 Table 3.1-5 (4/00) |  |  |  | 3 | lb/TBtu | 3000000 | lb/MMBtu | AP-42 Table 1.3-10 (9/98) | [18 empty] | 0.0018 | lb/1000 gal. | AP-42 Table 1.11-4 (10/96)
Biphenyl | [20 empty] | 3.95e-06 | lb/MMBtu | AP-42 Table 3.2-1 (8/00)
Cadmium | [6 empty] | 3.75e-06 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 4.8e-06 | lb/MMBtu | AP-42 Table 3.1-5 (4/00) |  |  |  | 3 | lb/TBtu | 3000000 | lb/MMBtu | AP-42 Table 1.3-10 (9/98) | [15 empty] | 0.00241 | lb/ton | AP-42 Table 2.1-9 (10/96) | 0.012 | lb/1000 gal. | AP-42 Table 1.11-4 (10/96)
Carbon Tetrachloride | [6 empty] | 3.06e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | [11 empty] | 6.07e-05 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 1.77e-05 | lb/MMBtu | AP-42 Table 3.2-3 (8/00)
Chlorobenzene | [6 empty] | 2.49e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | [11 empty] | 4.44e-05 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 1.29e-05 | lb/MMBtu | AP-42 Table 3.2-3 (8/00)
Chloroform | [6 empty] | 2.55e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | [11 empty] | 4.71e-05 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 1.37e-05 | lb/MMBtu | AP-42 Table 3.2-3 (8/00)
Chromium | [6 empty] | 8.43e-06 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 1.1e-05 | lb/MMBtu | AP-42 Table 3.1-5 (4/00) |  |  |  | 3 | lb/TBtu | 3000000 | lb/MMBtu | AP-42 Table 1.3-10 (9/98) | [15 empty] | 0.00331 | lb/ton | AP-42 Table 2.1-9 (10/96) | 0.18 | lb/1000 gal. | AP-42 Table 1.11-4 (10/96)
Cobalt | [38 empty] | 0.0052 | lb/1000 gal. | AP-42 Table 1.11-4 (10/96)
Dibutylphthalate | [38 empty] | 3.4e-05 | lb/1000 gal. | AP-42 Table 1.11-5 (10/96)
Ethylbenzene | 3.2e-05 | lb/MMBtu | EPA AP-42 Table 3.1-3 (4/00) | 2.58e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | [14 empty] | 0.000108 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 2.48e-05 | lb/MMBtu | AP-42 Table 3.2-3 (8/00) | [6 empty] | 0.0014157 | lb/MMBtu | VCAPCD (5/172001)
Ethylene Dibromide | [20 empty] | 7.34e-05 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 2.13e-05 | lb/MMBtu | AP-42 Table 3.2-3 (8/00)
Ethylene Dichloride | [6 empty] | 2.02e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00)
Formaldehyde | 0.00071 | lb/MMBtu | EPA AP-42 Table 3.1-3 (4/00) | 0.00312 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 0.000245 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 0.00028 | lb/MMBtu | AP-42 Table 3.1-4 (4/00) | 7.3529e-05 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | 0.061 | lb/1000 gal. | 453.3631 | lb/MMBtu | AP-42 Table 1.3-8 (9/98) | 0.0552 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 0.0205 | lb/MMBtu | AP-42 Table 3.2-3 (8/00) | 0.00118 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 7.89e-05 | lb/MMBtu | AP-42 Table 3.4-3 (10/96) | 0.0011461 | lb/MMBtu | VCAPCD (5/172001)
HCl | [35 empty] | 2.15 | lb/ton | AP-42 Table 2.1-9 (10/96)
Lead | [6 empty] | 1.34e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 1.4e-05 | lb/MMBtu | AP-42 Table 3.1-5 (4/00) | 4.902e-07 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | 9 | lb/TBtu | 9000000 | lb/MMBtu | AP-42 Table 1.3-10 (9/98)
Manganese | [6 empty] | 0.000789 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 0.00079 | lb/MMBtu | AP-42 Table 3.1-5 (4/00) |  |  |  | 6 | lb/TBtu | 6000000 | lb/MMBtu | AP-42 Table 1.3-10 (9/98) | [18 empty] | 0.05 | lb/1000 gal. | AP-42 Table 1.11-4 (10/96)
Mercury | [6 empty] | 1.2e-06 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 1.2e-06 | lb/MMBtu | AP-42 Table 3.1-5 (4/00) |  |  |  | 3 | lb/TBtu | 3000000 | lb/MMBtu | AP-42 Table 1.3-10 (9/98) | [15 empty] | 0.0056 | lb/ton | AP-42 Table 2.1-9 (10/96)
Methanol | [20 empty] | 0.00248 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 0.00306 | lb/MMBtu | AP-42 Table 3.2-3 (8/00)
Methylene Chloride | [6 empty] | 2.13e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | [11 empty] | 0.000147 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 4.12e-05 | lb/MMBtu | AP-42 Table 3.2-3 (8/00)
n-Hexane | [12 empty] | 0.0017647 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 0.000445 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | [9 empty] | 2.8431e-05 | lb/MMBtu | VCAPCD (5/172001)
Nickel | [6 empty] | 1.62e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 4.6e-06 | lb/MMBtu | AP-42 Table 3.1-5 (4/00) |  |  |  | 3 | lb/TBtu | 3000000 | lb/MMBtu | AP-42 Table 1.3-8 (9/98) | [15 empty] | 0.00552 | lb/ton | AP-42 Table 2.1-9 (10/96) | 0.16 | lb/1000 gal. | AP-42 Table 1.11-4 (10/96)
PAHs | 2.2e-06 | lb/MMBtu | EPA AP-42 Table 3.1-3 (4/00) | 2.25e-06 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 4.03e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 4e-05 | lb/MMBtu | AP-42 Table 3.1-4 (4/00) | [8 empty] | 0.000134 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 0.000141 | lb/MMBtu | AP-42 Table 3.2-3 (8/00) | 0.000168 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 0.000212 | lb/MMBtu | AP-42 Table 3.4-3 (10/96) | 1.3725e-05 | lb/MMBtu | VCAPCD (5/172001)
Phenol | [20 empty] | 4.21e-05 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | [15 empty] | 2.8e-05 | lb/1000 gal. | AP-42 Table 1.11-5 (10/96)
Phosphorus
POM (Total) | 1.3e-06 | g/bhp-hr |  | 1.37e-06 |  |  | 3.52e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 3.5e-05 | lb/MMBtu | AP-42 Table 3.1-4 (4/00) | 6.848e-07 | lb/MMBtu |  | 0.0033 | lb/1000 gal. | 24.5262 | lb/MMBtu | AP-42 Table 1.3-8 (9/98) | 0.00013014 |  |  | 9.71e-05 |  |  | 0.00016826 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 0.00021153 |  |  | 1.0573e-08 | lb/MMBtu | VCAPCD (5/172001) | 0 |  |  | 0.0002003 | lb/1000 gal. | AP-42 (10/96)
POM 2-Methylnaphthalene | [12 empty] | 2.35e-08 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 2.14e-05 | lb/MMBtu | AP-42 Table 3.2-1 (8/00)
POM 3-Methylcholanthrene | [12 empty] | 1.8e-09 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98)
POM 7,12-Dimethylbenz(a)anthracene | [12 empty] | 1.57e-08 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98)
POM Acenaphthene | [12 empty] | 1.8e-09 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 1.33e-06 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) |  |  |  | 1.42e-06 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 4.68e-06 | lb/MMBtu | AP-42 Table 3.4-3 (10/96)
POM Acenaphthylene | [12 empty] | 1.8e-09 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 3.17e-06 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) |  |  |  | 5.06e-06 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 9.23e-06 | lb/MMBtu | AP-42 Table 3.4-3 (10/96)
POM Anthracene | [12 empty] | 2.4e-09 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 7.18e-07 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) |  |  |  | 1.87e-06 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 1.23e-06 | lb/MMBtu | AP-42 Table 3.4-3 (10/96)
POM Benz(a)anthracene | [12 empty] | 1.8e-09 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 3.36e-07 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) |  |  |  | 1.68e-06 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 6.22e-07 | lb/MMBtu | AP-42 Table 3.4-3 (10/96)
POM Benzo(a)pyrene | [12 empty] | 1.2e-09 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 5.68e-09 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) |  |  |  | 1.88e-07 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 2.57e-07 | lb/MMBtu | AP-42 Table 3.4-3 (10/96)
POM Benzo(b)fluoranthene | [12 empty] | 1.8e-09 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 8.51e-09 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) |  |  |  | 9.91e-08 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 1.11e-06 | lb/MMBtu | AP-42 Table 3.4-3 (10/96)
POM Benzo(g,h,i)perylene | [12 empty] | 1.2e-09 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 2.48e-08 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) |  |  |  | 4.89e-07 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 5.56e-07 | lb/MMBtu | AP-42 Table 3.4-3 (10/96)
POM Benzo(k)fluoranthene | [12 empty] | 1.8e-09 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 4.26e-09 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) |  |  |  | 1.55e-07 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 2.18e-07 | lb/MMBtu | AP-42 Table 3.4-3 (10/96)
POM Chrysene | [12 empty] | 1.8e-09 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 6.72e-07 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) |  |  |  | 3.53e-07 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 1.53e-06 | lb/MMBtu | AP-42 Table 3.4-3 (10/96)
POM Dibenz(a,h)anthracene | [12 empty] | 1.2e-09 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [11 empty] | 5.83e-07 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 3.46e-07 | lb/MMBtu | AP-42 Table 3.4-3 (10/96)
POM Fluoranthene | [12 empty] | 2.9e-09 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 3.61e-07 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) |  |  |  | 7.61e-06 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 4.03e-06 | lb/MMBtu | AP-42 Table 3.4-3 (10/96)
POM Fluorene | [12 empty] | 2.7e-09 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 1.69e-06 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) |  |  |  | 2.94e-05 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 1.28e-05 | lb/MMBtu | AP-42 Table 3.4-3 (10/96)
POM Indeno(1,2,3-c,d)pyrene | [12 empty] | 1.8e-09 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 9.93e-09 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) |  |  |  | 3.75e-07 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 4.14e-07 | lb/MMBtu | AP-42 Table 3.4-3 (10/96)
POM Naphthalene | 1.3e-06 | lb/MMBtu | EPA AP-42 Table 3.1-3 (4/00) | 1.37e-06 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 3.52e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 3.5e-05 | lb/MMBtu | AP-42 Table 3.1-4 (4/00) | 5.98e-07 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 9.63e-05 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 9.71e-05 | lb/MMBtu | AP-42 Table 3.2-3 (8/00) | 8.48e-05 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 0.00013 | lb/MMBtu | AP-42 Table 3.4-3 (10/96) | 1.0784e-05 | lb/MMBtu | VCAPCD (5/172001) |  |  |  | 9.2e-05 | lb/1000 gal. | AP-42 Table 1.11-5 (10/96)
POM Phenanthrene | [12 empty] | 1.67e-08 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 3.53e-06 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) |  |  |  | 2.94e-05 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 4.08e-05 | lb/MMBtu | AP-42 Table 3.4-3 (10/96) | [6 empty] | 0.0001 | lb/1000 gal. | AP-42 Table 1.11-5 (10/96)
POM Pyrene | [12 empty] | 4.9e-09 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 5.84e-07 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) |  |  |  | 4.78e-06 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 3.71e-06 | lb/MMBtu | AP-42 Table 3.4-3 (10/96) | [6 empty] | 8.3e-06 | lb/1000 gal. | AP-42 Table 1.11-5 (10/96)
Propional[dehyde]
Propylene Oxide | 2.9e-05 | lb/MMBtu | EPA AP-42 Table 3.1-3 (4/00) | 2.86e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00)
Selenium | [6 empty] | 2.88e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 2.5e-05 | lb/MMBtu | AP-42 Table 3.1-5 (4/00) |  |  |  | 15 | lb/TBtu | 15000000 | lb/MMBtu | AP-42 Table 1.3-10 (9/98)
Styrene | [20 empty] | 5.48e-05 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 1.19e-05 | lb/MMBtu | AP-42 Table 3.2-3 (8/00)
Tetrachloroethylene | [6 empty] | 3.24e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00)
Toluene | 0.00013 | lb/MMBtu | EPA AP-42 Table 3.1-3 (4/00) | 9.37e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | [6 empty] | 3.3333e-06 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 0.000963 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 0.000558 | lb/MMBtu | AP-42 Table 3.2-3 (8/00) | 0.000409 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 0.000281 | lb/MMBtu | AP-42 Table 3.4-3 (10/96) | 5.6863e-05 | lb/MMBtu | VCAPCD (5/172001)
Trichloroethylene | [6 empty] | 2.75e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00)
Vinyl Chloride | [6 empty] | 5.27e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | [11 empty] | 2.47e-05 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 7.18e-06 | lb/MMBtu | AP-42 Table 3.2-3 (8/00)
Vinylidene Chloride | [6 empty] | 2.02e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00)
Xylenes(m,p,o) | 6.4e-05 | lb/MMBtu | EPA AP-42 Table 3.1-3 (4/00) | 5.48e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | [14 empty] | 0.000268 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 0.000195 | lb/MMBtu | AP-42 Table 3.2-3 (8/00) | 0.000285 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 0.000193 | lb/MMBtu | AP-42 Table 3.4-3 (10/96) | 2.8431e-05 | lb/MMBtu | VCAPCD (5/172001)
CDD/CDF | [35 empty] | 2.94e-06 | lb/ton | AP-42 Table 2.1-9 (10/96)
[17 empty] | Diesel HHV | 134550 | Btu/gal | [13 empty] | Fuel Gas HHV | 1020 | Btu/scf
TOTAL | 0.0010273 |  |  | 0.0034828 |  |  | 0.0015792 |  |  | 0.0012879 |  |  | 0.0018448 | lb/MMBtu | All |  |  | 49000477.8893 |  |  | 0.079535 |  |  | 0.032418 |  |  | 0.0040419 |  |  | 0.0017855 |  |  | 0.0028971 |  |  | 2.1675 |  |  | 0.47376
[13 empty] | 0.0018448 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98)
Note on AK1: Aleksa, Deborah: Emission Factors do not line up with using Heat Duty. Need to adjust calculation in HAPs calc sheet if equipment present
Note on Y36: kmalmquist: PAH emission factor in AP-42 Table 3.2-3 (7/00) missing in GRI-HAPCalc. Assume 7,276 Btu/hp-hr.
Note on Q39: kmalmquist: Includes AP-42 EF for total POM plus the FIRE EF for fluoranthene
Note on P62: kmalmquist: Revised 10/21/02 - see letter from Paul Drayton (GRI)

## Emission Factor Look Up (hidden)
Equipment/Fuel | 1,1,2,2-Tetrachloroethane | 1,1,2-Trichloroethane | 1,3-Butadiene | 1,3-Dichloropropene | 1,4-Dichlorobenzene | 2,2,4-Trimethylpentane | Acetaldehyde | Acrolein | Antimony | Arsenic | Benzene | Beryllium | Biphenyl | Cadmium | Carbon Tetrachloride | Chlorobenzene | Chloroform | Chromium | Cobalt | Dibutylphthalate | Ethylbenzene | Ethylene Dibromide | Ethylene Dichloride | Formaldehyde | HCl | Lead | Manganese | Mercury | Methanol | Methylene Chloride | n-Hexane | Nickel | PAHs | Phenol | Phosphorus | POM (Total) | POM 2-Methylnaphthalene | POM 3-Methylcholanthrene | POM 7,12-Dimethylbenz(a)anthracene | POM Acenaphthene | POM Acenaphthylene | POM Anthracene | POM Benz(a)anthracene | POM Benzo(a)pyrene | POM Benzo(b)fluoranthene | POM Benzo(g,h,i)perylene | POM Benzo(k)fluoranthene | POM Chrysene | POM Dibenz(a,h)anthracene | POM Fluoranthene | POM Fluorene | POM Indeno(1,2,3-c,d)pyrene | POM Naphthalene | POM Phenanthrene | POM Pyrene | Propional[dehyde] | Propylene Oxide | Selenium | Styrene | Tetrachloroethylene | Toluene | Trichloroethylene | Vinyl Chloride | Vinylidene Chloride | Xylenes(m,p,o) | CDD/CDF
CT¦>80%¦NG | 0 | 0 | 4.3e-07 | 0 | 0 | 0 | 4e-05 | 6.4e-06 | 0 | 0 | 1.2e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2e-05 | 0 | 0 | 0.00071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2e-06 | 0 | 0 | 1.3e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3e-06 | 0 | 0 | 0 | 2.9e-05 | 0 | 0 | 0 | 0.00013 | 0 | 0 | 0 | 6.4e-05 | 0
CT¦0¦NG | 0 | 0 | 4.29e-07 | 0 | 0 | 0 | 4.45e-05 | 8.31e-06 | 0 | 0 | 0.000103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.58e-05 | 0 | 0 | 0.00312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.25e-06 | 0 | 0 | 1.37e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.37e-06 | 0 | 0 | 0 | 2.86e-05 | 0 | 0 | 0 | 9.37e-05 | 0 | 0 | 0 | 5.48e-05 | 0
CT¦>80%¦D | 0 | 0 | 1.6e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1e-05 | 5.5e-05 | 3.1e-07 | 0 | 4.8e-06 | 0 | 0 | 0 | 1.1e-05 | 0 | 0 | 0 | 0 | 0 | 0.00028 | 0 | 1.4e-05 | 0.00079 | 1.2e-06 | 0 | 0 | 0 | 4.6e-06 | 4e-05 | 0 | 0 | 3.5e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5e-05 | 0 | 0 | 0 | 0 | 2.5e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CT¦0¦D | 0 | 0 | 1.65e-05 | 0 | 2.97e-05 | 0 | 3.03e-05 | 0 | 0 | 1.1e-05 | 5.48e-05 | 3.07e-07 | 0 | 3.75e-06 | 3.06e-05 | 2.49e-05 | 2.55e-05 | 8.43e-06 | 0 | 0 | 0 | 0 | 2.02e-05 | 0.000245 | 0 | 1.34e-05 | 0.000789 | 1.2e-06 | 0 | 2.13e-05 | 0 | 1.62e-05 | 4.03e-05 | 0 | 0 | 3.52e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.52e-05 | 0 | 0 | 0 | 0 | 2.88e-05 | 0 | 3.24e-05 | 0 | 2.75e-05 | 5.27e-05 | 2.02e-05 | 0 | 0
Heater¦0¦NG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0588e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3529e-05 | 0 | 4.902e-07 | 0 | 0 | 0 | 0 | 0.0017647 | 0 | 0 | 0 | 0 | 6.848e-07 | 2.35e-08 | 1.8e-09 | 1.57e-08 | 1.8e-09 | 1.8e-09 | 2.4e-09 | 1.8e-09 | 1.2e-09 | 1.8e-09 | 1.2e-09 | 1.8e-09 | 1.8e-09 | 1.2e-09 | 2.9e-09 | 2.7e-09 | 1.8e-09 | 5.98e-07 | 1.67e-08 | 4.9e-09 | 0 | 0 | 0 | 0 | 0 | 3.3333e-06 | 0 | 0 | 0 | 0 | 0
Heater¦0¦D | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4000000 | 0 | 3000000 | 0 | 3000000 | 0 | 0 | 0 | 3000000 | 0 | 0 | 0 | 0 | 0 | 453.3631 | 0 | 9000000 | 6000000 | 3000000 | 0 | 0 | 0 | 3000000 | 0 | 0 | 0 | 24.5262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ICE¦2-Stroke¦NG | 6.63e-05 | 5.27e-05 | 0.00082 | 4.38e-05 | 0 | 0.000846 | 0.00776 | 0.00778 | 0 | 0 | 0.00194 | 0 | 3.95e-06 | 0 | 6.07e-05 | 4.44e-05 | 4.71e-05 | 0 | 0 | 0 | 0.000108 | 7.34e-05 | 0 | 0.0552 | 0 | 0 | 0 | 0 | 0.00248 | 0.000147 | 0.000445 | 0 | 0.000134 | 4.21e-05 | 0 | 0.00013014 | 2.14e-05 | 0 | 0 | 1.33e-06 | 3.17e-06 | 7.18e-07 | 3.36e-07 | 5.68e-09 | 8.51e-09 | 2.48e-08 | 4.26e-09 | 6.72e-07 | 0 | 3.61e-07 | 1.69e-06 | 9.93e-09 | 9.63e-05 | 3.53e-06 | 5.84e-07 | 0 | 0 | 0 | 5.48e-05 | 0 | 0.000963 | 0 | 2.47e-05 | 0 | 0.000268 | 0
ICE¦4-Stroke¦NG | 2.53e-05 | 1.53e-05 | 0.000663 | 1.27e-05 | 0 | 0 | 0.00279 | 0.00263 | 0 | 0 | 0.00158 | 0 | 0 | 0 | 1.77e-05 | 1.29e-05 | 1.37e-05 | 0 | 0 | 0 | 2.48e-05 | 2.13e-05 | 0 | 0.0205 | 0 | 0 | 0 | 0 | 0.00306 | 4.12e-05 | 0 | 0 | 0.000141 | 0 | 0 | 9.71e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.71e-05 | 0 | 0 | 0 | 0 | 0 | 1.19e-05 | 0 | 0.000558 | 0 | 7.18e-06 | 0 | 0.000195 | 0
ICE¦<600hp¦D | 0 | 0 | 3.91e-05 | 0 | 0 | 0 | 0.000767 | 9.25e-05 | 0 | 0 | 0.000933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.000168 | 0 | 0 | 0.00016826 | 0 | 0 | 0 | 1.42e-06 | 5.06e-06 | 1.87e-06 | 1.68e-06 | 1.88e-07 | 9.91e-08 | 4.89e-07 | 1.55e-07 | 3.53e-07 | 5.83e-07 | 7.61e-06 | 2.94e-05 | 3.75e-07 | 8.48e-05 | 2.94e-05 | 4.78e-06 | 0 | 0 | 0 | 0 | 0 | 0.000409 | 0 | 0 | 0 | 0.000285 | 0
ICE¦>600hp¦D | 0 | 0 | 0 | 0 | 0 | 0 | 2.52e-05 | 7.88e-06 | 0 | 0 | 0.000776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.89e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.000212 | 0 | 0 | 0.00021153 | 0 | 0 | 0 | 4.68e-06 | 9.23e-06 | 1.23e-06 | 6.22e-07 | 2.57e-07 | 1.11e-06 | 5.56e-07 | 2.18e-07 | 1.53e-06 | 3.46e-07 | 4.03e-06 | 1.28e-05 | 4.14e-07 | 0.00013 | 4.08e-05 | 3.71e-06 | 0 | 0 | 0 | 0 | 0 | 0.000281 | 0 | 0 | 0 | 0.000193 | 0
Flare¦0¦NG | 0 | 0 | 0 | 0 | 0 | 0 | 4.2157e-05 | 9.8039e-06 | 0 | 0 | 0.00015588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0014157 | 0 | 0 | 0.0011461 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8431e-05 | 0 | 1.3725e-05 | 0 | 0 | 1.0573e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0784e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6863e-05 | 0 | 0 | 0 | 2.8431e-05 | 0
Incinerators¦0¦NG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.000669 | 0 | 0 | 0 | 0.00241 | 0 | 0 | 0 | 0.00331 | 0 | 0 | 0 | 0 | 0 | 0 | 2.15 | 0 | 0 | 0.0056 | 0 | 0 | 0 | 0.00552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.94e-06
Burners¦0¦D | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0045 | 0.06 | 0 | 0.0018 | 0 | 0.012 | 0 | 0 | 0 | 0.18 | 0.0052 | 3.4e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0.16 | 0 | 2.8e-05 | 0 | 0.0002003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.2e-05 | 0.0001 | 8.3e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tank¦0¦D | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fugitive¦0¦D | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0