## Diesel Eng-DPF (4060hp)
Alaska LNG Project
Diesel Driven Equipment - Black Start Generator
Diesel Particulate Filter (DPF) PM Cost Effectiveness Analysis
Cost Quantification:
Cost Category | Project Cost | Default Estimate | Default % Applied | EPA Equation / Estimate Basis | Reference | Default | Final | Final Units | Cond Format | Notes
Direct Capital Costs
Purchased Equipment:
Purchased Equipment Costs | 163650.9189 |  | - | A | Vendor Estimate (DCL email Aug. 1, 2018) |  | 163650.9189 | $ | FALSE | Need input
Ammonia System |  |  | - | B | Included in A |  | 0 | $ | Req'd | Need input
Instrumentation & Controls |  | 16365.0919 | 10% | C = 0.10 x A |  |  | 16365.0919 | $
Freight |  | 8182.5459 | 5% | D = 0.05 x (A+B) |  |  | 8182.5459 | $
Taxes (Enter sales tax rate in "% Applied") |  | 0 | 0% | TaxRate x (A+B+C) | No sales tax in Alaska |  | 0 | $
Total Purchased Equipment Cost (PE) | 188198.5568 |  | - | PE |  |  | 188198.5568 | $
Direct Installation Costs:
Foundation & Supports | 0 | 18819.8557 | 10% | 0.10 x PE | Not needed, equipment is skid mounted |  | 0 | $
Erection and Handling |  | 65869.4949 | 35% | 0.35 x PE |  |  | 65869.4949 | $
Electrical |  | 11291.9134 | 6% | 0.06 x PE |  |  | 11291.9134 | $
Piping |  | 15055.8845 | 8% | 0.08 x PE |  |  | 15055.8845 | $
Insulation |  | 3763.9711 | 2% | 0.02 x PE |  |  | 3763.9711 | $
Painting | 0 | 7527.9423 | 4% | 0.04 x PE | Not needed, included in equipment purchase price |  | 0 | $
Site Preparation | 11455.5643 |  | 7% | 0.07 x (A+B) | engineering judgement |  | 11455.5643 | $ | FALSE
Total Direct Installation Cost (DI) | 107436.8283 |  | - | DI |  |  | 107436.8283 | $
Total Direct Capital Costs (DC) | 295635.385 |  | - | DC = PE + DI |  |  | 295635.385 | $
Indirect Capital Costs
Indirect Costs:
Engineering & Supervision |  | 28229.7835 | 15% | 0.15 x PE |  |  | 28229.7835 | $ | FALSE
Construction and Field Expenses |  | 18819.8557 | 10% | 0.10 x PE |  |  | 18819.8557 | $ | FALSE
Contractor Fees |  | 9409.9278 | 5% | 0.05 x PE |  |  | 9409.9278 | $ | FALSE
Startup-up |  | 1881.9856 | 1% | 0.01 x PE |  |  | 1881.9856 | $ | FALSE
Performance Testing |  | 1881.9856 | 1% | 0.01 x PE |  |  | 1881.9856 | $ | FALSE
Total Indirect Costs (TIC) | 60223.5382 |  | - | IC |  |  | 60223.5382 | $
Capital Investment:
Project Contingency |  | 53378.8385 | 15% | E = 0.15 x (DC+IC) | OAQPS (15% of DC & TIC) |  | 53378.8385 | $
Preproduction Cost |  | 8184.7552 | 2% | F = 0.02 x (DC+IC+Cont) | OAQPS (2% of DC & TIC & Proj Contingency) |  | 8184.7552 | $
Inventory Capital (initial reagent fill) |  | 0 | - | G = [Storage Gal] x [Reagent $/gal] | See parameters below |  | 0 | $ |  | Eqn. 2.44 (Section 4.2, Ch. 2)
Total Capital Investment | 417422.5169 |  | - | TCI = DC + IC + E + F + G |  |  | 417422.5169 | $
Direct Annual Costs
Direct Annual Costs:
Operating Labor |  |  | - |  | Vendor Supplied |  | 0 |  | Req'd | Need input
Supervisory Labor |  | 0 | 15% | 15% of Op. Labor | OAQPS (15% of Op Labor) |  | 0 |  |  | Need input
Maintenance Labor |  | 6261.3378 | 1.5% | 0.015 x TCI | OAQPS (1.5% of TCI) |  | 6261.3378
Maintenance Materials |  | 6261.3378 | - | 100% of Maint. Labor | OAQPS (15% of Maint. Labor) |  | 6261.3378
Annual Reagent Cost | 0 | 0 | - | q*Cost*[op hr/yr] | No Reagent needed |  | 0 |  |  | Eqn 2.47 (Section 4.2, Ch. 2)
Annual Electricity Cost |  | 0 | - | See parameters below | See parameters below |  | 0 |  |  | Eqn 2.49 (Section 4.2, Ch. 2)
Catalyst Replacement |  | 0 | - | See parameters below | See parameters below |  | 0
Catalyst Disposal Cost |  | 0 | 10% | 0.100 x Cat Repl | Engineering Estimate |  | 0
Fuel Penalty Costs (specify) |  |  | - |  | Vendor Supplied |  | 0 |  | Req'd | Need input
Other Maintenance Cost (specify) |  |  | - |  | Vendor Supplied |  | 0 |  | Req'd | Need input
Total Direct Annual Costs | 12522.6755 |  | - | DAC |  |  | 12522.6755
Indirect Annual Costs
Indirect Annual Costs:
Overhead |  | 7513.6053 | 60% | 0.600 x Op/Super/Maint Labor & Mtls | OAQPS (60% of Op/Super/Maint. Labor & Mtls) |  | 7513.6053
Property Tax |  | 6261.3378 | 1.5% | 0.0150 x TCI | OAQPS (1%) |  | 6261.3378
Insurance |  | 4174.2252 | 1% | 0.010 x TCI | OAQPS (1%) |  | 4174.2252
General Administrative |  | 8348.4503 | 2% | 0.020 x TCI | OAQPS (2%) |  | 8348.4503
Total Indirect Annual Costs | 26297.6186 |  | - | DAC |  |  | 26297.6186
Capital Recovery Cost
Equipment Life (years) |  | 20 | - | n | Vendor Supplied |  | 20 | years | FALSE
Interest Rate | 7% | 7% | - | i | 7% per Agrium US Inc, Kenai Nitrogen Operations Facility Air Quality Control Construction Permit AQ0083CPT06 |  | 0.07 | % | FALSE
Capital Recovery Factor | 0.094393 |  | - | CRF = i/(1-(1+i)^-n) | -
Capital Recovery Cost (CRC) | 39401.7326 |  | - |  | OAQPS Eqn 2.54 (Section 4.2, Ch. 2) |  | 39401.7326 |  |  | Eqn 2.54 (Section 4.2, Ch. 2)
Total Annual Costs | 78222.0267 |  | - | TAC = DA + IDAC + CRC | OAQPS Eqn 2.56 (Section 4.2, Ch. 2) |  | 78222.0267 | $/yr |  | Eqn 2.56 (Section 4.2, Ch. 2)
Cost Effectiveness Analysis:
| PM |  |  |  | Reference
Uncontrolled Emissions (tpy) | 0.06713 |  |  |  | PTE Calculations before add on emissions controls
Controlled PM Emissions (tpy) | 0.006713 |  |  |  | Vendor Emissions Reduction Percentage (90%)
PM Reduction (tpy) | 0.060417 |  |  |  | Calculated below
Total Annual Costs | 78222.0267 |  |  |  | Calculated above
Cost Effectiveness ($/ton/yr) | 1294709.4077 |  |  |  | OAQPS Eqn 2.58 (Section 4.2, Ch. 2)
Cost Effectiveness Threshold ($/ton/yr) | [8 empty] | Req'd
Conclusion:
Project costs exceed BACT cost effectiveness threshold and may not be considered cost effective.
Design Parameters:
Enter values in boxes below. Where default value is available, entered value will override default.
Required data is highlighted yellow.
Combustion Unit Sizing | [5 empty] | Default | Final | Final Units | Cond Format | Notes
Reference
Turbine heat capacity: |  | MMBtu/hr |  |  |  |  | 0 | MMBtu/hr | Req'd
Duct burner heat capacity, if applicable: |  | MMBtu/hr |  |  |  |  | 0 | MMBtu/hr | FALSE
NOx Emission Rates
Reference
Turbine uncontrolled NOx concentration: |  | lb NOx/MMBtu |  |  |  | 0 | 0 | lb/MMBtu | FALSE
or |  | lb NOx/MMscf |  |  |  | 0 |  |  | FALSE
or |  | ppmv @ 15% O2 |  |  | Assumption for baseline/uncontrolled emissions | 0 |  |  | FALSE
or (default) |  | ppmv @ 15% O2 |  |  |  | 0 |  |  | FALSE
Duct burner uncontrolled NOx concentration: |  | lb NOx/MMBtu |  |  |  | 0 | 0 | lb/MMBtu | N/A
or |  | lb NOx/MMscf |  |  |  | 0 |  |  | N/A
or |  | ppmv @ 3% O2 |  |  |  | 0 |  |  | N/A
or (default) |  | ppmv @ 3% O2 |  |  |  | 0 |  |  | N/A
Controlled NOx concentration: |  | lb NOx/MMBtu |  |  |  | 0 | 0 | lb/MMBtu | Req'd
or |  | lb NOx/MMscf |  |  |  | 0 |  |  | Req'd
or |  | ppmv @ 15% O2 |  |  | Most stringent limit identified as BACT | 0 |  |  | Req'd
Natural Gas Properties
Reference
HHV [Default: 1050 Btu/scf] |  | Btu/scf |  |  |  | 1050 | 1050 | Btu/scf | FALSE
F-factor (dry) [Default: 8710 dscf/MMBtu] |  | dscf/MMBtu |  |  | EPA 40 CFR Part 60 Appendix A, Method 19, Table 19-2 | 8710 | 8710 | dscf/MMBtu | FALSE
Operational Parameters
Reference
Max annual op hours [Default: 8760 hr/yr] | 500 | hr/yr |  |  |  | 8760 | 500 | hours | FALSE
Annual Electricity Costs: Enter values below. Where default value is available, entered number overrides default.
Reference
Power demand: | 3027.542 | kW |  |  | Calculated below | #DIV/0! | 3027.542 | kW |  | Eqn 2.48 (Section 4.2, Ch. 2)
If power demand is not known, estimate on the basis of the parameters below:
delta P duct [Default: 3 in H2O] |  |  |  |  | OAQPS Eqn 2.48 (Section 4.2, Ch. 2) | 3 | 3 | in H2O | N/A
delta P catalyst (per layer) [Default: 1 in H2O] |  |  |  |  | OAQPS Eqn 2.48 (Section 4.2, Ch. 2) | 1 | 1 | in H2O | N/A
number of layers of catalyst | 1 | [5 empty] | 1 | # layers | N/A
Calculated Power demand: | 3027.542 | kW |  |  | OAQPS Eqn 2.48 (Section 4.2, Ch. 2) |  |  |  | N/A
Electricity Cost [Default: 0.1572 $/kWh] | 0 | $/kWh |  |  |  | 0.1572 | 0 | $/kWh | FALSE
Aqueous Ammonia Costs: Enter values below or parameters to estimate.
Reference
Aqueous ammonia cost: |  | $/gallon |  |  |  |  | 0 | $/gallon | Req'd
Aqueous ammonia storage volume: |  | gallons |  |  | Calculated below |  | 0 | gallons | Req'd
or |  | days' worth |  |  | Engineering Estimate |  | 0 | gallons | Req'd
Aqueous ammonia consumption rate: |  | gal/hr |  |  | Calculated below | 0 | 0 | gal/hr
If aqueous ammonia consumption rate not known, estimate on the basis of the parameters below:
Stored NH3 concentration [Default: 19.4%] |  | wt% |  |  |  | 19.4% | 19.4% | wt% | FALSE | Eqn 2.34 (Section 4.2, Ch. 2)
NH3 solution mass flow rate (msol) |  | lb/hr |  |  | Calculated below | 0 | 0 | lb/hr | FALSE | Eqn 2.32, 2.33 (Section 4.2, Ch. 2)
NH3 solution density [Default: 7.782 lb/gal] |  | lb/gal |  |  | Engineeering Data | 7.7818 | 7.7818 | lb/gal | FALSE
Calculated Aqueous ammonia consumption rate: | 0 | gal/hr |  |  | OAQPS Eqn 2.32-2.34 (Section 4.2, Ch. 2) |  |  |  | FALSE
Catalyst Costs:
Reference
Initial catalyst cost: |  |  |  |  | Vendor Data |  | 0 | $ | Req'd
Catalyst replacement frequency: |  | years |  |  |  |  | 0 | years | Req'd
Interest Rate | 7% | % |  |  | ADEC Default |  | 7% | % | FALSE
Annual Catalyst Replacement Cost | 0 |  |  |  | OAQPS Eqn 2.51 (Section 4.2, Ch. 2) | 0 | 0 | $ | FALSE | Eqn 2.51 (Section 4.2, Ch. 2)
* OAQPS refers to the EPA Air Pollution Control Cost Manual, Sixt Edition and subsequent revisions.
Purchased Equipment: | 2018 | 2025
Purchased Equipment Costs | 121101.68 | 163650.9189 | Annual Index: | CEPCI
|  |  | 2016 | 541.7
|  |  | 2017 | 567.5
|  |  | 2018 | 603.1
|  |  | 2019 | 607.5
|  |  | 2020 | 596.2
|  |  | 2021 | 708.8
|  |  | 2022 | 816
|  |  | 2023 | 797.9
|  |  | 2024 | 799.5
|  |  | 2025 | 815
Note on I130: Note: From EIA data, Table 5.6.A Nov 2014 - Retail Price of Electricity to Industrial Customers in Alaska: http://www.eia.gov/electricity/monthly/epm_table_grapher.cfm?t=epmt_5_06_a

## Diesel Eng-DPF (250hp)
Alaska LNG Project
Diesel Driven Equipment - Firewater Pump
Diesel Particulate Filter (DPF) PM Cost Effectiveness Analysis
Cost Quantification:
Cost Category | Project Cost | Default Estimate | Default % Applied | EPA Equation / Estimate Basis | Reference | Default | Final | Final Units | Cond Format | Notes
Direct Capital Costs
Purchased Equipment:
Purchased Equipment Costs | 10077.7027 |  | - | A | Vendor Estimate (DCL email Aug. 1, 2018) |  | 10077.7027 | $ | FALSE | Need input
Ammonia System |  |  | - | B | Included in A |  | 0 | $ | Req'd | Need input
Instrumentation & Controls |  | 1007.7703 | 10% | C = 0.10 x A |  |  | 1007.7703 | $
Freight |  | 503.8851 | 5% | D = 0.05 x (A+B) |  |  | 503.8851 | $
Taxes (Enter sales tax rate in "% Applied") |  | 0 | 0% | TaxRate x (A+B+C) | No sales tax in Alaska |  | 0 | $
Total Purchased Equipment Cost (PE) | 11589.3581 |  | - | PE |  |  | 11589.3581 | $
Direct Installation Costs:
Foundation & Supports | 0 | 1158.9358 | 10% | 0.10 x PE | Not needed, equipment is skid mounted |  | 0 | $
Erection and Handling |  | 4056.2753 | 35% | 0.35 x PE |  |  | 4056.2753 | $
Electrical |  | 695.3615 | 6% | 0.06 x PE |  |  | 695.3615 | $
Piping |  | 927.1486 | 8% | 0.08 x PE |  |  | 927.1486 | $
Insulation |  | 231.7872 | 2% | 0.02 x PE |  |  | 231.7872 | $
Painting | 0 | 463.5743 | 4% | 0.04 x PE | Not needed, included in equipment purchase price |  | 0 | $
Site Preparation | 705.4392 |  | 7% | 0.07 x (A+B) | engineering judgement |  | 705.4392 | $ | FALSE
Total Direct Installation Cost (DI) | 6616.0118 |  | - | DI |  |  | 6616.0118 | $
Total Direct Capital Costs (DC) | 18205.3699 |  | - | DC = PE + DI |  |  | 18205.3699 | $
Indirect Capital Costs
Indirect Costs:
Engineering & Supervision |  | 1738.4037 | 15% | 0.15 x PE |  |  | 1738.4037 | $ | FALSE
Construction and Field Expenses |  | 1158.9358 | 10% | 0.10 x PE |  |  | 1158.9358 | $ | FALSE
Contractor Fees |  | 579.4679 | 5% | 0.05 x PE |  |  | 579.4679 | $ | FALSE
Startup-up |  | 115.8936 | 1% | 0.01 x PE |  |  | 115.8936 | $ | FALSE
Performance Testing |  | 115.8936 | 1% | 0.01 x PE |  |  | 115.8936 | $ | FALSE
Total Indirect Costs (TIC) | 3708.5946 |  | - | IC |  |  | 3708.5946 | $
Capital Investment:
Project Contingency |  | 3287.0947 | 15% | E = 0.15 x (DC+IC) | OAQPS (15% of DC & TIC) |  | 3287.0947 | $
Preproduction Cost |  | 504.0212 | 2% | F = 0.02 x (DC+IC+Cont) | OAQPS (2% of DC & TIC & Proj Contingency) |  | 504.0212 | $
Inventory Capital (initial reagent fill) |  | 0 | - | G = [Storage Gal] x [Reagent $/gal] | See parameters below |  | 0 | $ |  | Eqn. 2.44 (Section 4.2, Ch. 2)
Total Capital Investment | 25705.0804 |  | - | TCI = DC + IC + E + F + G |  |  | 25705.0804 | $
Direct Annual Costs
Direct Annual Costs:
Operating Labor |  |  | - |  | Vendor Supplied |  | 0 |  | Req'd | Need input
Supervisory Labor |  | 0 | 15% | 15% of Op. Labor | OAQPS (15% of Op Labor) |  | 0 |  |  | Need input
Maintenance Labor |  | 385.5762 | 1.5% | 0.015 x TCI | OAQPS (1.5% of TCI) |  | 385.5762
Maintenance Materials |  | 385.5762 | - | 100% of Maint. Labor | OAQPS (15% of Maint. Labor) |  | 385.5762
Annual Reagent Cost | 0 | 0 | - | q*Cost*[op hr/yr] | No Reagent needed |  | 0 |  |  | Eqn 2.47 (Section 4.2, Ch. 2)
Annual Electricity Cost |  | 0 | - | See parameters below | See parameters below |  | 0 |  |  | Eqn 2.49 (Section 4.2, Ch. 2)
Catalyst Replacement |  | 0 | - | See parameters below | See parameters below |  | 0
Catalyst Disposal Cost |  | 0 | 10% | 0.100 x Cat Repl | Engineering Estimate |  | 0
Fuel Penalty Costs (specify) |  |  | - |  | Vendor Supplied |  | 0 |  | Req'd | Need input
Other Maintenance Cost (specify) |  |  | - |  | Vendor Supplied |  | 0 |  | Req'd | Need input
Total Direct Annual Costs | 771.1524 |  | - | DAC |  |  | 771.1524
Indirect Annual Costs
Indirect Annual Costs:
Overhead |  | 462.6914 | 60% | 0.600 x Op/Super/Maint Labor & Mtls | OAQPS (60% of Op/Super/Maint. Labor & Mtls) |  | 462.6914
Property Tax |  | 385.5762 | 1.5% | 0.0150 x TCI | OAQPS (1%) |  | 385.5762
Insurance |  | 257.0508 | 1% | 0.010 x TCI | OAQPS (1%) |  | 257.0508
General Administrative |  | 514.1016 | 2% | 0.020 x TCI | OAQPS (2%) |  | 514.1016
Total Indirect Annual Costs | 1619.4201 |  | - | DAC |  |  | 1619.4201
Capital Recovery Cost
Equipment Life (years) |  | 20 | - | n | Vendor Supplied |  | 20 | years | FALSE
Interest Rate | 7% | 7% | - | i | 7% per Agrium US Inc, Kenai Nitrogen Operations Facility Air Quality Control Construction Permit AQ0083CPT06 |  | 0.07 | % | FALSE
Capital Recovery Factor | 0.094393 |  | - | CRF = i/(1-(1+i)^-n) | -
Capital Recovery Cost (CRC) | 2426.3777 |  | - |  | OAQPS Eqn 2.54 (Section 4.2, Ch. 2) |  | 2426.3777 |  |  | Eqn 2.54 (Section 4.2, Ch. 2)
Total Annual Costs | 4816.9502 |  | - | TAC = DA + IDAC + CRC | OAQPS Eqn 2.56 (Section 4.2, Ch. 2) |  | 4816.9502 | $/yr |  | Eqn 2.56 (Section 4.2, Ch. 2)
Cost Effectiveness Analysis:
| PM |  |  |  | Reference
Uncontrolled Emissions (tpy) | 0.020669 |  |  |  | PTE Calculations before add on emissions controls
Controlled PM Emissions (tpy) | 0.0020669 |  |  |  | Vendor Emissions Reduction Percentage (90%)
PM Reduction (tpy) | 0.018602 |  |  |  | Calculated below
Total Annual Costs | 4816.9502 |  |  |  | Calculated above
Cost Effectiveness ($/ton/yr) | 258941.8815 |  |  |  | OAQPS Eqn 2.58 (Section 4.2, Ch. 2)
Cost Effectiveness Threshold ($/ton/yr) | [8 empty] | Req'd
Conclusion:
Project costs exceed BACT cost effectiveness threshold and may not be considered cost effective.
Design Parameters:
Enter values in boxes below. Where default value is available, entered value will override default.
Required data is highlighted yellow.
Combustion Unit Sizing | [5 empty] | Default | Final | Final Units | Cond Format | Notes
Reference
Turbine heat capacity: |  | MMBtu/hr |  |  |  |  | 0 | MMBtu/hr | Req'd
Duct burner heat capacity, if applicable: |  | MMBtu/hr |  |  |  |  | 0 | MMBtu/hr | FALSE
NOx Emission Rates
Reference
Turbine uncontrolled NOx concentration: |  | lb NOx/MMBtu |  |  |  | 0 | 0 | lb/MMBtu | FALSE
or |  | lb NOx/MMscf |  |  |  | 0 |  |  | FALSE
or |  | ppmv @ 15% O2 |  |  | Assumption for baseline/uncontrolled emissions | 0 |  |  | FALSE
or (default) |  | ppmv @ 15% O2 |  |  |  | 0 |  |  | FALSE
Duct burner uncontrolled NOx concentration: |  | lb NOx/MMBtu |  |  |  | 0 | 0 | lb/MMBtu | N/A
or |  | lb NOx/MMscf |  |  |  | 0 |  |  | N/A
or |  | ppmv @ 3% O2 |  |  |  | 0 |  |  | N/A
or (default) |  | ppmv @ 3% O2 |  |  |  | 0 |  |  | N/A
Controlled NOx concentration: |  | lb NOx/MMBtu |  |  |  | 0 | 0 | lb/MMBtu | Req'd
or |  | lb NOx/MMscf |  |  |  | 0 |  |  | Req'd
or |  | ppmv @ 15% O2 |  |  | Most stringent limit identified as BACT | 0 |  |  | Req'd
Natural Gas Properties
Reference
HHV [Default: 1050 Btu/scf] |  | Btu/scf |  |  |  | 1050 | 1050 | Btu/scf | FALSE
F-factor (dry) [Default: 8710 dscf/MMBtu] |  | dscf/MMBtu |  |  | EPA 40 CFR Part 60 Appendix A, Method 19, Table 19-2 | 8710 | 8710 | dscf/MMBtu | FALSE
Operational Parameters
Reference
Max annual op hours [Default: 8760 hr/yr] | 500 | hr/yr |  |  |  | 8760 | 500 | hours | FALSE
Annual Electricity Costs: Enter values below. Where default value is available, entered number overrides default.
Reference
Power demand: | 186.4375 | kW |  |  | Calculated below | #DIV/0! | 186.4375 | kW |  | Eqn 2.48 (Section 4.2, Ch. 2)
If power demand is not known, estimate on the basis of the parameters below:
delta P duct [Default: 3 in H2O] |  |  |  |  | OAQPS Eqn 2.48 (Section 4.2, Ch. 2) | 3 | 3 | in H2O | N/A
delta P catalyst (per layer) [Default: 1 in H2O] |  |  |  |  | OAQPS Eqn 2.48 (Section 4.2, Ch. 2) | 1 | 1 | in H2O | N/A
number of layers of catalyst | 1 | [5 empty] | 1 | # layers | N/A
Calculated Power demand: | 186.4375 | kW |  |  | OAQPS Eqn 2.48 (Section 4.2, Ch. 2) |  |  |  | N/A
Electricity Cost [Default: 0.1572 $/kWh] | 0 | $/kWh |  |  |  | 0.1572 | 0 | $/kWh | FALSE
Aqueous Ammonia Costs: Enter values below or parameters to estimate.
Reference
Aqueous ammonia cost: |  | $/gallon |  |  |  |  | 0 | $/gallon | Req'd
Aqueous ammonia storage volume: |  | gallons |  |  | Calculated below |  | 0 | gallons | Req'd
or |  | days' worth |  |  | Engineering Estimate |  | 0 | gallons | Req'd
Aqueous ammonia consumption rate: |  | gal/hr |  |  | Calculated below | 0 | 0 | gal/hr
If aqueous ammonia consumption rate not known, estimate on the basis of the parameters below:
Stored NH3 concentration [Default: 19.4%] |  | wt% |  |  |  | 19.4% | 19.4% | wt% | FALSE | Eqn 2.34 (Section 4.2, Ch. 2)
NH3 solution mass flow rate (msol) |  | lb/hr |  |  | Calculated below | 0 | 0 | lb/hr | FALSE | Eqn 2.32, 2.33 (Section 4.2, Ch. 2)
NH3 solution density [Default: 7.782 lb/gal] |  | lb/gal |  |  | Engineeering Data | 7.7818 | 7.7818 | lb/gal | FALSE
Calculated Aqueous ammonia consumption rate: | 0 | gal/hr |  |  | OAQPS Eqn 2.32-2.34 (Section 4.2, Ch. 2) |  |  |  | FALSE
Catalyst Costs:
Reference
Initial catalyst cost: |  |  |  |  | Vendor Data |  | 0 | $ | Req'd
Catalyst replacement frequency: |  | years |  |  |  |  | 0 | years | Req'd
Interest Rate | 7% | % |  |  | ADEC Default |  | 7% | % | FALSE
Annual Catalyst Replacement Cost | 0 |  |  |  | OAQPS Eqn 2.51 (Section 4.2, Ch. 2) | 0 | 0 | $ | FALSE | Eqn 2.51 (Section 4.2, Ch. 2)
* OAQPS refers to the EPA Air Pollution Control Cost Manual, Sixt Edition and subsequent revisions.
Purchased Equipment: | 2018 | 2025
Purchased Equipment Costs | 7457.5 | 10077.7027 | Annual Index: | CEPCI
|  |  | 2016 | 541.7
|  |  | 2017 | 567.5
|  |  | 2018 | 603.1
|  |  | 2019 | 607.5
|  |  | 2020 | 596.2
|  |  | 2021 | 708.8
|  |  | 2022 | 816
|  |  | 2023 | 797.9
|  |  | 2024 | 799.5
|  |  | 2025 | 815
Note on A130: Note: Default cost from EIA data, Table 5.6.A Nov 2014 - Retail Price of Electricity to Industrial Customers in Alaska: http://www.eia.gov/electricity/monthly/epm_table_grapher.cfm?t=epmt_5_06_a
Note on I130: Note: From EIA data, Table 5.6.A Nov 2014 - Retail Price of Electricity to Industrial Customers in Alaska: http://www.eia.gov/electricity/monthly/epm_table_grapher.cfm?t=epmt_5_06_a

## Diesel Eng-DPF (335hp)
Alaska LNG Project
Diesel Driven Equipment - Dormitory Emergency Generator
Diesel Particulate Filter (DPF) PM Cost Effectiveness Analysis
Cost Quantification:
Cost Category | Project Cost | Default Estimate | Default % Applied | EPA Equation / Estimate Basis | Reference | Default | Final | Final Units | Cond Format | Notes
Direct Capital Costs
Purchased Equipment:
Purchased Equipment Costs | 13504.1216 |  | - | A | Vendor Estimate (DCL email Aug. 1, 2018) |  | 13504.1216 | $ | FALSE | Need input
Ammonia System |  |  | - | B | Included in A |  | 0 | $ | Req'd | Need input
Instrumentation & Controls |  | 1350.4122 | 10% | C = 0.10 x A |  |  | 1350.4122 | $
Freight |  | 675.2061 | 5% | D = 0.05 x (A+B) |  |  | 675.2061 | $
Taxes (Enter sales tax rate in "% Applied") |  | 0 | 0% | TaxRate x (A+B+C) | No sales tax in Alaska |  | 0 | $
Total Purchased Equipment Cost (PE) | 15529.7399 |  | - | PE |  |  | 15529.7399 | $
Direct Installation Costs:
Foundation & Supports | 0 | 1552.974 | 10% | 0.10 x PE | Not needed, equipment is skid mounted |  | 0 | $
Erection and Handling |  | 5435.409 | 35% | 0.35 x PE |  |  | 5435.409 | $
Electrical |  | 931.7844 | 6% | 0.06 x PE |  |  | 931.7844 | $
Piping |  | 1242.3792 | 8% | 0.08 x PE |  |  | 1242.3792 | $
Insulation |  | 310.5948 | 2% | 0.02 x PE |  |  | 310.5948 | $
Painting | 0 | 621.1896 | 4% | 0.04 x PE | Not needed, included in equipment purchase price |  | 0 | $
Site Preparation | 945.2885 |  | 7% | 0.07 x (A+B) | engineering judgement |  | 945.2885 | $ | FALSE
Total Direct Installation Cost (DI) | 8865.4558 |  | - | DI |  |  | 8865.4558 | $
Total Direct Capital Costs (DC) | 24395.1957 |  | - | DC = PE + DI |  |  | 24395.1957 | $
Indirect Capital Costs
Indirect Costs:
Engineering & Supervision |  | 2329.461 | 15% | 0.15 x PE |  |  | 2329.461 | $ | FALSE
Construction and Field Expenses |  | 1552.974 | 10% | 0.10 x PE |  |  | 1552.974 | $ | FALSE
Contractor Fees |  | 776.487 | 5% | 0.05 x PE |  |  | 776.487 | $ | FALSE
Startup-up |  | 155.2974 | 1% | 0.01 x PE |  |  | 155.2974 | $ | FALSE
Performance Testing |  | 155.2974 | 1% | 0.01 x PE |  |  | 155.2974 | $ | FALSE
Total Indirect Costs (TIC) | 4969.5168 |  | - | IC |  |  | 4969.5168 | $
Capital Investment:
Project Contingency |  | 4404.7069 | 15% | E = 0.15 x (DC+IC) | OAQPS (15% of DC & TIC) |  | 4404.7069 | $
Preproduction Cost |  | 675.3884 | 2% | F = 0.02 x (DC+IC+Cont) | OAQPS (2% of DC & TIC & Proj Contingency) |  | 675.3884 | $
Inventory Capital (initial reagent fill) |  | 0 | - | G = [Storage Gal] x [Reagent $/gal] | See parameters below |  | 0 | $ |  | Eqn. 2.44 (Section 4.2, Ch. 2)
Total Capital Investment | 34444.8077 |  | - | TCI = DC + IC + E + F + G |  |  | 34444.8077 | $
Direct Annual Costs
Direct Annual Costs:
Operating Labor |  |  | - |  | Vendor Supplied |  | 0 |  | Req'd | Need input
Supervisory Labor |  | 0 | 15% | 15% of Op. Labor | OAQPS (15% of Op Labor) |  | 0 |  |  | Need input
Maintenance Labor |  | 516.6721 | 1.5% | 0.015 x TCI | OAQPS (1.5% of TCI) |  | 516.6721
Maintenance Materials |  | 516.6721 | - | 100% of Maint. Labor | OAQPS (15% of Maint. Labor) |  | 516.6721
Annual Reagent Cost | 0 | 0 | - | q*Cost*[op hr/yr] | No Reagent needed |  | 0 |  |  | Eqn 2.47 (Section 4.2, Ch. 2)
Annual Electricity Cost |  | 0 | - | See parameters below | See parameters below |  | 0 |  |  | Eqn 2.49 (Section 4.2, Ch. 2)
Catalyst Replacement |  | 0 | - | See parameters below | See parameters below |  | 0
Catalyst Disposal Cost |  | 0 | 10% | 0.100 x Cat Repl | Engineering Estimate |  | 0
Fuel Penalty Costs (specify) |  |  | - |  | Vendor Supplied |  | 0 |  | Req'd | Need input
Other Maintenance Cost (specify) |  |  | - |  | Vendor Supplied |  | 0 |  | Req'd | Need input
Total Direct Annual Costs | 1033.3442 |  | - | DAC |  |  | 1033.3442
Indirect Annual Costs
Indirect Annual Costs:
Overhead |  | 620.0065 | 60% | 0.600 x Op/Super/Maint Labor & Mtls | OAQPS (60% of Op/Super/Maint. Labor & Mtls) |  | 620.0065
Property Tax |  | 516.6721 | 1.5% | 0.0150 x TCI | OAQPS (1%) |  | 516.6721
Insurance |  | 344.4481 | 1% | 0.010 x TCI | OAQPS (1%) |  | 344.4481
General Administrative |  | 688.8962 | 2% | 0.020 x TCI | OAQPS (2%) |  | 688.8962
Total Indirect Annual Costs | 2170.0229 |  | - | DAC |  |  | 2170.0229
Capital Recovery Cost
Equipment Life (years) |  | 20 | - | n | Vendor Supplied |  | 20 | years | FALSE
Interest Rate | 7% | 7% | - | i | 7% per Agrium US Inc, Kenai Nitrogen Operations Facility Air Quality Control Construction Permit AQ0083CPT06 |  | 0.07 | % | FALSE
Capital Recovery Factor | 0.094393 |  | - | CRF = i/(1-(1+i)^-n) | -
Capital Recovery Cost (CRC) | 3251.3462 |  | - |  | OAQPS Eqn 2.54 (Section 4.2, Ch. 2) |  | 3251.3462 |  |  | Eqn 2.54 (Section 4.2, Ch. 2)
Total Annual Costs | 6454.7133 |  | - | TAC = DA + IDAC + CRC | OAQPS Eqn 2.56 (Section 4.2, Ch. 2) |  | 6454.7133 | $/yr |  | Eqn 2.56 (Section 4.2, Ch. 2)
Cost Effectiveness Analysis:
| PM |  |  |  | Reference
Uncontrolled Emissions (tpy) | 0.027512 |  |  |  | PTE Calculations before add on emissions controls
Controlled PM Emissions (tpy) | 0.0027512 |  |  |  | Vendor Emissions Reduction Percentage (90%)
PM Reduction (tpy) | 0.024761 |  |  |  | Calculated below
Total Annual Costs | 6454.7133 |  |  |  | Calculated above
Cost Effectiveness ($/ton/yr) | 260679.7465 |  |  |  | OAQPS Eqn 2.58 (Section 4.2, Ch. 2)
Cost Effectiveness Threshold ($/ton/yr) | [8 empty] | Req'd
Conclusion:
Project costs exceed BACT cost effectiveness threshold and may not be considered cost effective.
Design Parameters:
Enter values in boxes below. Where default value is available, entered value will override default.
Required data is highlighted yellow.
Combustion Unit Sizing | [5 empty] | Default | Final | Final Units | Cond Format | Notes
Reference
Turbine heat capacity: |  | MMBtu/hr |  |  |  |  | 0 | MMBtu/hr | Req'd
Duct burner heat capacity, if applicable: |  | MMBtu/hr |  |  |  |  | 0 | MMBtu/hr | FALSE
NOx Emission Rates
Reference
Turbine uncontrolled NOx concentration: |  | lb NOx/MMBtu |  |  |  | 0 | 0 | lb/MMBtu | FALSE
or |  | lb NOx/MMscf |  |  |  | 0 |  |  | FALSE
or |  | ppmv @ 15% O2 |  |  | Assumption for baseline/uncontrolled emissions | 0 |  |  | FALSE
or (default) |  | ppmv @ 15% O2 |  |  |  | 0 |  |  | FALSE
Duct burner uncontrolled NOx concentration: |  | lb NOx/MMBtu |  |  |  | 0 | 0 | lb/MMBtu | N/A
or |  | lb NOx/MMscf |  |  |  | 0 |  |  | N/A
or |  | ppmv @ 3% O2 |  |  |  | 0 |  |  | N/A
or (default) |  | ppmv @ 3% O2 |  |  |  | 0 |  |  | N/A
Controlled NOx concentration: |  | lb NOx/MMBtu |  |  |  | 0 | 0 | lb/MMBtu | Req'd
or |  | lb NOx/MMscf |  |  |  | 0 |  |  | Req'd
or |  | ppmv @ 15% O2 |  |  | Most stringent limit identified as BACT | 0 |  |  | Req'd
Natural Gas Properties
Reference
HHV [Default: 1050 Btu/scf] |  | Btu/scf |  |  |  | 1050 | 1050 | Btu/scf | FALSE
F-factor (dry) [Default: 8710 dscf/MMBtu] |  | dscf/MMBtu |  |  | EPA 40 CFR Part 60 Appendix A, Method 19, Table 19-2 | 8710 | 8710 | dscf/MMBtu | FALSE
Operational Parameters
Reference
Max annual op hours [Default: 8760 hr/yr] | 500 | hr/yr |  |  |  | 8760 | 500 | hours | FALSE
Annual Electricity Costs: Enter values below. Where default value is available, entered number overrides default.
Reference
Power demand: | 249.8263 | kW |  |  | Calculated below | #DIV/0! | 249.8263 | kW |  | Eqn 2.48 (Section 4.2, Ch. 2)
If power demand is not known, estimate on the basis of the parameters below:
delta P duct [Default: 3 in H2O] |  |  |  |  | OAQPS Eqn 2.48 (Section 4.2, Ch. 2) | 3 | 3 | in H2O | N/A
delta P catalyst (per layer) [Default: 1 in H2O] |  |  |  |  | OAQPS Eqn 2.48 (Section 4.2, Ch. 2) | 1 | 1 | in H2O | N/A
number of layers of catalyst | 1 | [5 empty] | 1 | # layers | N/A
Calculated Power demand: | 249.8263 | kW |  |  | OAQPS Eqn 2.48 (Section 4.2, Ch. 2) |  |  |  | N/A
Electricity Cost [Default: 0.1572 $/kWh] | 0 | $/kWh |  |  |  | 0.1572 | 0 | $/kWh | FALSE
Aqueous Ammonia Costs: Enter values below or parameters to estimate.
Reference
Aqueous ammonia cost: |  | $/gallon |  |  |  |  | 0 | $/gallon | Req'd
Aqueous ammonia storage volume: |  | gallons |  |  | Calculated below |  | 0 | gallons | Req'd
or |  | days' worth |  |  | Engineering Estimate |  | 0 | gallons | Req'd
Aqueous ammonia consumption rate: |  | gal/hr |  |  | Calculated below | 0 | 0 | gal/hr
If aqueous ammonia consumption rate not known, estimate on the basis of the parameters below:
Stored NH3 concentration [Default: 19.4%] |  | wt% |  |  |  | 19.4% | 19.4% | wt% | FALSE | Eqn 2.34 (Section 4.2, Ch. 2)
NH3 solution mass flow rate (msol) |  | lb/hr |  |  | Calculated below | 0 | 0 | lb/hr | FALSE | Eqn 2.32, 2.33 (Section 4.2, Ch. 2)
NH3 solution density [Default: 7.782 lb/gal] |  | lb/gal |  |  | Engineeering Data | 7.7818 | 7.7818 | lb/gal | FALSE
Calculated Aqueous ammonia consumption rate: | 0 | gal/hr |  |  | OAQPS Eqn 2.32-2.34 (Section 4.2, Ch. 2) |  |  |  | FALSE
Catalyst Costs:
Reference
Initial catalyst cost: |  |  |  |  | Vendor Data |  | 0 | $ | Req'd
Catalyst replacement frequency: |  | years |  |  |  |  | 0 | years | Req'd
Interest Rate | 7% | % |  |  | ADEC Default |  | 7% | % | FALSE
Annual Catalyst Replacement Cost | 0 |  |  |  | OAQPS Eqn 2.51 (Section 4.2, Ch. 2) | 0 | 0 | $ | FALSE | Eqn 2.51 (Section 4.2, Ch. 2)
* OAQPS refers to the EPA Air Pollution Control Cost Manual, Sixt Edition and subsequent revisions.
Purchased Equipment: | 2018 | 2025
Purchased Equipment Costs | 9993.05 | 13504.1216 | Annual Index: | CEPCI
|  |  | 2016 | 541.7
|  |  | 2017 | 567.5
|  |  | 2018 | 603.1
|  |  | 2019 | 607.5
|  |  | 2020 | 596.2
|  |  | 2021 | 708.8
|  |  | 2022 | 816
|  |  | 2023 | 797.9
|  |  | 2024 | 799.5
|  |  | 2025 | 815
Note on A130: Note: Default cost from EIA data, Table 5.6.A Nov 2014 - Retail Price of Electricity to Industrial Customers in Alaska: http://www.eia.gov/electricity/monthly/epm_table_grapher.cfm?t=epmt_5_06_a
Note on I130: Note: From EIA data, Table 5.6.A Nov 2014 - Retail Price of Electricity to Industrial Customers in Alaska: http://www.eia.gov/electricity/monthly/epm_table_grapher.cfm?t=epmt_5_06_a

## Diesel Eng-DPF (201hp)
Alaska LNG Project
Diesel Driven Equipment - Communications Tower Generator
Diesel Particulate Filter (DPF) PM Cost Effectiveness Analysis
Cost Quantification:
Cost Category | Project Cost | Default Estimate | Default % Applied | EPA Equation / Estimate Basis | Reference | Default | Final | Final Units | Cond Format | Notes
Direct Capital Costs
Purchased Equipment:
Purchased Equipment Costs | 8102.473 |  | - | A | Vendor Estimate (DCL email Aug. 1, 2018) |  | 8102.473 | $ | FALSE | Need input
Ammonia System |  |  | - | B | Included in A |  | 0 | $ | Req'd | Need input
Instrumentation & Controls |  | 810.2473 | 10% | C = 0.10 x A |  |  | 810.2473 | $
Freight |  | 405.1236 | 5% | D = 0.05 x (A+B) |  |  | 405.1236 | $
Taxes (Enter sales tax rate in "% Applied") |  | 0 | 0% | TaxRate x (A+B+C) | No sales tax in Alaska |  | 0 | $
Total Purchased Equipment Cost (PE) | 9317.8439 |  | - | PE |  |  | 9317.8439 | $
Direct Installation Costs:
Foundation & Supports | 0 | 931.7844 | 10% | 0.10 x PE | Not needed, equipment is skid mounted |  | 0 | $
Erection and Handling |  | 3261.2454 | 35% | 0.35 x PE |  |  | 3261.2454 | $
Electrical |  | 559.0706 | 6% | 0.06 x PE |  |  | 559.0706 | $
Piping |  | 745.4275 | 8% | 0.08 x PE |  |  | 745.4275 | $
Insulation |  | 186.3569 | 2% | 0.02 x PE |  |  | 186.3569 | $
Painting | 0 | 372.7138 | 4% | 0.04 x PE | Not needed, included in equipment purchase price |  | 0 | $
Site Preparation | 567.1731 |  | 7% | 0.07 x (A+B) | engineering judgement |  | 567.1731 | $ | FALSE
Total Direct Installation Cost (DI) | 5319.2735 |  | - | DI |  |  | 5319.2735 | $
Total Direct Capital Costs (DC) | 14637.1174 |  | - | DC = PE + DI |  |  | 14637.1174 | $
Indirect Capital Costs
Indirect Costs:
Engineering & Supervision |  | 1397.6766 | 15% | 0.15 x PE |  |  | 1397.6766 | $ | FALSE
Construction and Field Expenses |  | 931.7844 | 10% | 0.10 x PE |  |  | 931.7844 | $ | FALSE
Contractor Fees |  | 465.8922 | 5% | 0.05 x PE |  |  | 465.8922 | $ | FALSE
Startup-up |  | 93.1784 | 1% | 0.01 x PE |  |  | 93.1784 | $ | FALSE
Performance Testing |  | 93.1784 | 1% | 0.01 x PE |  |  | 93.1784 | $ | FALSE
Total Indirect Costs (TIC) | 2981.7101 |  | - | IC |  |  | 2981.7101 | $
Capital Investment:
Project Contingency |  | 2642.8241 | 15% | E = 0.15 x (DC+IC) | OAQPS (15% of DC & TIC) |  | 2642.8241 | $
Preproduction Cost |  | 405.233 | 2% | F = 0.02 x (DC+IC+Cont) | OAQPS (2% of DC & TIC & Proj Contingency) |  | 405.233 | $
Inventory Capital (initial reagent fill) |  | 0 | - | G = [Storage Gal] x [Reagent $/gal] | See parameters below |  | 0 | $ |  | Eqn. 2.44 (Section 4.2, Ch. 2)
Total Capital Investment | 20666.8846 |  | - | TCI = DC + IC + E + F + G |  |  | 20666.8846 | $
Direct Annual Costs
Direct Annual Costs:
Operating Labor |  |  | - |  | Vendor Supplied |  | 0 |  | Req'd | Need input
Supervisory Labor |  | 0 | 15% | 15% of Op. Labor | OAQPS (15% of Op Labor) |  | 0 |  |  | Need input
Maintenance Labor |  | 310.0033 | 1.5% | 0.015 x TCI | OAQPS (1.5% of TCI) |  | 310.0033
Maintenance Materials |  | 310.0033 | - | 100% of Maint. Labor | OAQPS (15% of Maint. Labor) |  | 310.0033
Annual Reagent Cost | 0 | 0 | - | q*Cost*[op hr/yr] | No Reagent needed |  | 0 |  |  | Eqn 2.47 (Section 4.2, Ch. 2)
Annual Electricity Cost |  | 0 | - | See parameters below | See parameters below |  | 0 |  |  | Eqn 2.49 (Section 4.2, Ch. 2)
Catalyst Replacement |  | 0 | - | See parameters below | See parameters below |  | 0
Catalyst Disposal Cost |  | 0 | 10% | 0.100 x Cat Repl | Engineering Estimate |  | 0
Fuel Penalty Costs (specify) |  |  | - |  | Vendor Supplied |  | 0 |  | Req'd | Need input
Other Maintenance Cost (specify) |  |  | - |  | Vendor Supplied |  | 0 |  | Req'd | Need input
Total Direct Annual Costs | 620.0065 |  | - | DAC |  |  | 620.0065
Indirect Annual Costs
Indirect Annual Costs:
Overhead |  | 372.0039 | 60% | 0.600 x Op/Super/Maint Labor & Mtls | OAQPS (60% of Op/Super/Maint. Labor & Mtls) |  | 372.0039
Property Tax |  | 310.0033 | 1.5% | 0.0150 x TCI | OAQPS (1%) |  | 310.0033
Insurance |  | 206.6688 | 1% | 0.010 x TCI | OAQPS (1%) |  | 206.6688
General Administrative |  | 413.3377 | 2% | 0.020 x TCI | OAQPS (2%) |  | 413.3377
Total Indirect Annual Costs | 1302.0137 |  | - | DAC |  |  | 1302.0137
Capital Recovery Cost
Equipment Life (years) |  | 20 | - | n | Vendor Supplied |  | 20 | years | FALSE
Interest Rate | 7% | 7% | - | i | 7% per Agrium US Inc, Kenai Nitrogen Operations Facility Air Quality Control Construction Permit AQ0083CPT06 |  | 0.07 | % | FALSE
Capital Recovery Factor | 0.094393 |  | - | CRF = i/(1-(1+i)^-n) | -
Capital Recovery Cost (CRC) | 1950.8077 |  | - |  | OAQPS Eqn 2.54 (Section 4.2, Ch. 2) |  | 1950.8077 |  |  | Eqn 2.54 (Section 4.2, Ch. 2)
Total Annual Costs | 3872.828 |  | - | TAC = DA + IDAC + CRC | OAQPS Eqn 2.56 (Section 4.2, Ch. 2) |  | 3872.828 | $/yr |  | Eqn 2.56 (Section 4.2, Ch. 2)
Cost Effectiveness Analysis:
| PM |  |  |  | Reference
Uncontrolled Emissions (tpy) | 0.016507 |  |  |  | PTE Calculations before add on emissions controls
Controlled PM Emissions (tpy) | 0.0016507 |  |  |  | Vendor Emissions Reduction Percentage (90%)
PM Reduction (tpy) | 0.014857 |  |  |  | Calculated below
Total Annual Costs | 3872.828 |  |  |  | Calculated above
Cost Effectiveness ($/ton/yr) | 260679.7465 |  |  |  | OAQPS Eqn 2.58 (Section 4.2, Ch. 2)
Cost Effectiveness Threshold ($/ton/yr) | [8 empty] | Req'd
Conclusion:
Project costs exceed BACT cost effectiveness threshold and may not be considered cost effective.
Design Parameters:
Enter values in boxes below. Where default value is available, entered value will override default.
Required data is highlighted yellow.
Combustion Unit Sizing | [5 empty] | Default | Final | Final Units | Cond Format | Notes
Reference
Turbine heat capacity: |  | MMBtu/hr |  |  |  |  | 0 | MMBtu/hr | Req'd
Duct burner heat capacity, if applicable: |  | MMBtu/hr |  |  |  |  | 0 | MMBtu/hr | FALSE
NOx Emission Rates
Reference
Turbine uncontrolled NOx concentration: |  | lb NOx/MMBtu |  |  |  | 0 | 0 | lb/MMBtu | FALSE
or |  | lb NOx/MMscf |  |  |  | 0 |  |  | FALSE
or |  | ppmv @ 15% O2 |  |  | Assumption for baseline/uncontrolled emissions | 0 |  |  | FALSE
or (default) |  | ppmv @ 15% O2 |  |  |  | 0 |  |  | FALSE
Duct burner uncontrolled NOx concentration: |  | lb NOx/MMBtu |  |  |  | 0 | 0 | lb/MMBtu | N/A
or |  | lb NOx/MMscf |  |  |  | 0 |  |  | N/A
or |  | ppmv @ 3% O2 |  |  |  | 0 |  |  | N/A
or (default) |  | ppmv @ 3% O2 |  |  |  | 0 |  |  | N/A
Controlled NOx concentration: |  | lb NOx/MMBtu |  |  |  | 0 | 0 | lb/MMBtu | Req'd
or |  | lb NOx/MMscf |  |  |  | 0 |  |  | Req'd
or |  | ppmv @ 15% O2 |  |  | Most stringent limit identified as BACT | 0 |  |  | Req'd
Natural Gas Properties
Reference
HHV [Default: 1050 Btu/scf] |  | Btu/scf |  |  |  | 1050 | 1050 | Btu/scf | FALSE
F-factor (dry) [Default: 8710 dscf/MMBtu] |  | dscf/MMBtu |  |  | EPA 40 CFR Part 60 Appendix A, Method 19, Table 19-2 | 8710 | 8710 | dscf/MMBtu | FALSE
Operational Parameters
Reference
Max annual op hours [Default: 8760 hr/yr] | 500 | hr/yr |  |  |  | 8760 | 500 | hours | FALSE
Annual Electricity Costs: Enter values below. Where default value is available, entered number overrides default.
Reference
Power demand: | 149.8957 | kW |  |  | Calculated below | #DIV/0! | 149.8957 | kW |  | Eqn 2.48 (Section 4.2, Ch. 2)
If power demand is not known, estimate on the basis of the parameters below:
delta P duct [Default: 3 in H2O] |  |  |  |  | OAQPS Eqn 2.48 (Section 4.2, Ch. 2) | 3 | 3 | in H2O | N/A
delta P catalyst (per layer) [Default: 1 in H2O] |  |  |  |  | OAQPS Eqn 2.48 (Section 4.2, Ch. 2) | 1 | 1 | in H2O | N/A
number of layers of catalyst | 1 | [5 empty] | 1 | # layers | N/A
Calculated Power demand: | 149.8957 | kW |  |  | OAQPS Eqn 2.48 (Section 4.2, Ch. 2) |  |  |  | N/A
Electricity Cost [Default: 0.1572 $/kWh] | 0 | $/kWh |  |  |  | 0.1572 | 0 | $/kWh | FALSE
Aqueous Ammonia Costs: Enter values below or parameters to estimate.
Reference
Aqueous ammonia cost: |  | $/gallon |  |  |  |  | 0 | $/gallon | Req'd
Aqueous ammonia storage volume: |  | gallons |  |  | Calculated below |  | 0 | gallons | Req'd
or |  | days' worth |  |  | Engineering Estimate |  | 0 | gallons | Req'd
Aqueous ammonia consumption rate: |  | gal/hr |  |  | Calculated below | 0 | 0 | gal/hr
If aqueous ammonia consumption rate not known, estimate on the basis of the parameters below:
Stored NH3 concentration [Default: 19.4%] |  | wt% |  |  |  | 19.4% | 19.4% | wt% | FALSE | Eqn 2.34 (Section 4.2, Ch. 2)
NH3 solution mass flow rate (msol) |  | lb/hr |  |  | Calculated below | 0 | 0 | lb/hr | FALSE | Eqn 2.32, 2.33 (Section 4.2, Ch. 2)
NH3 solution density [Default: 7.782 lb/gal] |  | lb/gal |  |  | Engineeering Data | 7.7818 | 7.7818 | lb/gal | FALSE
Calculated Aqueous ammonia consumption rate: | 0 | gal/hr |  |  | OAQPS Eqn 2.32-2.34 (Section 4.2, Ch. 2) |  |  |  | FALSE
Catalyst Costs:
Reference
Initial catalyst cost: |  |  |  |  | Vendor Data |  | 0 | $ | Req'd
Catalyst replacement frequency: |  | years |  |  |  |  | 0 | years | Req'd
Interest Rate | 7% | % |  |  | ADEC Default |  | 7% | % | FALSE
Annual Catalyst Replacement Cost | 0 |  |  |  | OAQPS Eqn 2.51 (Section 4.2, Ch. 2) | 0 | 0 | $ | FALSE | Eqn 2.51 (Section 4.2, Ch. 2)
* OAQPS refers to the EPA Air Pollution Control Cost Manual, Sixt Edition and subsequent revisions.
Purchased Equipment: | 2018 | 2025
Purchased Equipment Costs | 5995.83 | 8102.473 | Annual Index: | CEPCI
|  |  | 2016 | 541.7
|  |  | 2017 | 567.5
|  |  | 2018 | 603.1
|  |  | 2019 | 607.5
|  |  | 2020 | 596.2
|  |  | 2021 | 708.8
|  |  | 2022 | 816
|  |  | 2023 | 797.9
|  |  | 2024 | 799.5
|  |  | 2025 | 815
Note on A130: Note: Default cost from EIA data, Table 5.6.A Nov 2014 - Retail Price of Electricity to Industrial Customers in Alaska: http://www.eia.gov/electricity/monthly/epm_table_grapher.cfm?t=epmt_5_06_a
Note on I130: Note: From EIA data, Table 5.6.A Nov 2014 - Retail Price of Electricity to Industrial Customers in Alaska: http://www.eia.gov/electricity/monthly/epm_table_grapher.cfm?t=epmt_5_06_a