## 15.210 Large Combined Cycle Tur
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
VA-0332 | CHICKAHOMINY POWER LLC | CHICKAHOMINY POWER LLC | CHARLES CITY | VA | 23030 | USA | IRFAN ALI | (703) 226-0192 | IRFANKALI@BALICO.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer: Alison K. Sinclair Phone: (804)-527-5155 Email: Alison.Sinclair@deq.virginia.gov | 52610-1 | 4911 | 221112 | Not Found | 11/05/2018 &nbsp;ACT | 06/24/2019 &nbsp;ACT | 2019-08-07 | 2021-05-19 | A |  | Natural gas-fired combined cycle power plant, three 1 x1 configuration, 310 MW each, no duct firing, air cooled with two 84 MMBtu/H natural gas-fired auxiliary boilers, three fuel gas heaters, an emergency generator, fire water pump, and circuit breakers. | The proposed project will be a new combined-cycle electrical power generating facility utilizing three power blocks consisting of a combustion turbine with a heat recovery steam generator (HRSG) and a reheat condensing steam turbine generator (three 1 x 1 configuration). The turbine model proposed is a MHPS M501JAC turbine. The project will have a nominal net generating capacity of 1,650 MW. The proposed fuel for the turbines is pipeline-quality natural gas. Emissions from the turbines will be controlled by the use of low carbon fuels and high efficiency design (for GHG), clean fuels and GCPs (for PM, PM10 and PM2.5), SCR and dry low NOx burners (for NOx), and oxidation catalyst (for CO and VOC). Other equipment at the site, including two natural gas-fired auxiliary boilers, three fuel gas heaters, a diesel-fired emergency fire water pump, and a diesel-fired emergency generator, are also proposed and will be subject to emission controls. Natural gas piping components and electrical circuit breakers potentially emit GHG pollutants (expressed as carbon dioxide equivalents, or CO2e) and they will also be covered in the permit. This facility is not proposing duct firing in the HRSGs and is proposing air-cooled turbines that will not require cooling towers. | Three (3) Mitsubishi Hitachi Power Systems combustion turbine generators | 15.21 | natural gas | 35000 | MMCF/YR | One on one configuration: 4,066 MMBtu/H combustion turbine. Emission limits reflect the operation of each of the three turbines. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Controlled by the use of pipeline-quality natural gas with a maximum sulfur content of 0.4 grains per 100 standard cubic feet (scf), on a 12-month rolling average. | 0.0011 | LB/MMBTU | 3 HR AVG | BACT-PSD | NSPS , SIP | N | 0 | N | 20.4 | TONS/YR |  | 0 |  |  | 0 | 0 | N |  | Short term limits apply at all times. Compliance determined by fuel monitoring.
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | General Electric (GE) Combustion Turbines (P005 &amp; P006) | 15.21 | Natural gas | 3459.6 | MMBTU/H | Two identical GE Combustion Turbines 1 and 2; GE model 7HA.02 natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,459.6 MMBtu/hr (HHV) at 100% load and -2Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 570.45 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate additional electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Sulfur Dioxide (SO2) | Other - 40 CFR 60.4415 | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Good combustion practices and pipeline quality natural gas | 0.0017 | LB/MMBTU | SEE NOTES. | BACT-PSD | NSPS | U | 0 | U | 5.75 | LB/H | WITH DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 0.00174 lb/mmbtu and 4.13 lb/h with duct burner, except startup and shutdown. 0.00174 lb/mmbtu and 5.75 lb/h without duct burner. 28.65 tons per rolling 12 month period for all operating modes, including startup.
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | Mitsubishi Hitachi Power Systems (MHPS) Combustion Turbines (P007 &amp; P008) | 15.21 | Natural gas | 3231 | MMBTU/H | Two identical MHPS Combustion Turbines 1 and 2; Mitsubishi Model M501JAC natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,231 MMBtu/hr (HHV) at 100% load and 51Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 306 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Sulfur Dioxide (SO2) | Other - 40 CFR 60.4415 | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Good combustion practices and pipeline quality natural gas | 0.0021 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 7.22 | LB/H | WITH DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 0.0021 lb/mmbtu and 7.22 lb/h with duct burner. 0.0021 lb/mmbtu and 6.92 lb/h without duct burner. 29.57 tons per rolling 12 month period.
KS-0041 | HOLLYFRONTIER EL DORADO REFINERY | HOLLYFRONTIER EL DORADO REFINING LLC | BUTLER | KS | 67042 | USA | RACHEL HENRY | 316-321-8283 | RACHEL.HENRY@HOLLYFRONTIER.COM | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov |  | CSD00080 V1.0 | 2911 | 324110 | 110000446134 | 04/29/2019 &nbsp;ACT | 10/30/2019 &nbsp;ACT | 2020-08-25 | 2023-03-27 | D |  | Petroleum Refinery located in Butler County, KS. Facility processes include distillation, cracking, reforming, isomerization, alkylation, hydrotreating, and coking. Products include a variety of grades of gasoline, fuel oils, and other fuels, along with petroleum coke and commercial grade sulfur. Products stored on-site and transported through pipeline, and by railcar and commercial trucking. By-products include petroleum coke and asphalt. The facility operates a cogeneration system that fires sweet natual gas to produce electric power and steam primarily for consumption within the facility. | This permit is for planned debottle-necking operations. Facility plans to remove operational constraints in order to operate at an increased rate and produce additional product. The following new equipment will be installed: charge heater and boiler for fluid catalytic creacking unit (FCCU), auxiliary air heater for the cogeneration plant, crude heater, crude tank, gasoline storage tank, slop oil tank, gas oil tank, and fugitive components. Modifications will be made to seven process heaters and boilers, four compressor engines, the FCCU, and the cogeneration combustion turbine. There will also be modifications made to four stationary engines subject to NSPS JJJJ (4J). The Tail Gas Treatment Unit 2, will not be physically changed but will be operated continuously (increase in operational hours). Lastly, an increase in maximum-fired duty of 70 MMBtu/hr will be made to units B306 and B307 and have been added to the PSD permit as modified heaters. Facility proposed a single heat input limit for the units B306, B307, and B-NewCrudeHeater (B308) of 381.3 MMBtu/hr. | L3804 | 15.21 | Refinery Fuel Gas | 456.5 | MMBTU/H | Cogeneration Combustion Turbine, equipped with Heat Recovery Steam Generator and steam/water injection. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Proper combustion and operation | 0.0021 | LB/MMBTU | 3-HOUR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0085 | GAS TREATMENT PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | NORTH SLOPE BOROUGH | AK | 99734 | USA | LISA HAAS | 907.947.9353 | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - 907.465.5122 - dave.jones2@alaska.gov | AQ1524CPT01 | 4922 | 486210 | None Found | 01/25/2019 &nbsp;ACT | 08/13/2020 &nbsp;ACT | 2020-08-14 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Gas Treatment Plant (GTP) is part of one integrated liquefied natural gas (LNG) project to bring natural gas from Alaskaâ€™s North Slope to international markets in the form of LNG, as well as for in-state deliveries in the form of natural gas. The GTP will take gas from the Prudhoe Bay Unit and the Point Thomson Unit and treat/process the gas, before it is sent 807 miles through a 42-inch diameter pipeline to a liquefaction facility in Nikiski on Alaskaâ€™s Kenai Peninsula for export in foreign commerce. The emissions units at the stationary source will include cogeneration gas-fired turbines with supplemental firing duct burners for gas compression, simple cycle gas-fired turbines for power generation, gas-fired heaters for building and process heat, as well as flares for control of excess gas. In addition, the GTP will include a diesel-fired black start generator, several diesel-fired firewater pumps and emergency generators, and storage tanks for diesel and gasoline fuels. |  | Six (6) Cogeneration Gas-Fired Turbines (Treated Gas Compressor Turbines) | 15.21 | Natural Gas | 576 | MMBtu/hr | 576 MMBtu/hr includes turbine and supplemental duct burner for waste heat recovery unit for cogeneration. EUs 1-6, Treat Gas Compressor Turbines. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation catalyst and good combustion practices | 0.0022 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Potential VOC emissions of 4.85 tpy per turbine including supplemental firing duct burners for WHRU.
AK-0085 | GAS TREATMENT PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | NORTH SLOPE BOROUGH | AK | 99734 | USA | LISA HAAS | 907.947.9353 | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - 907.465.5122 - dave.jones2@alaska.gov | AQ1524CPT01 | 4922 | 486210 | None Found | 01/25/2019 &nbsp;ACT | 08/13/2020 &nbsp;ACT | 2020-08-14 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Gas Treatment Plant (GTP) is part of one integrated liquefied natural gas (LNG) project to bring natural gas from Alaskaâ€™s North Slope to international markets in the form of LNG, as well as for in-state deliveries in the form of natural gas. The GTP will take gas from the Prudhoe Bay Unit and the Point Thomson Unit and treat/process the gas, before it is sent 807 miles through a 42-inch diameter pipeline to a liquefaction facility in Nikiski on Alaskaâ€™s Kenai Peninsula for export in foreign commerce. The emissions units at the stationary source will include cogeneration gas-fired turbines with supplemental firing duct burners for gas compression, simple cycle gas-fired turbines for power generation, gas-fired heaters for building and process heat, as well as flares for control of excess gas. In addition, the GTP will include a diesel-fired black start generator, several diesel-fired firewater pumps and emergency generators, and storage tanks for diesel and gasoline fuels. |  | Six (6) Cogeneration Gas-Fired Turbines (CO2 Compressor Turbines)) | 15.21 | Natural Gas | 431 | MMBtu/hr | 431 MMBtu/hr includes turbine and supplemental duct burner for waste heat recovery unit for cogeneration. EUs 7-12, CO2 Compressor Turbines. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation catalyst and good combustion control practices | 0.0022 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Potential VOC emissions of 3.64 tpy per turbine including supplemental firing duct burners for WHRU
IL-0130 | JACKSON ENERGY CENTER | JACKSON GENERATION, LLC | WILL | IL | 60421 | USA | JAMES KIEFER | 847-908-2833 | JKEIFER@POWERUSA.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov |  | 17040013 | 4911 | 221112 | Not Found | 04/04/2017 &nbsp;ACT | 12/31/2018 &nbsp;ACT | 2019-07-23 | 2020-04-16 | A |  | The proposed facility is designed to generate baseload power. It will consist of two combined-cycle generating units, each with a combustion turbine and associated heat recovery steam generator (HRSG). The turbines would only burn natural gas. Other units include an auxiliary boiler, fuel heater, emergency engines, natural gas piping and components, circuit breakers and roadways | Additional pollutants: Sulfuric Acid Mist: 48 tons/year; GHG as CO2e: 4,752,085 tons/year | Combined-Cycle Combustion Turbine | 15.21 | Natural Gas | 3864 | mmBtu/hr | Combined-cycle combustion turbines with heat recovery steam generator (HRSG). Turbines will have inlet evaporative cooling systems to cool inlet air during warm weather to increase power output. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0026 | LB/MMBTU | 3-HR BLOCK AVERAGE | BACT-PSD |  | U | 0 | U | 0.0042 | LB/MMBTU | 3-HR BLOCK AVERAGE | 0 |  |  | 0 | 0 | N |  | Emission Limit 1 is applicable to PM. Emission Limit 2 is applicable to PM10/PM2.5. For PM, pounds/hour emission limits for startup/shutdown/commissioning are 11.5 (without duct burner) and 12.3 (with duct burner). For PM10/PM2.5, pounds/hour emission limits for startup/shutdown/commissioning are 12.4 (without duct burner) and 19.8 (with duct burner)
MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2019-02-19 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | FGCTGHRSG (EUCTGHRSG1 &amp; EUCTGHRSG2) | 15.21 | Natural gas | 0 |  | Two (2) combined-cycle natural gas-fired combustion turbine generators, each with a heat recovery steam generator (CTGHRSG). Plant nominal 1,150 MW electricity production. Turbines are each rated at 3,658 MMBTU/H and HRSG duct burners are each rated at 800 MMBTU/H. The HRSGs are not capable of operating independently from the CTGs. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst technology and good combustion practices. | 0.0026 | LB/MMBTU | EACH UNIT; HOURLY EXCEPT S.S. | BACT-PSD | SIP | N | 0 | N | 0.0013 | LB/MMBTU | EACH UNIT W/O DUCT BURNER FIRING; NOT SS | 0 |  |  | 0 | 0 | N |  | The emission limits above are described further below: Emission limit 1 applies to each unit and is 0.0026 LB/MMBTU, hourly except during startup and shutdown. Emission limit 2 applies to each unit without duct burner firing and is 0.0013 LB/MMBTU, hourly except during startup and shutdown.
MI-0442 | THOMAS TOWNSHIP ENERGY, LLC | THOMAS TOWNSHIP ENERGY, LLC | SAGINAW | MI | 48626-9409 | USA | DAN EWAN | 312-582-1504 | DEWAN@INVENERGYLLC.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions, please contact the permit engineer, Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you! | 210-18 | 4911 | 221112 | Not Found | 06/10/2019 &nbsp;ACT | 08/21/2019 &nbsp;ACT | 2019-11-18 | 2021-08-09 | A |  | New power plant | Thomas Township Energy is proposing to install two combustion turbine generators (CTG). Each CTG is connected to a heat recovery steam generator (HRSG), together referred to as a CTGHRSG. To reduce emissions of nitrogen oxides (NOx), the high-efficiency CTGHRSGs will be equipped with dry low-NOx burners and selective catalytic reduction (SCR). To reduce the emissions of carbon monoxide (CO) and volatile organic compounds (VOCs), each CTGHRSG will be equipped with an oxidation catalyst. | FGCTGHRSG | 15.21 | Natural gas | 625 | MW | Two (2) combined-cycle natural gas-fired combustion turbine generators (CTGs), each with a heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG). Each CTGHRSG has a combined nominal 625 MW electricity production (ISO) and a maximum combined heat input rating of 4,200 MMBTU/hr (HHV). Each HRSG is equipped with a natural gas-fired duct burner with a maximum rating of 560 MMBTU/hr (HHV) (ISO) to provide heat for additional steam production. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | The use of clean fuel (natural gas), with a fuel sulfur limit of 1 grain per 100 standard cubic feet of natural gas. | 0.003 | LB/MMBTU | HOURLY; EACH UNIT | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Flue gas desulfurization (FGD) and fuel desulfurization were not considered as feasible control alternative for this project.
IL-0133 | LINCOLN LAND ENERGY CENTER | LINCOLN LAND ENERGY CENTER (A/K/A EMBERCLEAR) | SANGAMON | IL | 62558 | USA | JIM PALUMBO | 888-582-4460 X 55 | JPALUMBO@EMBERCLEAR.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov |  | 18040008 | 4911 | 221112 | Not Found | 09/30/2021 &nbsp;ACT | 07/29/2022 &nbsp;ACT | 2022-08-26 | 2022-12-06 | A | www2.illinois.gov/epa/public-notices/boa-notices/pages/archive.aspx | The proposed facility is designed to generate baseload power. It will consist of two combined-cycle generating units, with each a Siemens combustion turbine (3,647 mmBtu/hr) and a heat recovery steam generator (HRSG) with duct burners (35 mmBtu/hr); fired by natural gas only. Other units at the facility include an auxiliary boiler, engines, piping and piping components, circuit breakers and roadways. | Additional facility-wide pollutants, in tons/year: PM10/PM 2.5: 131.7 and 131.6 (respectively); sulfuric acid mist (SAM): 17.2; greenhouse gasses (GHG): 3,586,918 | Combined-Cycle Combustion Turbines | 15.21 | Natural Gas | 3647 | mmBtu/hour | Combined-cycle comustion turbines and heat recovery steam generators (HRSG) with a 35 mmBtu/hr duct burner. Turbine inlets would have evaporative cooling systems to cool the inlet air during warm weather to increase power output. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0032 | POUNDS/MMBTU | WITH DUCT BURNER; ROLLING 3-OPERATING HR | BACT-PSD |  | U | 0 | U | 0.0031 | POUNDS/MMBTU | W/O DUCT BURNER; ROLLING 3-OPERATING HR | 0 |  |  | 0 | 0 | N |  | Compliance is determined by performance testing.
MI-0442 | THOMAS TOWNSHIP ENERGY, LLC | THOMAS TOWNSHIP ENERGY, LLC | SAGINAW | MI | 48626-9409 | USA | DAN EWAN | 312-582-1504 | DEWAN@INVENERGYLLC.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions, please contact the permit engineer, Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you! | 210-18 | 4911 | 221112 | Not Found | 06/10/2019 &nbsp;ACT | 08/21/2019 &nbsp;ACT | 2019-11-18 | 2021-08-09 | A |  | New power plant | Thomas Township Energy is proposing to install two combustion turbine generators (CTG). Each CTG is connected to a heat recovery steam generator (HRSG), together referred to as a CTGHRSG. To reduce emissions of nitrogen oxides (NOx), the high-efficiency CTGHRSGs will be equipped with dry low-NOx burners and selective catalytic reduction (SCR). To reduce the emissions of carbon monoxide (CO) and volatile organic compounds (VOCs), each CTGHRSG will be equipped with an oxidation catalyst. | FGCTGHRSG | 15.21 | Natural gas | 625 | MW | Two (2) combined-cycle natural gas-fired combustion turbine generators (CTGs), each with a heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG). Each CTGHRSG has a combined nominal 625 MW electricity production (ISO) and a maximum combined heat input rating of 4,200 MMBTU/hr (HHV). Each HRSG is equipped with a natural gas-fired duct burner with a maximum rating of 560 MMBTU/hr (HHV) (ISO) to provide heat for additional steam production. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Low sulfur fuel and good combustion practices. | 0.0034 | LB/MMBTU | HOURLY; EACH UNIT | BACT-PSD |  | N | 0 | U | 123 | T/YR | 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | Emission limit 2 is 123 tons/year based upon a 12-month rolling time period as determined at the end of each calendar month. Limit applies to the entire flexible group. The lowest cost (for a fabric filter) was greater than $87,000/ton of total PM controlled. Therefore, add-on controls were not considered economically feasible for particulate control.
KS-0041 | HOLLYFRONTIER EL DORADO REFINERY | HOLLYFRONTIER EL DORADO REFINING LLC | BUTLER | KS | 67042 | USA | RACHEL HENRY | 316-321-8283 | RACHEL.HENRY@HOLLYFRONTIER.COM | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov |  | CSD00080 V1.0 | 2911 | 324110 | 110000446134 | 04/29/2019 &nbsp;ACT | 10/30/2019 &nbsp;ACT | 2020-08-25 | 2023-03-27 | D |  | Petroleum Refinery located in Butler County, KS. Facility processes include distillation, cracking, reforming, isomerization, alkylation, hydrotreating, and coking. Products include a variety of grades of gasoline, fuel oils, and other fuels, along with petroleum coke and commercial grade sulfur. Products stored on-site and transported through pipeline, and by railcar and commercial trucking. By-products include petroleum coke and asphalt. The facility operates a cogeneration system that fires sweet natual gas to produce electric power and steam primarily for consumption within the facility. | This permit is for planned debottle-necking operations. Facility plans to remove operational constraints in order to operate at an increased rate and produce additional product. The following new equipment will be installed: charge heater and boiler for fluid catalytic creacking unit (FCCU), auxiliary air heater for the cogeneration plant, crude heater, crude tank, gasoline storage tank, slop oil tank, gas oil tank, and fugitive components. Modifications will be made to seven process heaters and boilers, four compressor engines, the FCCU, and the cogeneration combustion turbine. There will also be modifications made to four stationary engines subject to NSPS JJJJ (4J). The Tail Gas Treatment Unit 2, will not be physically changed but will be operated continuously (increase in operational hours). Lastly, an increase in maximum-fired duty of 70 MMBtu/hr will be made to units B306 and B307 and have been added to the PSD permit as modified heaters. Facility proposed a single heat input limit for the units B306, B307, and B-NewCrudeHeater (B308) of 381.3 MMBtu/hr. | L3804 | 15.21 | Refinery Fuel Gas | 456.5 | MMBTU/H | Cogeneration Combustion Turbine, equipped with Heat Recovery Steam Generator and steam/water injection. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Low Sulfur Fuel Gas | 0.0034 | LB/MMBTU | 3-HOUR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0129 | CPV THREE RIVERS ENERGY CENTER | CPV THREE RIVERS, LLC | GRUNDY | IL | 60450 | USA | MIKE BRUNO | 781-817-8972 | MBRUNO@CPV.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Illinois EPA, Bureau of Air Permit Section | 16060032 | 4911 | 221112 | Not Found | 06/10/2018 &nbsp;ACT | 07/30/2018 &nbsp;ACT | 2019-01-02 | 2019-02-19 | A |  | The proposed facility is designed to generate baseload power. It will consist of two combined-cycle generating units, each with a combustion turbine and associated heat recovery steam generator (HRSG). The turbines would burn natural gas and ultra-low sulfur diesel (ULSD) as a backup fuel. Other units include an auxiliary boiler, fuel heater, engines, natural gas piping and components, circuit breakers and roadways. |  | Combined Cycle Combustion Turbines | 15.21 | Natural Gas | 3474 | mmBtu/hr | Throughput of ultra-low sulfur diesel (ULSD) is 3798 mmBtu/hr. Combined cycle combustion turbines w/ heat recovery steam generator (HRSG). Turbine inlets will have inlet evaporative cooling systems to cool inlet air during warm weather to increase power output. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0037 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  | U | 0 | U | 0.0167 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | 0 |  |  | 0 | 0 | N |  | Emission Limit 1 is for natural gas. Emission limit 2 is for ULSD. Permit limits are as follows. Averaging time for all permit limits are 3-hour block average. For natural gas: Without duct burner: 8.6 lb/hr With duct burner: 14.4 lb/hr For ULSD: 34.3 lb/hr
*VA-0335 | PANDA STONEWALL LLC | PANDA STONEWALL LLC | LOUDOUN | VA | 20175 | USA | MARK KKAN | (703) 779-4101 |  | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Mr. Ali Khalilzadeh by phone at (703) 583-3839 or by e-mail: Alireza.Khalilzadeh@deq.virginia.gov | 73826-6 | 4911 | 221112 | 110041353 | &nbsp; | 12/18/2020 &nbsp;ACT | 2021-03-29 | 2022-09-12 | U |  | Panda Stonewall, LLC (Panda) is a combined-cycle electric power generating facility in Loudoun County with a nominal generating capacity increased from 778 to 802 megawatts (MW) â€œgrossâ€ at ISO (International Organization for Standardization) conditions (which is at 15 C or 59 F, 60% relative humidity, and 1 atmosphere or 14.7 psia pressure). The facility is a fossil fuel-fired steam electric plant of more than 250 million British thermal units (MMBtu) heat input capacity, and is located in an ozone nonattainment area. | The original permit dated April 30, 2013 (amended 5/31/2013, 6/11/2014 & 7/15/2014) allowed for either of two alternative combined cycle combustion turbine manufacturers â€“ General Electric or Siemens. The permittee selected the Siemens SGT6-5000F5 combustion turbines. The turbine manufacturer, Siemens, has increased the maximum shaft torque limit between the combustion turbine and the generator that allows for increased gross power output of the SGT6-5000F5 units. The gross power output rating on each combustion turbine generator has increased from 232 megawatt (MW) to 242 MW. This change in output equates to an increase in its maximum fuel heat input rate from 2,276 million British thermal units (MMBtu/hr) to 2,450 MMBtu/hr. This change does not alter the air pollutant concentration (ppm) in the flue gas or the emission factor (in lb/MMBtu) that represent Lowest Achievable Emission Rate (LAER) for NOx and VOC, and Best Available Control Technology (BACT) for CO, CO2, PM-10 and other pollutants, which are state and federally enforceable due to conditions established in the April 30, 2013 permit. The increase in the maximum fuel firing rate results in corresponding increase in lb/hr emission limits (except for PM-10/PM-2.5). This permit increases the two duct burner hours of operation limitations from 1,400 hours/year (each) to 8,760 hours/year (each). This permit also includes installation of ancillary equipment with lower rated capacities than initially permitted and requested updates to the permit for the changes with corresponding lower emissions. | Combustion Turbines, Two (2) and HRSG Duct Burners | 15.21 | Natural Gas | 2.55 | MMBTU/H | 2x1 natural gas-only configuration: Two Siemens SGT6-5000F5 CTs at 2554 MMBtu/hr and two 430 MMBtu/hr duct burners | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and use of low-sulfur fuels | 0.0037 | LB/MMBTU | AT FULL LOAD W & W/O DB | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AL-0328 | PLANT BARRY | ALABAMA POWER COMPANY | MOBILE | AL | 36512 | USA | TYLER PHILLIPS |  | TYLER.PHILLIPS@ADEM.ALABAMA.GOV | 4 | AL001 | ALABAMA DEPT OF ENVIRONMENTAL MGMT | MR. DALE HURST | (334) 271-7882 | ADH@ADEM.STATE.AL.US |  | 503-1001 | 4911 | 221112 | 110000741270 | 05/01/2020 &nbsp;ACT | 11/09/2020 &nbsp;ACT | 2021-09-30 | 2022-03-04 | B |  |  |  | Two 744 MW Combined Cycle Units | 15.21 | Natural Gas | 744 | MW |  | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.004 | LB/MMBTU | 3 HOUR AVG | BACT-PSD | SIP , OPERATING PERMIT , NSPS | U | 0 | N | 21.51 | LB/HR | 3 HOUR AVG | 0 |  |  | 0 | 0 | N
AL-0328 | PLANT BARRY | ALABAMA POWER COMPANY | MOBILE | AL | 36512 | USA | TYLER PHILLIPS |  | TYLER.PHILLIPS@ADEM.ALABAMA.GOV | 4 | AL001 | ALABAMA DEPT OF ENVIRONMENTAL MGMT | MR. DALE HURST | (334) 271-7882 | ADH@ADEM.STATE.AL.US |  | 503-1001 | 4911 | 221112 | 110000741270 | 05/01/2020 &nbsp;ACT | 11/09/2020 &nbsp;ACT | 2021-09-30 | 2022-03-04 | B |  |  |  | Two 744 MW Combined Cycle Units | 15.21 | Natural Gas | 744 | MW |  | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | N |  | 0.004 | LB/MMBTU | 3 HOUR AVG | BACT-PSD | NSPS , SIP , OPERATING PERMIT | U | 0 | N | 21.51 | LB/HR | 3 HOUR AVG | 0 |  |  | 0 | 0 | N
MI-0442 | THOMAS TOWNSHIP ENERGY, LLC | THOMAS TOWNSHIP ENERGY, LLC | SAGINAW | MI | 48626-9409 | USA | DAN EWAN | 312-582-1504 | DEWAN@INVENERGYLLC.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions, please contact the permit engineer, Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you! | 210-18 | 4911 | 221112 | Not Found | 06/10/2019 &nbsp;ACT | 08/21/2019 &nbsp;ACT | 2019-11-18 | 2021-08-09 | A |  | New power plant | Thomas Township Energy is proposing to install two combustion turbine generators (CTG). Each CTG is connected to a heat recovery steam generator (HRSG), together referred to as a CTGHRSG. To reduce emissions of nitrogen oxides (NOx), the high-efficiency CTGHRSGs will be equipped with dry low-NOx burners and selective catalytic reduction (SCR). To reduce the emissions of carbon monoxide (CO) and volatile organic compounds (VOCs), each CTGHRSG will be equipped with an oxidation catalyst. | FGCTGHRSG | 15.21 | Natural gas | 625 | MW | Two (2) combined-cycle natural gas-fired combustion turbine generators (CTGs), each with a heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG). Each CTGHRSG has a combined nominal 625 MW electricity production (ISO) and a maximum combined heat input rating of 4,200 MMBTU/hr (HHV). Each HRSG is equipped with a natural gas-fired duct burner with a maximum rating of 560 MMBTU/hr (HHV) (ISO) to provide heat for additional steam production. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst and good combustion practices. | 0.004 | LB/MMBTU | HOURLY; NOT STARTUP/SHUTDOWN;EACH UNIT | BACT-PSD |  | N | 70 | U | 377 | T/YR | 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | Emission Limit 1 = 0.004 lb/MMBTU, applies to each unit and is hourly except during startup/shutdown. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the combustion process ends at flame-off. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in special condition (SC) III.2 of the permit. Thermal oxidation, EMxGT, NSCR are not technically feasible control options for VOCs.
IL-0133 | LINCOLN LAND ENERGY CENTER | LINCOLN LAND ENERGY CENTER (A/K/A EMBERCLEAR) | SANGAMON | IL | 62558 | USA | JIM PALUMBO | 888-582-4460 X 55 | JPALUMBO@EMBERCLEAR.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov |  | 18040008 | 4911 | 221112 | Not Found | 09/30/2021 &nbsp;ACT | 07/29/2022 &nbsp;ACT | 2022-08-26 | 2022-12-06 | A | www2.illinois.gov/epa/public-notices/boa-notices/pages/archive.aspx | The proposed facility is designed to generate baseload power. It will consist of two combined-cycle generating units, with each a Siemens combustion turbine (3,647 mmBtu/hr) and a heat recovery steam generator (HRSG) with duct burners (35 mmBtu/hr); fired by natural gas only. Other units at the facility include an auxiliary boiler, engines, piping and piping components, circuit breakers and roadways. | Additional facility-wide pollutants, in tons/year: PM10/PM 2.5: 131.7 and 131.6 (respectively); sulfuric acid mist (SAM): 17.2; greenhouse gasses (GHG): 3,586,918 | Combined-Cycle Combustion Turbines | 15.21 | Natural Gas | 3647 | mmBtu/hour | Combined-cycle comustion turbines and heat recovery steam generators (HRSG) with a 35 mmBtu/hr duct burner. Turbine inlets would have evaporative cooling systems to cool the inlet air during warm weather to increase power output. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.0041 | POUNDS/MMBTU | ROLLING 3-OPERATING HOUR | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Limit for PM10 also includes PM2.5, i.e., PM10/PM2.5. Compliance is demonstrated by performance testing.
*PA-0319 | RENAISSANCE ENERGY CENTER | APV RENAISSANCE PARTNERS | GREENE | PA | 15320 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | SHELBI MEYNARD | (717)772-3968 | smeynard@pa.gov |  | 30-00235A | 4911 | 221112 | Not Found | 03/17/2017 &nbsp;ACT | 08/27/2018 &nbsp;ACT | 2019-03-26 | 2019-10-11 | U |  | This Plan Approval is to allow the construction and temporary operation of a natural gas-fired combined cycle power plant to be located in Monongahela Township, Greene County. with Two (2) Siemens, SGT6-8000H (or equivalent), natural gas-fired combustion turbines 3,580 MMBtu/hr heat input rating (LHV) each (controlled with low NOx burners), including natural gas-fired duct burners, 914.1 MMBtu/hr heat input rating each; controlled by Ultra-low NOx combustors, SCR, and oxidation catalysts; 1,127 MW total net generating capacity. One (1) natural gas-fired auxiliary boiler, 90 MMBtu/hr heat input rating. One (1) Cummins model #CFP15E-F20 (or equivalent), diesel-fired fire pump engine, 411 bhp rating; including One (1) diesel fuel storage tank, 2,175 gallons One (1) Caterpillar 3516 (or equivalent), diesel-fired emergency generator engine rated at 2000 kW. Miscellaneous components in natural gas service, and circuit breakers; controlled by leak detection and repair (â€œLDARâ€). One (1) aqueous ammonia (19%) storage vessel rated at 19,000 gallons (or as determined during final design). |  | COMBUSTION TURBINE UNIT w/o DUCT BURNERS UNIT | 15.21 | Natural Gas | 2665.9 | MMBtu/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0043 | LB/MMBTU | HR | BACT-PSD |  | U | 0 | U | 121.72 | TPY |  | 0 |  |  | 0 | 0 | N
*PA-0319 | RENAISSANCE ENERGY CENTER | APV RENAISSANCE PARTNERS | GREENE | PA | 15320 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | SHELBI MEYNARD | (717)772-3968 | smeynard@pa.gov |  | 30-00235A | 4911 | 221112 | Not Found | 03/17/2017 &nbsp;ACT | 08/27/2018 &nbsp;ACT | 2019-03-26 | 2019-10-11 | U |  | This Plan Approval is to allow the construction and temporary operation of a natural gas-fired combined cycle power plant to be located in Monongahela Township, Greene County. with Two (2) Siemens, SGT6-8000H (or equivalent), natural gas-fired combustion turbines 3,580 MMBtu/hr heat input rating (LHV) each (controlled with low NOx burners), including natural gas-fired duct burners, 914.1 MMBtu/hr heat input rating each; controlled by Ultra-low NOx combustors, SCR, and oxidation catalysts; 1,127 MW total net generating capacity. One (1) natural gas-fired auxiliary boiler, 90 MMBtu/hr heat input rating. One (1) Cummins model #CFP15E-F20 (or equivalent), diesel-fired fire pump engine, 411 bhp rating; including One (1) diesel fuel storage tank, 2,175 gallons One (1) Caterpillar 3516 (or equivalent), diesel-fired emergency generator engine rated at 2000 kW. Miscellaneous components in natural gas service, and circuit breakers; controlled by leak detection and repair (â€œLDARâ€). One (1) aqueous ammonia (19%) storage vessel rated at 19,000 gallons (or as determined during final design). |  | COMBUSTION TURBINE UNIT w/o DUCT BURNERS UNIT | 15.21 | Natural Gas | 2665.9 | MMBtu/hr |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0043 | LB/MMBTU | HR | BACT-PSD |  | U | 0 | U | 121.72 | TPY |  | 0 |  |  | 0 | 0 | N
*PA-0319 | RENAISSANCE ENERGY CENTER | APV RENAISSANCE PARTNERS | GREENE | PA | 15320 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | SHELBI MEYNARD | (717)772-3968 | smeynard@pa.gov |  | 30-00235A | 4911 | 221112 | Not Found | 03/17/2017 &nbsp;ACT | 08/27/2018 &nbsp;ACT | 2019-03-26 | 2019-10-11 | U |  | This Plan Approval is to allow the construction and temporary operation of a natural gas-fired combined cycle power plant to be located in Monongahela Township, Greene County. with Two (2) Siemens, SGT6-8000H (or equivalent), natural gas-fired combustion turbines 3,580 MMBtu/hr heat input rating (LHV) each (controlled with low NOx burners), including natural gas-fired duct burners, 914.1 MMBtu/hr heat input rating each; controlled by Ultra-low NOx combustors, SCR, and oxidation catalysts; 1,127 MW total net generating capacity. One (1) natural gas-fired auxiliary boiler, 90 MMBtu/hr heat input rating. One (1) Cummins model #CFP15E-F20 (or equivalent), diesel-fired fire pump engine, 411 bhp rating; including One (1) diesel fuel storage tank, 2,175 gallons One (1) Caterpillar 3516 (or equivalent), diesel-fired emergency generator engine rated at 2000 kW. Miscellaneous components in natural gas service, and circuit breakers; controlled by leak detection and repair (â€œLDARâ€). One (1) aqueous ammonia (19%) storage vessel rated at 19,000 gallons (or as determined during final design). |  | COMBUSTION TURBINE UNIT w/o DUCT BURNERS UNIT | 15.21 | Natural Gas | 2665.9 | MMBtu/hr |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0043 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 121.72 |  |  | 0 |  |  | 0 | 0 | N
MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2019-02-19 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | FGCTGHRSG (EUCTGHRSG1 &amp; EUCTGHRSG2) | 15.21 | Natural gas | 0 |  | Two (2) combined-cycle natural gas-fired combustion turbine generators, each with a heat recovery steam generator (CTGHRSG). Plant nominal 1,150 MW electricity production. Turbines are each rated at 3,658 MMBTU/H and HRSG duct burners are each rated at 800 MMBTU/H. The HRSGs are not capable of operating independently from the CTGs. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst technology and good combustion practices. | 0.0045 | LB/MMBTU | EACH UNIT; 24-H ROLL AVG; NOT S.S. | BACT-PSD |  | N | 85 | N | 17.59 | LB/H | EACH UNIT; 24-H ROLL AVG; NOT S.S. | 0 |  |  | 0 | 0 | N |  | There are 3 CO emission limits in the permit; as follows: Emission limit 1 = 0.0045 LB/MMBTU based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown (S.S.). The limit applies to each unit. Emission limit 2 = 17.59 LB/H based on a 24-hour rolling average as determined each operating hour except during startup and shutdown (S.S.). The limit applies to each unit. Emission limit 3 = 791.5 LB/H each operating hour during startup or shutdown. Oxidation catalyst reduction is expected to reduce CO by 85-90%. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in Special Condition III.2 in the permit.
CA-1251 | PALMDALE ENERGY PROJECT | PALMDALE ENERGY, LLC | LOS ANGELES | CA | 93551 | USA | TOM CAMERON |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov | Staff Contact: Lisa Beckham beckham.lisa@epa.gov (415) 972-3811 | SE 17-01 | 4911 | 221122 | Not Found | 08/16/2017 &nbsp;ACT | 04/25/2018 &nbsp;ACT | 2018-10-25 | 2020-01-31 | A | https://www.epa.gov/caa-permitting/palmdale-energy-project-prevention-significant-deterioration-psd-permit | 645 MW (nominal) Natural Gas-fired Combined Cycle Power Plant, 2 x 1 configuration, auxiliary boiler for faster startup | See also docket: https://www.regulations.gov/docket?D=EPA-R09-OAR-2017-0473. Permit decision was appealed to EPA's Environmental Appeals Board. Board denied review on October 23, 2018. Information available through www.epa.gov/eab and https://yosemite.epa.gov/oa/EAB_Web_Docket.nsf/f22b4b245fab46c6852570e6004df1bd/ad735c0b822500258525829d004217eb!OpenDocument. 1/31/20 -- SYS MGR -- Link to permit is <https://www.regulations.gov/document?D=EPA-R09-OAR-2017-0473-0028> | Combustion Turbines (GEN1 and GEN2) | 15.21 | Natural Gas | 2217 | MMBTU/H | Each combustion turbine rated at 214 MW, with a maximum heat input rate of 2,217 MMBtu/H (HHV, at ISO conditions); natural gas-fired Siemens SGT6-5000F; each vents to dedicated Heat Recovery Steam Generator and a shared 276 MW Steam Turbine Generator; 160-ft stack height; 22-ft stack diameter | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | P | Clean fuel and good combustion practices | 0.0048 | LB/MMBTU | TEST AVERAGE | BACT-PSD |  | U | 0 | U | 11.8 | LB/H | TEST AVERAGE | 0 |  |  | 0 | 0 | N |  | The sulfur content of the gas shall not exceed 0.20 grains per 100 dry standard cubic feet (dscf), based on a 12-month rolling average, and shall not exceed 1.0 grains per 100 dscf at any time.
CA-1251 | PALMDALE ENERGY PROJECT | PALMDALE ENERGY, LLC | LOS ANGELES | CA | 93551 | USA | TOM CAMERON |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov | Staff Contact: Lisa Beckham beckham.lisa@epa.gov (415) 972-3811 | SE 17-01 | 4911 | 221122 | Not Found | 08/16/2017 &nbsp;ACT | 04/25/2018 &nbsp;ACT | 2018-10-25 | 2020-01-31 | A | https://www.epa.gov/caa-permitting/palmdale-energy-project-prevention-significant-deterioration-psd-permit | 645 MW (nominal) Natural Gas-fired Combined Cycle Power Plant, 2 x 1 configuration, auxiliary boiler for faster startup | See also docket: https://www.regulations.gov/docket?D=EPA-R09-OAR-2017-0473. Permit decision was appealed to EPA's Environmental Appeals Board. Board denied review on October 23, 2018. Information available through www.epa.gov/eab and https://yosemite.epa.gov/oa/EAB_Web_Docket.nsf/f22b4b245fab46c6852570e6004df1bd/ad735c0b822500258525829d004217eb!OpenDocument. 1/31/20 -- SYS MGR -- Link to permit is <https://www.regulations.gov/document?D=EPA-R09-OAR-2017-0473-0028> | Combustion Turbines (GEN1 and GEN2) | 15.21 | Natural Gas | 2217 | MMBTU/H | Each combustion turbine rated at 214 MW, with a maximum heat input rate of 2,217 MMBtu/H (HHV, at ISO conditions); natural gas-fired Siemens SGT6-5000F; each vents to dedicated Heat Recovery Steam Generator and a shared 276 MW Steam Turbine Generator; 160-ft stack height; 22-ft stack diameter | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | Clean fuel and good combustion practices | 0.0048 | LB/MMBTU | TEST AVERAGE | BACT-PSD |  | N | 0 | U | 11.8 | LB/H | TEST AVERAGE | 0 |  |  | 0 | 0 | N |  | The sulfur content of the gas shall not exceed 0.20 grains per 100 dry standard cubic feet (dscf), based on a 12-month rolling average, and shall not exceed 1.0 grains per 100 dscf at any time.
CA-1251 | PALMDALE ENERGY PROJECT | PALMDALE ENERGY, LLC | LOS ANGELES | CA | 93551 | USA | TOM CAMERON |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov | Staff Contact: Lisa Beckham beckham.lisa@epa.gov (415) 972-3811 | SE 17-01 | 4911 | 221122 | Not Found | 08/16/2017 &nbsp;ACT | 04/25/2018 &nbsp;ACT | 2018-10-25 | 2020-01-31 | A | https://www.epa.gov/caa-permitting/palmdale-energy-project-prevention-significant-deterioration-psd-permit | 645 MW (nominal) Natural Gas-fired Combined Cycle Power Plant, 2 x 1 configuration, auxiliary boiler for faster startup | See also docket: https://www.regulations.gov/docket?D=EPA-R09-OAR-2017-0473. Permit decision was appealed to EPA's Environmental Appeals Board. Board denied review on October 23, 2018. Information available through www.epa.gov/eab and https://yosemite.epa.gov/oa/EAB_Web_Docket.nsf/f22b4b245fab46c6852570e6004df1bd/ad735c0b822500258525829d004217eb!OpenDocument. 1/31/20 -- SYS MGR -- Link to permit is <https://www.regulations.gov/document?D=EPA-R09-OAR-2017-0473-0028> | Combustion Turbines (GEN1 and GEN2) | 15.21 | Natural Gas | 2217 | MMBTU/H | Each combustion turbine rated at 214 MW, with a maximum heat input rate of 2,217 MMBtu/H (HHV, at ISO conditions); natural gas-fired Siemens SGT6-5000F; each vents to dedicated Heat Recovery Steam Generator and a shared 276 MW Steam Turbine Generator; 160-ft stack height; 22-ft stack diameter | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - Methods 201A and 202 | (Particulate Matter (PM)) | PM | P | Clean fuel and good combustion practices | 0.0048 | LB/MMBTU | TEST AVERAGE | BACT-PSD |  | N | 0 | U | 11.8 | LB/H | TEST AVERAGE | 0 |  |  | 0 | 0 | N |  | The sulfur content of the gas shall not exceed 0.20 grains per 100 dry standard cubic feet (dscf), based on a 12-month rolling average, and shall not exceed 1.0 grains per 100 dscf at any time.
TX-0939 | ORANGE COUNTY ADVANCED POWER STATION | ENTERGY TEXAS, INC. | ORANGE | TX |  | USA | JASON WILLIS | 281-297-1937 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Huy Pham, (512) 239-1358, Huy.Pham@tceq.texas.gov | 166032 PSDTX1598 GHGPSDTX210 | 4911 | 221122 | Not found | 06/06/2022 &nbsp;ACT | 03/13/2023 &nbsp;ACT | 2022-06-06 | 2023-05-23 | A |  | Entergy Texas, Inc. proposes construction of a power plant consisting of two natural gas-fired combined cycle turbines with a maximum total nominal output of 1,215 MW. The turbines can also be fired with up to 30% volume hydrogen co-firing (blended fuel). Emergency engines, a cooling tower, storage tanks, and maintenance activities support operation of the turbines. |  | Combined Cycle Turbines | 15.21 | NATURAL GAS | 1215 | MW | 2 Mitsubishi M501JAC combustion turbines 1,215 MW (in a 2x1 configuration) output and 6,762 Btu/kW-hr (with a 9% degradation) gross heat rate. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices | 0.005 | LB/MMBTU |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0939 | ORANGE COUNTY ADVANCED POWER STATION | ENTERGY TEXAS, INC. | ORANGE | TX |  | USA | JASON WILLIS | 281-297-1937 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Huy Pham, (512) 239-1358, Huy.Pham@tceq.texas.gov | 166032 PSDTX1598 GHGPSDTX210 | 4911 | 221122 | Not found | 06/06/2022 &nbsp;ACT | 03/13/2023 &nbsp;ACT | 2022-06-06 | 2023-05-23 | A |  | Entergy Texas, Inc. proposes construction of a power plant consisting of two natural gas-fired combined cycle turbines with a maximum total nominal output of 1,215 MW. The turbines can also be fired with up to 30% volume hydrogen co-firing (blended fuel). Emergency engines, a cooling tower, storage tanks, and maintenance activities support operation of the turbines. |  | Combined Cycle Turbines | 15.21 | NATURAL GAS | 1215 | MW | 2 Mitsubishi M501JAC combustion turbines 1,215 MW (in a 2x1 configuration) output and 6,762 Btu/kW-hr (with a 9% degradation) gross heat rate. | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices | 0.005 | LB/MMBTU |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*TN-0164 | TVA - JOHNSONVILLE COGENERATION | TENNESSEE VALLEY AUTHORITY | HUMPHREYS | TN | 37134 | USA | JACK BYARS | (423) 751-2666 | JGBYARS@TVA.GOV | 4 | TN001 | TENN.DEPT. OF ENVIRONMENT & CONSERVATION, DIV OF AIR POLLUTION CONTROL | LACEY HARDIN | (615) 532-0545 | Lacey.Hardin@tn.gov |  | 972969 | 4911 | 221112 | 110070502905 | 09/26/2017 &nbsp;ACT | 02/01/2018 &nbsp;ACT | 2019-03-21 | 2019-03-21 | D |  | Combustion turbines and combined cycle plant | Permit 972969 adds startup and shutdown limits to the requirements established in PSD permit 970816F. | Dual-fuel CT and HRSG with duct burner | 15.21 | Natural Gas | 1020 | MMBtu/hr | Rated input capacity is 1020 MMBtu/hr (CT) and 319 MMBtu/hr (duct burner) when burning natural gas and 1084 MMBtu/hr when burning #2 oil. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion design & practice | 0.005 | LB/MMBTU | WHEN BURNING NATURAL GAS | BACT-PSD |  | U | 0 | U | 0.015 | LB/MMBTU | WHEN BURNING #2 OIL | 0 |  |  | 0 | 0 | N
TX-0939 | ORANGE COUNTY ADVANCED POWER STATION | ENTERGY TEXAS, INC. | ORANGE | TX |  | USA | JASON WILLIS | 281-297-1937 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Huy Pham, (512) 239-1358, Huy.Pham@tceq.texas.gov | 166032 PSDTX1598 GHGPSDTX210 | 4911 | 221122 | Not found | 06/06/2022 &nbsp;ACT | 03/13/2023 &nbsp;ACT | 2022-06-06 | 2023-05-23 | A |  | Entergy Texas, Inc. proposes construction of a power plant consisting of two natural gas-fired combined cycle turbines with a maximum total nominal output of 1,215 MW. The turbines can also be fired with up to 30% volume hydrogen co-firing (blended fuel). Emergency engines, a cooling tower, storage tanks, and maintenance activities support operation of the turbines. |  | Combined Cycle Turbines | 15.21 | NATURAL GAS | 1215 | MW | 2 Mitsubishi M501JAC combustion turbines 1,215 MW (in a 2x1 configuration) output and 6,762 Btu/kW-hr (with a 9% degradation) gross heat rate. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices | 0.005 | LB/MMBTU |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | Mitsubishi Hitachi Power Systems (MHPS) Combustion Turbines (P007 &amp; P008) | 15.21 | Natural gas | 3231 | MMBTU/H | Two identical MHPS Combustion Turbines 1 and 2; Mitsubishi Model M501JAC natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,231 MMBtu/hr (HHV) at 100% load and 51Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 306 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices and pipeline quality natural gas | 0.005 | LB/MMBTU | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 17.7 | LB/H | WITH DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 0.005 lb/mmbtu and 17.7 lb/h with duct burner. 0.00444 lb/mmbtu and 14.10 lb/h without duct burner. 77.5 tons per rolling 12 month period for all operating modes.
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | Mitsubishi Hitachi Power Systems (MHPS) Combustion Turbines (P007 &amp; P008) | 15.21 | Natural gas | 3231 | MMBTU/H | Two identical MHPS Combustion Turbines 1 and 2; Mitsubishi Model M501JAC natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,231 MMBtu/hr (HHV) at 100% load and 51Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 306 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - Methods 201A and 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices and pipeline quality natural gas | 0.005 | LB/MMBTU | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 17.7 | LB/H | WITH DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 0.005 lb/mmbtu and 17.7 lb/h with duct burner. 0.00444 lb/mmbtu and 14.10 lb/h without duct burner. 77.5 tons per rolling 12 month period for all operating modes.
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | Mitsubishi Hitachi Power Systems (MHPS) Combustion Turbines (P007 &amp; P008) | 15.21 | Natural gas | 3231 | MMBTU/H | Two identical MHPS Combustion Turbines 1 and 2; Mitsubishi Model M501JAC natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,231 MMBtu/hr (HHV) at 100% load and 51Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 306 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices and pipeline quality natural gas | 0.005 | LB/MMBTU | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 17.7 | LB/H | WITH DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 0.005 lb/mmbtu and 17.7 lb/h with duct burner. 0.00444 lb/mmbtu and 14.10 lb/h without duct burner. 77.5 tons per rolling 12 month period for all operating modes.
VA-0332 | CHICKAHOMINY POWER LLC | CHICKAHOMINY POWER LLC | CHARLES CITY | VA | 23030 | USA | IRFAN ALI | (703) 226-0192 | IRFANKALI@BALICO.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer: Alison K. Sinclair Phone: (804)-527-5155 Email: Alison.Sinclair@deq.virginia.gov | 52610-1 | 4911 | 221112 | Not Found | 11/05/2018 &nbsp;ACT | 06/24/2019 &nbsp;ACT | 2019-08-07 | 2021-05-19 | A |  | Natural gas-fired combined cycle power plant, three 1 x1 configuration, 310 MW each, no duct firing, air cooled with two 84 MMBtu/H natural gas-fired auxiliary boilers, three fuel gas heaters, an emergency generator, fire water pump, and circuit breakers. | The proposed project will be a new combined-cycle electrical power generating facility utilizing three power blocks consisting of a combustion turbine with a heat recovery steam generator (HRSG) and a reheat condensing steam turbine generator (three 1 x 1 configuration). The turbine model proposed is a MHPS M501JAC turbine. The project will have a nominal net generating capacity of 1,650 MW. The proposed fuel for the turbines is pipeline-quality natural gas. Emissions from the turbines will be controlled by the use of low carbon fuels and high efficiency design (for GHG), clean fuels and GCPs (for PM, PM10 and PM2.5), SCR and dry low NOx burners (for NOx), and oxidation catalyst (for CO and VOC). Other equipment at the site, including two natural gas-fired auxiliary boilers, three fuel gas heaters, a diesel-fired emergency fire water pump, and a diesel-fired emergency generator, are also proposed and will be subject to emission controls. Natural gas piping components and electrical circuit breakers potentially emit GHG pollutants (expressed as carbon dioxide equivalents, or CO2e) and they will also be covered in the permit. This facility is not proposing duct firing in the HRSGs and is proposing air-cooled turbines that will not require cooling towers. | Three (3) Mitsubishi Hitachi Power Systems combustion turbine generators | 15.21 | natural gas | 35000 | MMCF/YR | One on one configuration: 4,066 MMBtu/H combustion turbine. Emission limits reflect the operation of each of the three turbines. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Controlled by good combustion practices (e.g. controlled fuel/air mixing, adequate temperature, and gas residence time) and the use of pipeline-quality natural gas with a maximum sulfur content of 0.4 grains per 100 scf, on a 12-month rolling average. | 0.0052 | LB/MMBTU | AVG. OF 3 TEST RUNS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | General Electric (GE) Combustion Turbines (P005 &amp; P006) | 15.21 | Natural gas | 3459.6 | MMBTU/H | Two identical GE Combustion Turbines 1 and 2; GE model 7HA.02 natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,459.6 MMBtu/hr (HHV) at 100% load and -2Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 570.45 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate additional electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices and pipeline quality natural gas | 0.0052 | LB/MMBTU | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 18.4 | LB/H | WITH DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 0.00522 lb/mmbtu and 18.4 lb/h with duct burner. 0.00735 lb/mmbtu and 12.0 lb/h without duct burner. 80.2 tons per rolling 12 month period for all operating modes.
VA-0332 | CHICKAHOMINY POWER LLC | CHICKAHOMINY POWER LLC | CHARLES CITY | VA | 23030 | USA | IRFAN ALI | (703) 226-0192 | IRFANKALI@BALICO.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer: Alison K. Sinclair Phone: (804)-527-5155 Email: Alison.Sinclair@deq.virginia.gov | 52610-1 | 4911 | 221112 | Not Found | 11/05/2018 &nbsp;ACT | 06/24/2019 &nbsp;ACT | 2019-08-07 | 2021-05-19 | A |  | Natural gas-fired combined cycle power plant, three 1 x1 configuration, 310 MW each, no duct firing, air cooled with two 84 MMBtu/H natural gas-fired auxiliary boilers, three fuel gas heaters, an emergency generator, fire water pump, and circuit breakers. | The proposed project will be a new combined-cycle electrical power generating facility utilizing three power blocks consisting of a combustion turbine with a heat recovery steam generator (HRSG) and a reheat condensing steam turbine generator (three 1 x 1 configuration). The turbine model proposed is a MHPS M501JAC turbine. The project will have a nominal net generating capacity of 1,650 MW. The proposed fuel for the turbines is pipeline-quality natural gas. Emissions from the turbines will be controlled by the use of low carbon fuels and high efficiency design (for GHG), clean fuels and GCPs (for PM, PM10 and PM2.5), SCR and dry low NOx burners (for NOx), and oxidation catalyst (for CO and VOC). Other equipment at the site, including two natural gas-fired auxiliary boilers, three fuel gas heaters, a diesel-fired emergency fire water pump, and a diesel-fired emergency generator, are also proposed and will be subject to emission controls. Natural gas piping components and electrical circuit breakers potentially emit GHG pollutants (expressed as carbon dioxide equivalents, or CO2e) and they will also be covered in the permit. This facility is not proposing duct firing in the HRSGs and is proposing air-cooled turbines that will not require cooling towers. | Three (3) Mitsubishi Hitachi Power Systems combustion turbine generators | 15.21 | natural gas | 35000 | MMCF/YR | One on one configuration: 4,066 MMBtu/H combustion turbine. Emission limits reflect the operation of each of the three turbines. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Controlled by good combustion practices (e.g. controlled fuel/air mixing, adequate temperature, and gas residence time) and the use of pipeline-quality natural gas with a maximum sulfur content of 0.4 grains per 100 scf, on a 12-month rolling average. | 0.0052 | LB/MMBTU | AVG OF 3 TEST RUNS | BACT-PSD | NSPS , SIP | N | 0 | N | 12.3 | LB/H | AVG OF 3 TEST RUNS | 0 |  |  | 0 | 0 | N |  | Short term limits apply at all times. Additional limit: 53.9 tons/year
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | General Electric (GE) Combustion Turbines (P005 &amp; P006) | 15.21 | Natural gas | 3459.6 | MMBTU/H | Two identical GE Combustion Turbines 1 and 2; GE model 7HA.02 natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,459.6 MMBtu/hr (HHV) at 100% load and -2Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 570.45 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate additional electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - Methods 201A and 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices and pipeline quality natural gas | 0.0052 | LB/MMBTU | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 18.4 | LB/H | WITH DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 0.00522 lb/mmbtu and 18.4 lb/h with duct burner. 0.00735 lb/mmbtu and 12.0 lb/h without duct burner. 80.2 tons per rolling 12 month period for all operating modes.
VA-0332 | CHICKAHOMINY POWER LLC | CHICKAHOMINY POWER LLC | CHARLES CITY | VA | 23030 | USA | IRFAN ALI | (703) 226-0192 | IRFANKALI@BALICO.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer: Alison K. Sinclair Phone: (804)-527-5155 Email: Alison.Sinclair@deq.virginia.gov | 52610-1 | 4911 | 221112 | Not Found | 11/05/2018 &nbsp;ACT | 06/24/2019 &nbsp;ACT | 2019-08-07 | 2021-05-19 | A |  | Natural gas-fired combined cycle power plant, three 1 x1 configuration, 310 MW each, no duct firing, air cooled with two 84 MMBtu/H natural gas-fired auxiliary boilers, three fuel gas heaters, an emergency generator, fire water pump, and circuit breakers. | The proposed project will be a new combined-cycle electrical power generating facility utilizing three power blocks consisting of a combustion turbine with a heat recovery steam generator (HRSG) and a reheat condensing steam turbine generator (three 1 x 1 configuration). The turbine model proposed is a MHPS M501JAC turbine. The project will have a nominal net generating capacity of 1,650 MW. The proposed fuel for the turbines is pipeline-quality natural gas. Emissions from the turbines will be controlled by the use of low carbon fuels and high efficiency design (for GHG), clean fuels and GCPs (for PM, PM10 and PM2.5), SCR and dry low NOx burners (for NOx), and oxidation catalyst (for CO and VOC). Other equipment at the site, including two natural gas-fired auxiliary boilers, three fuel gas heaters, a diesel-fired emergency fire water pump, and a diesel-fired emergency generator, are also proposed and will be subject to emission controls. Natural gas piping components and electrical circuit breakers potentially emit GHG pollutants (expressed as carbon dioxide equivalents, or CO2e) and they will also be covered in the permit. This facility is not proposing duct firing in the HRSGs and is proposing air-cooled turbines that will not require cooling towers. | Three (3) Mitsubishi Hitachi Power Systems combustion turbine generators | 15.21 | natural gas | 35000 | MMCF/YR | One on one configuration: 4,066 MMBtu/H combustion turbine. Emission limits reflect the operation of each of the three turbines. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Controlled by good combustion practices (e.g. controlled fuel/air mixing, adequate temperature, and gas residence time) and the use of pipeline-quality natural gas with a maximum sulfur content of 0.4 grains per 100 scf, on a 12-month rolling average. | 0.0052 | LB/MMBTU | AVG OF 3 TEST RUNS | BACT-PSD | NSPS , SIP | N | 0 | N | 12.3 | LB/H | AVG OF 3 TEST RUNS | 0 |  |  | 0 | 0 | N |  | Short term limits apply at all times. Additional limit: 53.9 tons/year
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | General Electric (GE) Combustion Turbines (P005 &amp; P006) | 15.21 | Natural gas | 3459.6 | MMBTU/H | Two identical GE Combustion Turbines 1 and 2; GE model 7HA.02 natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,459.6 MMBtu/hr (HHV) at 100% load and -2Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 570.45 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate additional electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices and pipeline quality natural gas | 0.0052 | LB/MMBTU | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 18.4 | LB/H | WITH DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 0.00522 lb/mmbtu and 18.4 lb/h with duct burner. 0.00735 lb/mmbtu and 12.0 lb/h without duct burner. 80.2 tons per rolling 12 month period for all operating modes.
MI-0442 | THOMAS TOWNSHIP ENERGY, LLC | THOMAS TOWNSHIP ENERGY, LLC | SAGINAW | MI | 48626-9409 | USA | DAN EWAN | 312-582-1504 | DEWAN@INVENERGYLLC.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions, please contact the permit engineer, Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you! | 210-18 | 4911 | 221112 | Not Found | 06/10/2019 &nbsp;ACT | 08/21/2019 &nbsp;ACT | 2019-11-18 | 2021-08-09 | A |  | New power plant | Thomas Township Energy is proposing to install two combustion turbine generators (CTG). Each CTG is connected to a heat recovery steam generator (HRSG), together referred to as a CTGHRSG. To reduce emissions of nitrogen oxides (NOx), the high-efficiency CTGHRSGs will be equipped with dry low-NOx burners and selective catalytic reduction (SCR). To reduce the emissions of carbon monoxide (CO) and volatile organic compounds (VOCs), each CTGHRSG will be equipped with an oxidation catalyst. | FGCTGHRSG | 15.21 | Natural gas | 625 | MW | Two (2) combined-cycle natural gas-fired combustion turbine generators (CTGs), each with a heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG). Each CTGHRSG has a combined nominal 625 MW electricity production (ISO) and a maximum combined heat input rating of 4,200 MMBTU/hr (HHV). Each HRSG is equipped with a natural gas-fired duct burner with a maximum rating of 560 MMBTU/hr (HHV) (ISO) to provide heat for additional steam production. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Low sulfur fuel and good combustion practices. | 0.006 | LB/MMBTU | HOURLY; EACH UNIT | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The lowest cost (for a fabric filter) was greater than $87,000/ton of total PM controlled. Therefore, add-on controls were not considered economically feasible for particulate control.
MI-0442 | THOMAS TOWNSHIP ENERGY, LLC | THOMAS TOWNSHIP ENERGY, LLC | SAGINAW | MI | 48626-9409 | USA | DAN EWAN | 312-582-1504 | DEWAN@INVENERGYLLC.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions, please contact the permit engineer, Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you! | 210-18 | 4911 | 221112 | Not Found | 06/10/2019 &nbsp;ACT | 08/21/2019 &nbsp;ACT | 2019-11-18 | 2021-08-09 | A |  | New power plant | Thomas Township Energy is proposing to install two combustion turbine generators (CTG). Each CTG is connected to a heat recovery steam generator (HRSG), together referred to as a CTGHRSG. To reduce emissions of nitrogen oxides (NOx), the high-efficiency CTGHRSGs will be equipped with dry low-NOx burners and selective catalytic reduction (SCR). To reduce the emissions of carbon monoxide (CO) and volatile organic compounds (VOCs), each CTGHRSG will be equipped with an oxidation catalyst. | FGCTGHRSG | 15.21 | Natural gas | 625 | MW | Two (2) combined-cycle natural gas-fired combustion turbine generators (CTGs), each with a heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG). Each CTGHRSG has a combined nominal 625 MW electricity production (ISO) and a maximum combined heat input rating of 4,200 MMBTU/hr (HHV). Each HRSG is equipped with a natural gas-fired duct burner with a maximum rating of 560 MMBTU/hr (HHV) (ISO) to provide heat for additional steam production. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Low sulfur fuel and good combustion practices. | 0.006 | LB/MMBTU | HOURLY; EACH UNIT | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The lowest cost (for a fabric filter) was greater than $87,000/ton of total PM controlled. Therefore, add-on controls were not considered economically feasible for particulate control.
*WV-0033 | MAIDSVILLE | MOUNTAIN STATE CLEAN ENERGY, LLC | MONONGALIA | WV | 26541 | USA | BRIAN HOYT | 304-559-0930 X2203 | BHOYT@LONGVIEWPOWER.NET | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Mr. Ed Andrews edward.s.andrews@wv.gov | R14-0038 | 4911 | 221112 | 054-061-00134 | 05/05/2020 &nbsp;ACT | 01/05/2022 &nbsp;ACT | 2022-04-01 | 2022-06-28 | U | https://dep.wv.gov/daq/permitting/Pages/NSR-Permit-Applications.aspx | This project consist of constructing two combined cycle combustion turbine with duct burners, two fuel gas heaters, two emergency engines (emergency generator and fire water pump), and cooling tower. The configuration of these combustion turbines with heat recovery steam generators will be a 2X1. This facility will be co-located next to existing EGU (Longview Power LLC). The CCCTs with duct burners and fuel gas heaters will operate only on natural gas. Both emergency engines will be diesel fired units. | A bi-direction steam line between the Mountain State Clean Energy and Longview Power will be use to provide startup steam in lieu of a auxiliary boiler. No limits on operating hours or fuel use for the duct burners. Applicant proposed two different model combustion turbine (GE 7HA.03 and MHPS M501JAC). Gross Generation for the facility is 1275 MWh. | Combustion Turbine &amp; Duct Burner (CT-01/HRSG1 &amp; CT-02/HRSG2) | 15.21 | Pipeline Natural Gas | 1275 | mw | CT - 3,875 MMBtu/hr DB - 586 MMBtu/hr Gross Generation - 1275 MW | Particulate matter, total (TPM) | Other - 201/201a filterable, 202 condensable | (Particulate Matter (PM)) | PM | P | Clean Fuels and Good Combustion Practice | 0.006 | LB/MMBTU | AVG OF 3 4-HR TEST RUNS | BACT-PSD | N/A | N | 0 | U | 25.32 | LB/HR | 12-HR AVERAGE | 0 |  |  | 0 | 0 | N |  | Concentration and Mass limits apply at all times excluding startup and shutdown events. These limits apply with or without duct firing. Same information above also applies to PM10 and PM2.5 including emission limits.
*WV-0033 | MAIDSVILLE | MOUNTAIN STATE CLEAN ENERGY, LLC | MONONGALIA | WV | 26541 | USA | BRIAN HOYT | 304-559-0930 X2203 | BHOYT@LONGVIEWPOWER.NET | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Mr. Ed Andrews edward.s.andrews@wv.gov | R14-0038 | 4911 | 221112 | 054-061-00134 | 05/05/2020 &nbsp;ACT | 01/05/2022 &nbsp;ACT | 2022-04-01 | 2022-06-28 | U | https://dep.wv.gov/daq/permitting/Pages/NSR-Permit-Applications.aspx | This project consist of constructing two combined cycle combustion turbine with duct burners, two fuel gas heaters, two emergency engines (emergency generator and fire water pump), and cooling tower. The configuration of these combustion turbines with heat recovery steam generators will be a 2X1. This facility will be co-located next to existing EGU (Longview Power LLC). The CCCTs with duct burners and fuel gas heaters will operate only on natural gas. Both emergency engines will be diesel fired units. | A bi-direction steam line between the Mountain State Clean Energy and Longview Power will be use to provide startup steam in lieu of a auxiliary boiler. No limits on operating hours or fuel use for the duct burners. Applicant proposed two different model combustion turbine (GE 7HA.03 and MHPS M501JAC). Gross Generation for the facility is 1275 MWh. | Combustion Turbine &amp; Duct Burner (CT-01/HRSG1 &amp; CT-02/HRSG2) | 15.21 | Pipeline Natural Gas | 1275 | mw | CT - 3,875 MMBtu/hr DB - 586 MMBtu/hr Gross Generation - 1275 MW | Particulate matter, total (TPM) | Other - 201/201a filterable, 202 condensable | (Particulate Matter (PM)) | PM | P | Good Combustion Practice and Clean Fuel | 0.006 | LB/MMBTU | AVG OF 3 4-HR TEST RUNS | BACT-PSD | N/A | N | 0 | U | 23.36 | LB/HR | 12-HR AVERAGE | 0 |  |  | 0 | 0 | N |  | Concentration and Mass limits apply at all times excluding startup and shutdown events. These limits apply with or without duct firing. Same information above also applies to PM10 and PM2.5 including emission limits.
AK-0085 | GAS TREATMENT PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | NORTH SLOPE BOROUGH | AK | 99734 | USA | LISA HAAS | 907.947.9353 | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - 907.465.5122 - dave.jones2@alaska.gov | AQ1524CPT01 | 4922 | 486210 | None Found | 01/25/2019 &nbsp;ACT | 08/13/2020 &nbsp;ACT | 2020-08-14 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Gas Treatment Plant (GTP) is part of one integrated liquefied natural gas (LNG) project to bring natural gas from Alaskaâ€™s North Slope to international markets in the form of LNG, as well as for in-state deliveries in the form of natural gas. The GTP will take gas from the Prudhoe Bay Unit and the Point Thomson Unit and treat/process the gas, before it is sent 807 miles through a 42-inch diameter pipeline to a liquefaction facility in Nikiski on Alaskaâ€™s Kenai Peninsula for export in foreign commerce. The emissions units at the stationary source will include cogeneration gas-fired turbines with supplemental firing duct burners for gas compression, simple cycle gas-fired turbines for power generation, gas-fired heaters for building and process heat, as well as flares for control of excess gas. In addition, the GTP will include a diesel-fired black start generator, several diesel-fired firewater pumps and emergency generators, and storage tanks for diesel and gasoline fuels. |  | Six (6) Cogeneration Gas-Fired Turbines (Treated Gas Compressor Turbines) | 15.21 | Natural Gas | 576 | MMBtu/hr | 576 MMBtu/hr includes turbine and supplemental duct burner for waste heat recovery unit for cogeneration. EUs 1-6, Treat Gas Compressor Turbines. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and clean burning fuel (NG) | 0.0063 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Potential particulate matter emissions of 15.92 tpy per turbine including supplemental firing duct burners for WHRU.
AK-0085 | GAS TREATMENT PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | NORTH SLOPE BOROUGH | AK | 99734 | USA | LISA HAAS | 907.947.9353 | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - 907.465.5122 - dave.jones2@alaska.gov | AQ1524CPT01 | 4922 | 486210 | None Found | 01/25/2019 &nbsp;ACT | 08/13/2020 &nbsp;ACT | 2020-08-14 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Gas Treatment Plant (GTP) is part of one integrated liquefied natural gas (LNG) project to bring natural gas from Alaskaâ€™s North Slope to international markets in the form of LNG, as well as for in-state deliveries in the form of natural gas. The GTP will take gas from the Prudhoe Bay Unit and the Point Thomson Unit and treat/process the gas, before it is sent 807 miles through a 42-inch diameter pipeline to a liquefaction facility in Nikiski on Alaskaâ€™s Kenai Peninsula for export in foreign commerce. The emissions units at the stationary source will include cogeneration gas-fired turbines with supplemental firing duct burners for gas compression, simple cycle gas-fired turbines for power generation, gas-fired heaters for building and process heat, as well as flares for control of excess gas. In addition, the GTP will include a diesel-fired black start generator, several diesel-fired firewater pumps and emergency generators, and storage tanks for diesel and gasoline fuels. |  | Six (6) Cogeneration Gas-Fired Turbines (CO2 Compressor Turbines)) | 15.21 | Natural Gas | 431 | MMBtu/hr | 431 MMBtu/hr includes turbine and supplemental duct burner for waste heat recovery unit for cogeneration. EUs 7-12, CO2 Compressor Turbines. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion Practices and burning clean fuels (NG) | 0.0063 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Potential particulate matter emissions of 11.99 tpy per turbine including supplemental firing duct burners for WHRU.
AK-0085 | GAS TREATMENT PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | NORTH SLOPE BOROUGH | AK | 99734 | USA | LISA HAAS | 907.947.9353 | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - 907.465.5122 - dave.jones2@alaska.gov | AQ1524CPT01 | 4922 | 486210 | None Found | 01/25/2019 &nbsp;ACT | 08/13/2020 &nbsp;ACT | 2020-08-14 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Gas Treatment Plant (GTP) is part of one integrated liquefied natural gas (LNG) project to bring natural gas from Alaskaâ€™s North Slope to international markets in the form of LNG, as well as for in-state deliveries in the form of natural gas. The GTP will take gas from the Prudhoe Bay Unit and the Point Thomson Unit and treat/process the gas, before it is sent 807 miles through a 42-inch diameter pipeline to a liquefaction facility in Nikiski on Alaskaâ€™s Kenai Peninsula for export in foreign commerce. The emissions units at the stationary source will include cogeneration gas-fired turbines with supplemental firing duct burners for gas compression, simple cycle gas-fired turbines for power generation, gas-fired heaters for building and process heat, as well as flares for control of excess gas. In addition, the GTP will include a diesel-fired black start generator, several diesel-fired firewater pumps and emergency generators, and storage tanks for diesel and gasoline fuels. |  | Six (6) Cogeneration Gas-Fired Turbines (Treated Gas Compressor Turbines) | 15.21 | Natural Gas | 576 | MMBtu/hr | 576 MMBtu/hr includes turbine and supplemental duct burner for waste heat recovery unit for cogeneration. EUs 1-6, Treat Gas Compressor Turbines. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and burning clean fuel (NG) | 0.0063 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Potential particulate matter emissions of 15.92 tpy per turbine including supplemental firing duct burners for WHRU.
AK-0085 | GAS TREATMENT PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | NORTH SLOPE BOROUGH | AK | 99734 | USA | LISA HAAS | 907.947.9353 | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - 907.465.5122 - dave.jones2@alaska.gov | AQ1524CPT01 | 4922 | 486210 | None Found | 01/25/2019 &nbsp;ACT | 08/13/2020 &nbsp;ACT | 2020-08-14 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Gas Treatment Plant (GTP) is part of one integrated liquefied natural gas (LNG) project to bring natural gas from Alaskaâ€™s North Slope to international markets in the form of LNG, as well as for in-state deliveries in the form of natural gas. The GTP will take gas from the Prudhoe Bay Unit and the Point Thomson Unit and treat/process the gas, before it is sent 807 miles through a 42-inch diameter pipeline to a liquefaction facility in Nikiski on Alaskaâ€™s Kenai Peninsula for export in foreign commerce. The emissions units at the stationary source will include cogeneration gas-fired turbines with supplemental firing duct burners for gas compression, simple cycle gas-fired turbines for power generation, gas-fired heaters for building and process heat, as well as flares for control of excess gas. In addition, the GTP will include a diesel-fired black start generator, several diesel-fired firewater pumps and emergency generators, and storage tanks for diesel and gasoline fuels. |  | Six (6) Cogeneration Gas-Fired Turbines (CO2 Compressor Turbines)) | 15.21 | Natural Gas | 431 | MMBtu/hr | 431 MMBtu/hr includes turbine and supplemental duct burner for waste heat recovery unit for cogeneration. EUs 7-12, CO2 Compressor Turbines. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion Practices and burning clean fuels (NG) | 0.0063 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Potential particulate matter emissions of 11.99 tpy per turbine including supplemental firing duct burners for WHRU.
AK-0085 | GAS TREATMENT PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | NORTH SLOPE BOROUGH | AK | 99734 | USA | LISA HAAS | 907.947.9353 | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - 907.465.5122 - dave.jones2@alaska.gov | AQ1524CPT01 | 4922 | 486210 | None Found | 01/25/2019 &nbsp;ACT | 08/13/2020 &nbsp;ACT | 2020-08-14 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Gas Treatment Plant (GTP) is part of one integrated liquefied natural gas (LNG) project to bring natural gas from Alaskaâ€™s North Slope to international markets in the form of LNG, as well as for in-state deliveries in the form of natural gas. The GTP will take gas from the Prudhoe Bay Unit and the Point Thomson Unit and treat/process the gas, before it is sent 807 miles through a 42-inch diameter pipeline to a liquefaction facility in Nikiski on Alaskaâ€™s Kenai Peninsula for export in foreign commerce. The emissions units at the stationary source will include cogeneration gas-fired turbines with supplemental firing duct burners for gas compression, simple cycle gas-fired turbines for power generation, gas-fired heaters for building and process heat, as well as flares for control of excess gas. In addition, the GTP will include a diesel-fired black start generator, several diesel-fired firewater pumps and emergency generators, and storage tanks for diesel and gasoline fuels. |  | Six (6) Cogeneration Gas-Fired Turbines (Treated Gas Compressor Turbines) | 15.21 | Natural Gas | 576 | MMBtu/hr | 576 MMBtu/hr includes turbine and supplemental duct burner for waste heat recovery unit for cogeneration. EUs 1-6, Treat Gas Compressor Turbines. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion Practices and burning clean fuels (NG) | 0.0063 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Potential particulate matter emissions of 15.92 tpy per turbine including supplemental firing duct burners for WHRU.
AK-0085 | GAS TREATMENT PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | NORTH SLOPE BOROUGH | AK | 99734 | USA | LISA HAAS | 907.947.9353 | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - 907.465.5122 - dave.jones2@alaska.gov | AQ1524CPT01 | 4922 | 486210 | None Found | 01/25/2019 &nbsp;ACT | 08/13/2020 &nbsp;ACT | 2020-08-14 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Gas Treatment Plant (GTP) is part of one integrated liquefied natural gas (LNG) project to bring natural gas from Alaskaâ€™s North Slope to international markets in the form of LNG, as well as for in-state deliveries in the form of natural gas. The GTP will take gas from the Prudhoe Bay Unit and the Point Thomson Unit and treat/process the gas, before it is sent 807 miles through a 42-inch diameter pipeline to a liquefaction facility in Nikiski on Alaskaâ€™s Kenai Peninsula for export in foreign commerce. The emissions units at the stationary source will include cogeneration gas-fired turbines with supplemental firing duct burners for gas compression, simple cycle gas-fired turbines for power generation, gas-fired heaters for building and process heat, as well as flares for control of excess gas. In addition, the GTP will include a diesel-fired black start generator, several diesel-fired firewater pumps and emergency generators, and storage tanks for diesel and gasoline fuels. |  | Six (6) Cogeneration Gas-Fired Turbines (CO2 Compressor Turbines)) | 15.21 | Natural Gas | 431 | MMBtu/hr | 431 MMBtu/hr includes turbine and supplemental duct burner for waste heat recovery unit for cogeneration. EUs 7-12, CO2 Compressor Turbines. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion Practices and burning clean fuels (NG) | 0.0063 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Potential particulate matter emissions of 11.99 tpy per turbine including supplemental firing duct burners for WHRU.
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | Siemens Combusion Turbine - Option 2 - Normal Operation | 15.21 | Natural Gas | 35000 | MMCF/YR | Option 2: Two on one configuration: 3,116 MMBtu/hr combustion turbine with 991 MMBtu/hr duct-fired HRSG. Emission limits reflect the operation of one turbine with or without duct firing. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices and the use of pipeline quality natural gas with a maximum sulfur content of 0.4 gr/100 scf on a 12 mo rolling av. | 0.0065 | LB/MMBTU | AV OF 3 TEST RUNS/WITHOUT DUCT BURNING | BACT-PSD | SIP | N | 0 | N | 0.0065 | LB/MMBTU | AV OF 3 TEST RUNS/WITH DUCT BURNING | 0 |  |  | 0 | 0 | N |  | Additional limits: 13.7 lb/hr without duct burning; 24.2 lb/hr with duct burning. These short term limits apply at all times.
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | Siemens Combusion Turbine - Option 2 - Normal Operation | 15.21 | Natural Gas | 35000 | MMCF/YR | Option 2: Two on one configuration: 3,116 MMBtu/hr combustion turbine with 991 MMBtu/hr duct-fired HRSG. Emission limits reflect the operation of one turbine with or without duct firing. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices and the use of pipeline quality natural gas with a maximum sulfur content of 0.4 gr/100 scf on a 12-month rolling average. | 0.0065 | LB/MMBTU | AV OF 3 TEST RUNS/WITHOUT DUCT BURNING | BACT-PSD | SIP | N | 0 | N | 0.0065 | LB/MMBTU | AV OF 3 TEST RUNS/WITH DUCT BURNING | 0 |  |  | 0 | 0 | N |  | Additional limits: 13.7 lb/hr without duct burning; 24.2 lb/hr with duct burning. These short term limits apply at all times.
KS-0041 | HOLLYFRONTIER EL DORADO REFINERY | HOLLYFRONTIER EL DORADO REFINING LLC | BUTLER | KS | 67042 | USA | RACHEL HENRY | 316-321-8283 | RACHEL.HENRY@HOLLYFRONTIER.COM | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov |  | CSD00080 V1.0 | 2911 | 324110 | 110000446134 | 04/29/2019 &nbsp;ACT | 10/30/2019 &nbsp;ACT | 2020-08-25 | 2023-03-27 | D |  | Petroleum Refinery located in Butler County, KS. Facility processes include distillation, cracking, reforming, isomerization, alkylation, hydrotreating, and coking. Products include a variety of grades of gasoline, fuel oils, and other fuels, along with petroleum coke and commercial grade sulfur. Products stored on-site and transported through pipeline, and by railcar and commercial trucking. By-products include petroleum coke and asphalt. The facility operates a cogeneration system that fires sweet natual gas to produce electric power and steam primarily for consumption within the facility. | This permit is for planned debottle-necking operations. Facility plans to remove operational constraints in order to operate at an increased rate and produce additional product. The following new equipment will be installed: charge heater and boiler for fluid catalytic creacking unit (FCCU), auxiliary air heater for the cogeneration plant, crude heater, crude tank, gasoline storage tank, slop oil tank, gas oil tank, and fugitive components. Modifications will be made to seven process heaters and boilers, four compressor engines, the FCCU, and the cogeneration combustion turbine. There will also be modifications made to four stationary engines subject to NSPS JJJJ (4J). The Tail Gas Treatment Unit 2, will not be physically changed but will be operated continuously (increase in operational hours). Lastly, an increase in maximum-fired duty of 70 MMBtu/hr will be made to units B306 and B307 and have been added to the PSD permit as modified heaters. Facility proposed a single heat input limit for the units B306, B307, and B-NewCrudeHeater (B308) of 381.3 MMBtu/hr. | L3804 | 15.21 | Refinery Fuel Gas | 456.5 | MMBTU/H | Cogeneration Combustion Turbine, equipped with Heat Recovery Steam Generator and steam/water injection. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Proper combustion and operation | 0.0066 | LB/MMBTU | 3-HOUR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
KS-0041 | HOLLYFRONTIER EL DORADO REFINERY | HOLLYFRONTIER EL DORADO REFINING LLC | BUTLER | KS | 67042 | USA | RACHEL HENRY | 316-321-8283 | RACHEL.HENRY@HOLLYFRONTIER.COM | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov |  | CSD00080 V1.0 | 2911 | 324110 | 110000446134 | 04/29/2019 &nbsp;ACT | 10/30/2019 &nbsp;ACT | 2020-08-25 | 2023-03-27 | D |  | Petroleum Refinery located in Butler County, KS. Facility processes include distillation, cracking, reforming, isomerization, alkylation, hydrotreating, and coking. Products include a variety of grades of gasoline, fuel oils, and other fuels, along with petroleum coke and commercial grade sulfur. Products stored on-site and transported through pipeline, and by railcar and commercial trucking. By-products include petroleum coke and asphalt. The facility operates a cogeneration system that fires sweet natual gas to produce electric power and steam primarily for consumption within the facility. | This permit is for planned debottle-necking operations. Facility plans to remove operational constraints in order to operate at an increased rate and produce additional product. The following new equipment will be installed: charge heater and boiler for fluid catalytic creacking unit (FCCU), auxiliary air heater for the cogeneration plant, crude heater, crude tank, gasoline storage tank, slop oil tank, gas oil tank, and fugitive components. Modifications will be made to seven process heaters and boilers, four compressor engines, the FCCU, and the cogeneration combustion turbine. There will also be modifications made to four stationary engines subject to NSPS JJJJ (4J). The Tail Gas Treatment Unit 2, will not be physically changed but will be operated continuously (increase in operational hours). Lastly, an increase in maximum-fired duty of 70 MMBtu/hr will be made to units B306 and B307 and have been added to the PSD permit as modified heaters. Facility proposed a single heat input limit for the units B306, B307, and B-NewCrudeHeater (B308) of 381.3 MMBtu/hr. | L3804 | 15.21 | Refinery Fuel Gas | 456.5 | MMBTU/H | Cogeneration Combustion Turbine, equipped with Heat Recovery Steam Generator and steam/water injection. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Proper combustion and operation | 0.0066 | LB/MMBTU | 3-HOUR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
KS-0041 | HOLLYFRONTIER EL DORADO REFINERY | HOLLYFRONTIER EL DORADO REFINING LLC | BUTLER | KS | 67042 | USA | RACHEL HENRY | 316-321-8283 | RACHEL.HENRY@HOLLYFRONTIER.COM | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov |  | CSD00080 V1.0 | 2911 | 324110 | 110000446134 | 04/29/2019 &nbsp;ACT | 10/30/2019 &nbsp;ACT | 2020-08-25 | 2023-03-27 | D |  | Petroleum Refinery located in Butler County, KS. Facility processes include distillation, cracking, reforming, isomerization, alkylation, hydrotreating, and coking. Products include a variety of grades of gasoline, fuel oils, and other fuels, along with petroleum coke and commercial grade sulfur. Products stored on-site and transported through pipeline, and by railcar and commercial trucking. By-products include petroleum coke and asphalt. The facility operates a cogeneration system that fires sweet natual gas to produce electric power and steam primarily for consumption within the facility. | This permit is for planned debottle-necking operations. Facility plans to remove operational constraints in order to operate at an increased rate and produce additional product. The following new equipment will be installed: charge heater and boiler for fluid catalytic creacking unit (FCCU), auxiliary air heater for the cogeneration plant, crude heater, crude tank, gasoline storage tank, slop oil tank, gas oil tank, and fugitive components. Modifications will be made to seven process heaters and boilers, four compressor engines, the FCCU, and the cogeneration combustion turbine. There will also be modifications made to four stationary engines subject to NSPS JJJJ (4J). The Tail Gas Treatment Unit 2, will not be physically changed but will be operated continuously (increase in operational hours). Lastly, an increase in maximum-fired duty of 70 MMBtu/hr will be made to units B306 and B307 and have been added to the PSD permit as modified heaters. Facility proposed a single heat input limit for the units B306, B307, and B-NewCrudeHeater (B308) of 381.3 MMBtu/hr. | L3804 | 15.21 | Refinery Fuel Gas | 456.5 | MMBTU/H | Cogeneration Combustion Turbine, equipped with Heat Recovery Steam Generator and steam/water injection. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Proper combustion and operation | 0.0066 | LB/MMBTU | 3-HOUR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0129 | CPV THREE RIVERS ENERGY CENTER | CPV THREE RIVERS, LLC | GRUNDY | IL | 60450 | USA | MIKE BRUNO | 781-817-8972 | MBRUNO@CPV.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Illinois EPA, Bureau of Air Permit Section | 16060032 | 4911 | 221112 | Not Found | 06/10/2018 &nbsp;ACT | 07/30/2018 &nbsp;ACT | 2019-01-02 | 2019-02-19 | A |  | The proposed facility is designed to generate baseload power. It will consist of two combined-cycle generating units, each with a combustion turbine and associated heat recovery steam generator (HRSG). The turbines would burn natural gas and ultra-low sulfur diesel (ULSD) as a backup fuel. Other units include an auxiliary boiler, fuel heater, engines, natural gas piping and components, circuit breakers and roadways. |  | Combined Cycle Combustion Turbines | 15.21 | Natural Gas | 3474 | mmBtu/hr | Throughput of ultra-low sulfur diesel (ULSD) is 3798 mmBtu/hr. Combined cycle combustion turbines w/ heat recovery steam generator (HRSG). Turbine inlets will have inlet evaporative cooling systems to cool inlet air during warm weather to increase power output. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practice | 0.0069 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  | U | 0 | U | 0.032 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | 0 |  |  | 0 | 0 | N |  | Emission Limit 1 is for natural gas. Emission Limit 2 is for ULSD. Emission Limits 1 and 2 and permit limits address PM10 and PM2.5 together as PM10/PM2.5. Permit limits are as follows. For natural gas: With duct burner: 18.9 lb/hr Without duct burner: 11.5 lb/hr For ULSD: 65.1 lb/hr
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | GE Combustion Turbine - Option 1 - Normal Operation | 15.21 | natural gas | 34000 | MMCF/YR | Option 1: Two on one configuration: 3,482 MMBtu/hr combustion turbine with 475 MMBtu/hr duct-fired HRSG. Emission limits reflect the operation of one turbine with or without duct firing. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices and the use of pipeline quality natural gas with a maximum sulfur content of 0.4 gr/100 scf on a 12-month rolling average. | 0.0069 | LB/MMBTU WITHOUT DUC | AV OF 3 TEST RUNS | BACT-PSD | SIP | N | 0 | N | 0.0049 | LB/MMBTU WITH DUC | AV OF 3 TEST RUNS | 0 |  |  | 0 | 0 | N |  | Additional limits: 12.2 lb/hr without duct burning; 17.3 lb/hr with duct burning. These short term limits apply at all times.
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | GE Combustion Turbine - Option 1 - Normal Operation | 15.21 | natural gas | 34000 | MMCF/YR | Option 1: Two on one configuration: 3,482 MMBtu/hr combustion turbine with 475 MMBtu/hr duct-fired HRSG. Emission limits reflect the operation of one turbine with or without duct firing. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices and the use of pipeline quality natural gas with a maximum sulfur content of 0.4 gr/100 scf on a 12-month rolling average. | 0.0069 | LB/MMBTU WITHOUT DUC | AV OF 3 TEST RUNS | BACT-PSD | SIP | N | 0 | N | 0.0049 | LB/MMBTU WITH DUC | AV OF 3 TEST RUNS | 0 |  |  | 0 | 0 | N |  | Additional limits: 12.2 lb/hr without duct burning; 17.3 lb/hr with duct burning. These short term limits apply at all times.
AK-0088 | LIQUEFACTION PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | KENAI PENNINSULA BOROUGH | AK | 99635 | USA | LISA HAAS |  | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - Permit Writer - dave.jones2@alaska.gov | AQ1539CPT01 | 4922 | 488999 | Not Found | 01/14/2020 &nbsp;ACT | 07/07/2022 &nbsp;ACT | 2022-08-04 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Liquefaction Plant is planned to encompass 921 acres, including 901 acres onshore for the liquefied natural gas (LNG) Plant as well as 20 acres offshore for the Marine Terminal. The Liquefaction Plant will be the terminus of an approximately 807-mile gas pipeline, allowing natural gas from Alaskaâ€™s North Slope to be shipped to outside markets. The stationary source will consist of structures and equipment associated with processing, storage, and loading of LNG. There will be three liquefaction trains combining to process up to approximately 20 million metric tons per annun of LNG. |  | Four Combined Cycle Gas-Fired Turbines | 15.21 | Natural Gas | 384 | MMBtu/hr | EUs 7 - 10 are combined cycle gas turbines used for power generation at LNG facility | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and burning clean fuel (natural gas) | 0.007 | LB/MMBTU | 3-HOURS | BACT-PSD |  | U | 0 | U | 10 | % OPACITY | 6 CONSECUTIVE MINUTES | 0 |  |  | 0 | 0 | N
AK-0088 | LIQUEFACTION PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | KENAI PENNINSULA BOROUGH | AK | 99635 | USA | LISA HAAS |  | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - Permit Writer - dave.jones2@alaska.gov | AQ1539CPT01 | 4922 | 488999 | Not Found | 01/14/2020 &nbsp;ACT | 07/07/2022 &nbsp;ACT | 2022-08-04 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Liquefaction Plant is planned to encompass 921 acres, including 901 acres onshore for the liquefied natural gas (LNG) Plant as well as 20 acres offshore for the Marine Terminal. The Liquefaction Plant will be the terminus of an approximately 807-mile gas pipeline, allowing natural gas from Alaskaâ€™s North Slope to be shipped to outside markets. The stationary source will consist of structures and equipment associated with processing, storage, and loading of LNG. There will be three liquefaction trains combining to process up to approximately 20 million metric tons per annun of LNG. |  | Four Combined Cycle Gas-Fired Turbines | 15.21 | Natural Gas | 384 | MMBtu/hr | EUs 7 - 10 are combined cycle gas turbines used for power generation at LNG facility | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and burning clean fuel (natural gas) | 0.007 | LB/MMBTU | 3-HOURS | BACT-PSD |  | U | 0 | U | 10 | % OPACITY | 6 CONSECUTIVE MINUTES | 0 |  |  | 0 | 0 | N
AK-0088 | LIQUEFACTION PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | KENAI PENNINSULA BOROUGH | AK | 99635 | USA | LISA HAAS |  | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - Permit Writer - dave.jones2@alaska.gov | AQ1539CPT01 | 4922 | 488999 | Not Found | 01/14/2020 &nbsp;ACT | 07/07/2022 &nbsp;ACT | 2022-08-04 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Liquefaction Plant is planned to encompass 921 acres, including 901 acres onshore for the liquefied natural gas (LNG) Plant as well as 20 acres offshore for the Marine Terminal. The Liquefaction Plant will be the terminus of an approximately 807-mile gas pipeline, allowing natural gas from Alaskaâ€™s North Slope to be shipped to outside markets. The stationary source will consist of structures and equipment associated with processing, storage, and loading of LNG. There will be three liquefaction trains combining to process up to approximately 20 million metric tons per annun of LNG. |  | Four Combined Cycle Gas-Fired Turbines | 15.21 | Natural Gas | 384 | MMBtu/hr | EUs 7 - 10 are combined cycle gas turbines used for power generation at LNG facility | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and burning clean fuel (natural gas) | 0.007 | LB/MMBTU | 3-HOURS | BACT-PSD |  | U | 0 | U | 10 | % OPACITY | 6 CONSECUTIVE MINUTES | 0 |  |  | 0 | 0 | N
LA-0391 | MAGNOLIA POWER GENERATING STATION UNIT 1 | MAGNOLIA POWER LLC | IBERVILLE | LA | 70764 | USA | WILLIAM DAVIS | 609-250-7707 | LEE.DAVIS@KINDLE-ENERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Ms. Lori Pittman, (225)219-3180 | PSD-LA-839 | 4911 | 221112 | Not Found | 09/08/2020 &nbsp;ACT | 06/03/2022 &nbsp;ACT | 2023-03-02 | 2023-05-23 | A | https://edms.deq.louisiana.gov/app/doc/view?doc=13323738 | Magnolia Power LLC (Magnolia Power) is proposing to construct and operate a power plant, Magnolia Power Generating Station Unit 1, consisting of a natural gas-fired combined cycle gas turbine (CCGT Unit) in Iberville Parish, Louisiana. The CCGT Unit (EQT001), which includes a heat recovery steam generator (HRSG) equipped with duct burners, will have a predicted net nominal output of 730 megawatts (MW) |  | Combined Cycle Gas Turbine w/ Duct Burners and HRSG | 15.21 | Natural Gas | 5081 | mm BTU/h | Normal operating rate is 4930 MMBTU/h. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and OTM 28 | (Particulate Matter (PM)) | PM | P | Use of gaseous fuel (pipeline-quality natural gas) and good combustion practices. | 0.008 | LB/MM BTU | 3 ONE-HOUR TEST AVERAGE | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0391 | MAGNOLIA POWER GENERATING STATION UNIT 1 | MAGNOLIA POWER LLC | IBERVILLE | LA | 70764 | USA | WILLIAM DAVIS | 609-250-7707 | LEE.DAVIS@KINDLE-ENERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Ms. Lori Pittman, (225)219-3180 | PSD-LA-839 | 4911 | 221112 | Not Found | 09/08/2020 &nbsp;ACT | 06/03/2022 &nbsp;ACT | 2023-03-02 | 2023-05-23 | A | https://edms.deq.louisiana.gov/app/doc/view?doc=13323738 | Magnolia Power LLC (Magnolia Power) is proposing to construct and operate a power plant, Magnolia Power Generating Station Unit 1, consisting of a natural gas-fired combined cycle gas turbine (CCGT Unit) in Iberville Parish, Louisiana. The CCGT Unit (EQT001), which includes a heat recovery steam generator (HRSG) equipped with duct burners, will have a predicted net nominal output of 730 megawatts (MW) |  | Combined Cycle Gas Turbine w/ Duct Burners and HRSG | 15.21 | Natural Gas | 5081 | mm BTU/h | Normal operating rate is 4930 MMBTU/h. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and Mthd 202 | (Particulate Matter (PM)) | PM | P | Use of gaseous fuel (pipeline-quality natural gas) and good combustion practices. | 0.008 | LB/MM BTU | 3 ONE-HOUR TEST AVERAGE | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AL-0328 | PLANT BARRY | ALABAMA POWER COMPANY | MOBILE | AL | 36512 | USA | TYLER PHILLIPS |  | TYLER.PHILLIPS@ADEM.ALABAMA.GOV | 4 | AL001 | ALABAMA DEPT OF ENVIRONMENTAL MGMT | MR. DALE HURST | (334) 271-7882 | ADH@ADEM.STATE.AL.US |  | 503-1001 | 4911 | 221112 | 110000741270 | 05/01/2020 &nbsp;ACT | 11/09/2020 &nbsp;ACT | 2021-09-30 | 2022-03-04 | B |  |  |  | Two 744 MW Combined Cycle Units | 15.21 | Natural Gas | 744 | MW |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N |  | 0.6 | GR S/100 SCF FUEL |  | BACT-PSD | NSPS , SIP , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | GE Combustion Turbine - Option 1 - Normal Operation | 15.21 | natural gas | 34000 | MMCF/YR | Option 1: Two on one configuration: 3,482 MMBtu/hr combustion turbine with 475 MMBtu/hr duct-fired HRSG. Emission limits reflect the operation of one turbine with or without duct firing. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst and good combustion practices | 0.7 | PPMVD @ 15% O2 | 3 HR AV/WITHOUT DB | BACT-PSD | SIP , NSPS | U | 0 | N | 1.4 | PPMVD @ 15% O2 | 3 HR AV/WITH DB | 0 |  |  | 0 | 0 | N |  | Alternative emission limits apply during startup and shutdown. Compliance is based on compliance with CO limits, determined by CEMS.
VA-0332 | CHICKAHOMINY POWER LLC | CHICKAHOMINY POWER LLC | CHARLES CITY | VA | 23030 | USA | IRFAN ALI | (703) 226-0192 | IRFANKALI@BALICO.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer: Alison K. Sinclair Phone: (804)-527-5155 Email: Alison.Sinclair@deq.virginia.gov | 52610-1 | 4911 | 221112 | Not Found | 11/05/2018 &nbsp;ACT | 06/24/2019 &nbsp;ACT | 2019-08-07 | 2021-05-19 | A |  | Natural gas-fired combined cycle power plant, three 1 x1 configuration, 310 MW each, no duct firing, air cooled with two 84 MMBtu/H natural gas-fired auxiliary boilers, three fuel gas heaters, an emergency generator, fire water pump, and circuit breakers. | The proposed project will be a new combined-cycle electrical power generating facility utilizing three power blocks consisting of a combustion turbine with a heat recovery steam generator (HRSG) and a reheat condensing steam turbine generator (three 1 x 1 configuration). The turbine model proposed is a MHPS M501JAC turbine. The project will have a nominal net generating capacity of 1,650 MW. The proposed fuel for the turbines is pipeline-quality natural gas. Emissions from the turbines will be controlled by the use of low carbon fuels and high efficiency design (for GHG), clean fuels and GCPs (for PM, PM10 and PM2.5), SCR and dry low NOx burners (for NOx), and oxidation catalyst (for CO and VOC). Other equipment at the site, including two natural gas-fired auxiliary boilers, three fuel gas heaters, a diesel-fired emergency fire water pump, and a diesel-fired emergency generator, are also proposed and will be subject to emission controls. Natural gas piping components and electrical circuit breakers potentially emit GHG pollutants (expressed as carbon dioxide equivalents, or CO2e) and they will also be covered in the permit. This facility is not proposing duct firing in the HRSGs and is proposing air-cooled turbines that will not require cooling towers. | Three (3) Mitsubishi Hitachi Power Systems combustion turbine generators | 15.21 | natural gas | 35000 | MMCF/YR | One on one configuration: 4,066 MMBtu/H combustion turbine. Emission limits reflect the operation of each of the three turbines. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Controlled by an oxidation catalyst and good combustion practices (e.g. controlled fuel/air mixing, adequate temperature, and gas residence time) | 0.7 | PPMVD @ 15% O2 | 3 HR AVG | BACT-PSD | SIP , NSPS | N | 0 | N | 68.1 | T/YR | 12 MO ROLLING AVG | 0 |  |  | 0 | 0 | N |  | Alternative emission limits apply during startup and shutdown. Compliance is based on compliance with CO limits, determined by CEMS. VOC emissions during tuning are limited by the duration of the tuning event.
MI-0432 | NEW COVERT GENERATING FACILITY | NEW COVERT GENERATING COMPANY, LLC | VAN BUREN | MI | 49043 | USA | JOHN REESE | 212-792-0897 | JREESE@EASTERNGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 186-17 | 4911 | 221112 | Not Found | 04/17/2018 &nbsp;ACT | 07/30/2018 &nbsp;ACT | 2018-08-13 | 2019-02-19 | C |  | Power plant | The equipment consists of three advanced firing temperature Mitsubishi 501G combustion turbines, three heat recovery steam generators supplemented with gas-fired duct burners each with a max firing rate of 256 million British thermal units per hour (MMBtu/hr), three steam turbine generators. Auxiliary equipment includes three mechanical draft evaporative cooling towers, one natural gas auxiliary boiler, one diesel emergency generator, one diesel fire water pump, one aqueous parts cleaner, and one gas heater. | FG-TURB/DB1-3 (3 combined cycle combustion turbine and heat recovery steam generator trains) | 15.21 | Natural gas | 1230 | MW | Three (3) combined-cycle combustion turbine (CT) / heat recovery steam generator (HRSG) trains. Each CT is a natural gas fired Mitsubishi model 501G, equipped with dry low NOx combustor and inlet air evaporative cooling. Each HRSG includes a natural gas fired duct burner with a 256 MMBtu/hr heat input capacity and a dry low NOx burner. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Use of clean fuel (natural gas) with a fuel sulfur limit of 0.8 grains per 100 standard cubic feet of natural gas. | 0.8 | GR/100 SCF | NAT.GAS BURNED IN FG-TURB/DB1-3 | BACT-PSD | NSPS , SIP | N | 0 | N | 0.06 | LB/MMBTU | HOURLY; EACH CT/HRSG TRAIN; NSPS KKKK | 0 |  |  | 0 | 0 | N |  | Emission limit 2 above is from NSPS KKKK and is 0.060 LB/MMBTU heat input. Emission limit 1 above is a material limit of 0.8 grains/100 scf of natural gas burned in FG-TURB/DB1-3
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | GE Combustion Turbine - Option 1 - Normal Operation | 15.21 | natural gas | 34000 | MMCF/YR | Option 1: Two on one configuration: 3,482 MMBtu/hr combustion turbine with 475 MMBtu/hr duct-fired HRSG. Emission limits reflect the operation of one turbine with or without duct firing. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practices | 1 | PPMVD@ 15% O2 | 3 HR AV/WITHOUT DB | BACT-PSD | NSPS , SIP | U | 0 | N | 1.6 | PPMVD@ 15% O2 | 3 HR AV/WITH DB | 0 |  |  | 0 | 0 | N |  | Alternative emission limits apply during startup and shutdown. CEMS required.
VA-0332 | CHICKAHOMINY POWER LLC | CHICKAHOMINY POWER LLC | CHARLES CITY | VA | 23030 | USA | IRFAN ALI | (703) 226-0192 | IRFANKALI@BALICO.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer: Alison K. Sinclair Phone: (804)-527-5155 Email: Alison.Sinclair@deq.virginia.gov | 52610-1 | 4911 | 221112 | Not Found | 11/05/2018 &nbsp;ACT | 06/24/2019 &nbsp;ACT | 2019-08-07 | 2021-05-19 | A |  | Natural gas-fired combined cycle power plant, three 1 x1 configuration, 310 MW each, no duct firing, air cooled with two 84 MMBtu/H natural gas-fired auxiliary boilers, three fuel gas heaters, an emergency generator, fire water pump, and circuit breakers. | The proposed project will be a new combined-cycle electrical power generating facility utilizing three power blocks consisting of a combustion turbine with a heat recovery steam generator (HRSG) and a reheat condensing steam turbine generator (three 1 x 1 configuration). The turbine model proposed is a MHPS M501JAC turbine. The project will have a nominal net generating capacity of 1,650 MW. The proposed fuel for the turbines is pipeline-quality natural gas. Emissions from the turbines will be controlled by the use of low carbon fuels and high efficiency design (for GHG), clean fuels and GCPs (for PM, PM10 and PM2.5), SCR and dry low NOx burners (for NOx), and oxidation catalyst (for CO and VOC). Other equipment at the site, including two natural gas-fired auxiliary boilers, three fuel gas heaters, a diesel-fired emergency fire water pump, and a diesel-fired emergency generator, are also proposed and will be subject to emission controls. Natural gas piping components and electrical circuit breakers potentially emit GHG pollutants (expressed as carbon dioxide equivalents, or CO2e) and they will also be covered in the permit. This facility is not proposing duct firing in the HRSGs and is proposing air-cooled turbines that will not require cooling towers. | Three (3) Mitsubishi Hitachi Power Systems combustion turbine generators | 15.21 | natural gas | 35000 | MMCF/YR | One on one configuration: 4,066 MMBtu/H combustion turbine. Emission limits reflect the operation of each of the three turbines. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Controlled by an oxidation catalyst and good combustion practices (e.g. controlled fuel/air mixing, adequate temperature, and gas residence time). | 1 | PPMVD @ 15% O2 | 3 HR AVG | BACT-PSD | NSPS , SIP | N | 0 | N | 94.3 | TONS/YR | 12 MO ROLLING AVG | 0 |  |  | 0 | 0 | N |  | Alternative emission limits apply during startup, shutdown, and tuning. CEMS required.
TX-0834 | MONTGOMERY COUNTY POWER STATIOIN | ENTERGY TEXAS INC | MONTGOMERY | TX |  | USA | CHRISTOPHER BURKE | 281-297-3369 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., 512-239-2175 laura.gibson@tceq.texas.gov | N256, PSDTX1510, AND GHGPSDTX1 | 4911 | 221112 | Not Found | 01/18/2018 &nbsp;ACT | 03/30/2018 &nbsp;ACT | 2018-04-26 | 2019-02-19 | A |  |  |  | Combined Cycle Turbine | 15.21 | NATURAL GAS | 2635 | MMBTU/HR/UNIT | Two Mitsubishi M501GAC turbines (without fast start) | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | PIPELINE QUALITY NATURAL GAS | 1 | GR/100 DSCF |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK & TTTT, MACT YYYY
FL-0364 | SEMINOLE GENERATING STATION | SEMINOLE ELECTRIC COOPERATIVE, INC. | PUTNAM | FL | 32177 | USA | CHRIS WEBER | 813-739-1359 | CWEBER@SEMINOLE-ELECTRIC.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 1070025-028-AC / PSD-FL-443 | 4911 | 221112 | 110041142304 | 12/11/2017 &nbsp;ACT | 03/21/2018 &nbsp;ACT | 2018-04-13 | 2018-05-11 | B | https://arm-permit2k.dep.state.fl.us/nontv/1070025.028.AC.F.ZIP | Existing fossil-fueled power plant. Two coal-fired units each rated at 736 MW. Project entails retirement of one coal-fired unit and construction of a 2-on-1 natural gas combined cycle unit. | Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/1070025.028.AC.D.ZIP | 2-on-1 natural gas combined-cycle unit (GE 7HA.02) | 15.21 | Natural gas | 3514 | MMBtu/hr | Two GE 7HA.02 combustion turbines, each rated at 415 MW. Total unit capacity is approximately 1,183 MW (gross) and 1,050 MW (net). Due to netting, triggered PSD only for VOC. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 18 | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation catalyst | 1 | PPMVD@15% O2 | WITHOUT DUCT BURNER FIRING | BACT-PSD |  | U | 0 | U | 2 | PPMVD@15% O2 | CT + DUCT BURNER OPERATION | 0 |  |  | 0 | 0 | N |  | Methods 18 and 25A are permitted. Compliance by stack test upon Title V permit renewal. Separate tests with and without duct burner firing are required.
IL-0133 | LINCOLN LAND ENERGY CENTER | LINCOLN LAND ENERGY CENTER (A/K/A EMBERCLEAR) | SANGAMON | IL | 62558 | USA | JIM PALUMBO | 888-582-4460 X 55 | JPALUMBO@EMBERCLEAR.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov |  | 18040008 | 4911 | 221112 | Not Found | 09/30/2021 &nbsp;ACT | 07/29/2022 &nbsp;ACT | 2022-08-26 | 2022-12-06 | A | www2.illinois.gov/epa/public-notices/boa-notices/pages/archive.aspx | The proposed facility is designed to generate baseload power. It will consist of two combined-cycle generating units, with each a Siemens combustion turbine (3,647 mmBtu/hr) and a heat recovery steam generator (HRSG) with duct burners (35 mmBtu/hr); fired by natural gas only. Other units at the facility include an auxiliary boiler, engines, piping and piping components, circuit breakers and roadways. | Additional facility-wide pollutants, in tons/year: PM10/PM 2.5: 131.7 and 131.6 (respectively); sulfuric acid mist (SAM): 17.2; greenhouse gasses (GHG): 3,586,918 | Combined-Cycle Combustion Turbines | 15.21 | Natural Gas | 3647 | mmBtu/hour | Combined-cycle comustion turbines and heat recovery steam generators (HRSG) with a 35 mmBtu/hr duct burner. Turbine inlets would have evaporative cooling systems to cool the inlet air during warm weather to increase power output. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst and good combustion practices. | 1 | PPMV, ADJ. TO 15% O2 | ROLLING 3-OPERATING HOUR | BACT-PSD |  | U | 0 | U | 1.1 | PPMV, ADJ. TO 15% O2 | ROLLING 3-OPERATING HOUR | 0 |  |  | 0 | 0 | N |  | Emission Limits 1 and 2 exclude startup and shutdown. Emission Limit 3: 56 pounds/hour (cold start); 48 pounds/hour (non-cold start); and 44 pounds/hour (shutdown) during each hour that includes a startup or shutdown and shakedown.
LA-0391 | MAGNOLIA POWER GENERATING STATION UNIT 1 | MAGNOLIA POWER LLC | IBERVILLE | LA | 70764 | USA | WILLIAM DAVIS | 609-250-7707 | LEE.DAVIS@KINDLE-ENERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Ms. Lori Pittman, (225)219-3180 | PSD-LA-839 | 4911 | 221112 | Not Found | 09/08/2020 &nbsp;ACT | 06/03/2022 &nbsp;ACT | 2023-03-02 | 2023-05-23 | A | https://edms.deq.louisiana.gov/app/doc/view?doc=13323738 | Magnolia Power LLC (Magnolia Power) is proposing to construct and operate a power plant, Magnolia Power Generating Station Unit 1, consisting of a natural gas-fired combined cycle gas turbine (CCGT Unit) in Iberville Parish, Louisiana. The CCGT Unit (EQT001), which includes a heat recovery steam generator (HRSG) equipped with duct burners, will have a predicted net nominal output of 730 megawatts (MW) |  | Combined Cycle Gas Turbine w/ Duct Burners and HRSG | 15.21 | Natural Gas | 5081 | mm BTU/h | Normal operating rate is 4930 MMBTU/h. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | B | Catalytic oxidation and good combustion practices. | 1 | PPMVD | 3 1-HR TEST AVERAGE | BACT-PSD | NSPS | U | 0 | U | 2 | PPMVD | 3 1-HR TEST AVERAGE | 0 |  |  | 0 | 0 | N |  | 1.0 and 2.0 ppmvd at 15% O2 based on a three one-hour test average without and with duct firing, respectively.
MI-0432 | NEW COVERT GENERATING FACILITY | NEW COVERT GENERATING COMPANY, LLC | VAN BUREN | MI | 49043 | USA | JOHN REESE | 212-792-0897 | JREESE@EASTERNGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 186-17 | 4911 | 221112 | Not Found | 04/17/2018 &nbsp;ACT | 07/30/2018 &nbsp;ACT | 2018-08-13 | 2019-02-19 | C |  | Power plant | The equipment consists of three advanced firing temperature Mitsubishi 501G combustion turbines, three heat recovery steam generators supplemented with gas-fired duct burners each with a max firing rate of 256 million British thermal units per hour (MMBtu/hr), three steam turbine generators. Auxiliary equipment includes three mechanical draft evaporative cooling towers, one natural gas auxiliary boiler, one diesel emergency generator, one diesel fire water pump, one aqueous parts cleaner, and one gas heater. | FG-TURB/DB1-3 (3 combined cycle combustion turbine and heat recovery steam generator trains) | 15.21 | Natural gas | 1230 | MW | Three (3) combined-cycle combustion turbine (CT) / heat recovery steam generator (HRSG) trains. Each CT is a natural gas fired Mitsubishi model 501G, equipped with dry low NOx combustor and inlet air evaporative cooling. Each HRSG includes a natural gas fired duct burner with a 256 MMBtu/hr heat input capacity and a dry low NOx burner. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | An oxidation catalyst and good combustion practices. | 1 | PPMVD | HOURLY; EACH CT/HRSG TRAIN | BACT-PSD | SIP | N | 0 | N | 48 | T/YR | EACH CT/HRSG TRAIN; 12-MO ROLL TIME PER. | 0 |  |  | 0 | 0 | N |  | Emission limit 1 above does not include startup and shutdown. Emission limit 2 above is 48 ton/year based on a 12-month rolling time period as determined at the end of each calendar month.
TX-0915 | UNIT 5 | NRG CEDAR BAYOU LLC | CHAMBERS | TX |  | USA | CRAIG ECKBERG | 713-537-2776 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Ruth Alvirez, (512) 239-5220, Ruth.Alvirez@tceq.texas.gov | 160538, PSDTX1528, GHGPSDTX204 | 4911 | 221112 | Not Found | 11/05/2020 &nbsp;ACT | 03/17/2021 &nbsp;ACT | 2020-12-08 | 2022-03-08 | U |  | UNIT 5 |  | COMBINED CYCLE TURBINE | 15.21 | NATURAL GAS | 0 |  |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | OXIDATION CATALYST | 1 | PPMVD | 3-HR ROLLING | BACT-PSD | NSPS , MACT , SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | Siemens Combusion Turbine - Option 2 - Normal Operation | 15.21 | Natural Gas | 35000 | MMCF/YR | Option 2: Two on one configuration: 3,116 MMBtu/hr combustion turbine with 991 MMBtu/hr duct-fired HRSG. Emission limits reflect the operation of one turbine with or without duct firing. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst and good combustion practice | 1 | PPMVD @ 15% O2 | 3 H AV/WITHOUT DB | BACT-PSD | NSPS , SIP | N | 0 | N | 2 | PPMVD @ 15% O2 | 3 H AV/WITH DB | 0 |  |  | 0 | 0 | N |  | Alternative emission limits apply during startup and shutdown. Compliance is based on compliance with CO limits, determined by CEMS.
*WV-0033 | MAIDSVILLE | MOUNTAIN STATE CLEAN ENERGY, LLC | MONONGALIA | WV | 26541 | USA | BRIAN HOYT | 304-559-0930 X2203 | BHOYT@LONGVIEWPOWER.NET | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Mr. Ed Andrews edward.s.andrews@wv.gov | R14-0038 | 4911 | 221112 | 054-061-00134 | 05/05/2020 &nbsp;ACT | 01/05/2022 &nbsp;ACT | 2022-04-01 | 2022-06-28 | U | https://dep.wv.gov/daq/permitting/Pages/NSR-Permit-Applications.aspx | This project consist of constructing two combined cycle combustion turbine with duct burners, two fuel gas heaters, two emergency engines (emergency generator and fire water pump), and cooling tower. The configuration of these combustion turbines with heat recovery steam generators will be a 2X1. This facility will be co-located next to existing EGU (Longview Power LLC). The CCCTs with duct burners and fuel gas heaters will operate only on natural gas. Both emergency engines will be diesel fired units. | A bi-direction steam line between the Mountain State Clean Energy and Longview Power will be use to provide startup steam in lieu of a auxiliary boiler. No limits on operating hours or fuel use for the duct burners. Applicant proposed two different model combustion turbine (GE 7HA.03 and MHPS M501JAC). Gross Generation for the facility is 1275 MWh. | Combustion Turbine &amp; Duct Burner (CT-01/HRSG1 &amp; CT-02/HRSG2) | 15.21 | Pipeline Natural Gas | 1275 | mw | CT - 3,875 MMBtu/hr DB - 586 MMBtu/hr Gross Generation - 1275 MW | Volatile Organic Compounds (VOC) | Other - Method 25A/18 | (Volatile Organic Compounds (VOC)) | VOC | B | good combustion practices and oxidation catalyst | 1 | PPMDV @ 15% O2 | AVG OF 3 1-HR TEST RUNS (W/O DUCT FIRING | BACT-PSD | N/A | U | 0 | U | 2 | PPMDV @ 15% O2 | AVG OF 3 1-HR TEST RUNS (W DUCT FIRING | 11.19 | LB/HR | AVG OF 3 1-HR TEST RUNS | 0 | 0 | N |  | Concentration and Mass limits apply at all times excluding startup and shutdown events.
*WV-0033 | MAIDSVILLE | MOUNTAIN STATE CLEAN ENERGY, LLC | MONONGALIA | WV | 26541 | USA | BRIAN HOYT | 304-559-0930 X2203 | BHOYT@LONGVIEWPOWER.NET | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Mr. Ed Andrews edward.s.andrews@wv.gov | R14-0038 | 4911 | 221112 | 054-061-00134 | 05/05/2020 &nbsp;ACT | 01/05/2022 &nbsp;ACT | 2022-04-01 | 2022-06-28 | U | https://dep.wv.gov/daq/permitting/Pages/NSR-Permit-Applications.aspx | This project consist of constructing two combined cycle combustion turbine with duct burners, two fuel gas heaters, two emergency engines (emergency generator and fire water pump), and cooling tower. The configuration of these combustion turbines with heat recovery steam generators will be a 2X1. This facility will be co-located next to existing EGU (Longview Power LLC). The CCCTs with duct burners and fuel gas heaters will operate only on natural gas. Both emergency engines will be diesel fired units. | A bi-direction steam line between the Mountain State Clean Energy and Longview Power will be use to provide startup steam in lieu of a auxiliary boiler. No limits on operating hours or fuel use for the duct burners. Applicant proposed two different model combustion turbine (GE 7HA.03 and MHPS M501JAC). Gross Generation for the facility is 1275 MWh. | Combustion Turbine &amp; Duct Burner (CT-01/HRSG1 &amp; CT-02/HRSG2) | 15.21 | Pipeline Natural Gas | 1275 | mw | CT - 3,875 MMBtu/hr DB - 586 MMBtu/hr Gross Generation - 1275 MW | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | B | good combustion practices and oxidation catalyst | 1 | PPMDV @ 15% O2 | AVG OF 3 1-HR TEST RUNS (W/O DUCT FIRING | BACT-PSD | N/A | N | 0 | U | 2 | PPMDV @ 15% O2 | AVG OF 3 1-HR TEST RUNS (W DUCT FIRING | 11.89 | LB/HR | AVG OF 3 1-HR TEST RUNS | 0 | 0 | N |  | Concentration and Mass limits apply at all times excluding startup and shutdown events.
LA-0331 | CALCASIEU PASS LNG PROJECT | VENTURE GLOBAL CALCASIEU PASS, LLC | CAMERON | LA | 70631 | USA | GRAHAM MCARTHUR | 202-759-6741 | GMCARTHUR@VGLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Ms. Mei Wu, (225)219-3180 | PDS-LA-805 | 4925 | 221210 | Not Found | 06/25/2018 &nbsp;ACT | 09/21/2018 &nbsp;ACT | 2019-02-14 | 2019-06-19 | A |  | New Liquefied Natural Gas (LNG) production, storage, and export terminal. | Application Received September 2, 2015. | Combined Cycle Combustion Turbines (CCCT1 to CCCT5) | 15.21 | Natural Gas | 921 | MM BTU/h |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Catalytic Oxidation, Proper Equipment Design and Good Combustion Practices. | 1.1 | PPMV | 3 HOUR AVERAGE | BACT-PSD | OPERATING PERMIT , NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Units are in ppmv @ 15% O2; Averaging Time 3-Hour Average During Normal Operations.
LA-0364 | FG LA COMPLEX | FG LA LLC | ST. JAMES | LA | 70086 | USA | KUAN-MING PEMG | 2813026850 | KMPEMG@FPCC.COM.TW | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mr. Anthony Randall, (225)219-3180 | PSD-LA-812 | 2869 | 325110 | Not Found | 01/14/2019 &nbsp;ACT | 01/06/2020 &nbsp;ACT | 2020-05-05 | 2021-08-09 | A | https://edms.deq.louisiana.gov/app/doc/view.aspx?doc=11998450&ob=yes&child=yes | The FG LA complex will produce ethylene, propylene, ethylene glycol, high density polyethylene, low density polyethylene, linear low-density polyethylene and polypropylene. To support the operation of these production plants, the complex will also include electric power and steam generating units (Utility), wastewater treatment (Central Wastewater Treatment Plant), storage and loading operations (Logistics), and associated flare systems. | FG LA was issued PSD-LA-812 to construct the FG LA Complex which involves the construction of fourteen facilities permitted under fourteen Title V Permits to manufacture ethylene and propylene, ultimately producing high and low density polyethylene, propylene, and ethylene glycol. | Cogeneration Units | 15.21 | Natural Gas | 2222 | mm btu/h | Throughput is maximum operating rate. 2139 MM BTU/hr normal operating rate. | Sulfur Dioxide (SO2) | EPA/OAR Mthd 6A | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Use of pipeline quality natural gas or fuel gas. | 1.24 | LB/H |  | BACT-PSD | NSPS , NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0371 | SHADY HILLS COMBINED CYCLE FACILITY | SHADY HILLS ENERGY CENTER, LLC | PASCO | FL | 34610 | USA | ROY BELDEN |  | ROY.BELDEN@GE.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 1010524-003-AC (PSD-FL-444A) | 4911 | 221112 | 110012581820 | 04/02/2021 &nbsp;ACT | 06/07/2021 &nbsp;ACT | 2021-11-19 | 2022-03-04 | U | https://depedms.dep.state.fl.us:443/Oculus/servlet/shell?command=hitlist&[freeText=]&[folderName=]&[profile=Permitting_Authorization]&[creator=]&[entityType=any]&[createdDateTo=]&[catalog=75]&[searchBy=Profile]&[sortBy=Document Date]&[createdDate=]&{County=_EQ_PASCO}&{District=_EQ_SWD}&{Facility-Site ID=_EQ_AIR_1010524}&{Document Type=_EQ_PERMIT - FINAL}&{Facility Type=_LK_N/A}&{Application Number=_EQ_1010524003} | The Shady Hills Combined Cycle Facility (SHCCF), a new 573-megawatt (MW) (winter) 1-on-1 combined cycle electrical generating facility to be owned and operated by Shady Hills Energy Center, LLC, which will be located at 14350 Merchant Energy Way, Spring Hill, Florida. The proposed work will be conducted on an approximately 14-acre parcel east of and located adjacent to the existing Shady Hills Generating Station (SHGS) power plant, which is owned and operated by Shady Hills Power Company, L.L.C. |  | GE 7HA.02 Combustion Turbine and HRSG with Duct Firing | 15.21 | Natural Gas | 3622.1 | MMBtu/hour | Throughput based on a compressor inlet air temperature of 59Â° F, the higher heating value (HHV) of natural gas, and 100% load | Particulate matter, filterable (FPM) | Other - Fuel Recordkeeping | (Particulate Matter (PM)) | PM | P | Low sulfur fuel | 1.4 | GR. S/100 SCF NG |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0371 | SHADY HILLS COMBINED CYCLE FACILITY | SHADY HILLS ENERGY CENTER, LLC | PASCO | FL | 34610 | USA | ROY BELDEN |  | ROY.BELDEN@GE.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 1010524-003-AC (PSD-FL-444A) | 4911 | 221112 | 110012581820 | 04/02/2021 &nbsp;ACT | 06/07/2021 &nbsp;ACT | 2021-11-19 | 2022-03-04 | U | https://depedms.dep.state.fl.us:443/Oculus/servlet/shell?command=hitlist&[freeText=]&[folderName=]&[profile=Permitting_Authorization]&[creator=]&[entityType=any]&[createdDateTo=]&[catalog=75]&[searchBy=Profile]&[sortBy=Document Date]&[createdDate=]&{County=_EQ_PASCO}&{District=_EQ_SWD}&{Facility-Site ID=_EQ_AIR_1010524}&{Document Type=_EQ_PERMIT - FINAL}&{Facility Type=_LK_N/A}&{Application Number=_EQ_1010524003} | The Shady Hills Combined Cycle Facility (SHCCF), a new 573-megawatt (MW) (winter) 1-on-1 combined cycle electrical generating facility to be owned and operated by Shady Hills Energy Center, LLC, which will be located at 14350 Merchant Energy Way, Spring Hill, Florida. The proposed work will be conducted on an approximately 14-acre parcel east of and located adjacent to the existing Shady Hills Generating Station (SHGS) power plant, which is owned and operated by Shady Hills Power Company, L.L.C. |  | GE 7HA.02 Combustion Turbine and HRSG with Duct Firing | 15.21 | Natural Gas | 3622.1 | MMBtu/hour | Throughput based on a compressor inlet air temperature of 59Â° F, the higher heating value (HHV) of natural gas, and 100% load | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - Fuel Recordkeeping | (Particulate Matter (PM)) | PM | P | Clean fuels | 1.4 | GR. S/100 SCF NG |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0371 | SHADY HILLS COMBINED CYCLE FACILITY | SHADY HILLS ENERGY CENTER, LLC | PASCO | FL | 34610 | USA | ROY BELDEN |  | ROY.BELDEN@GE.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 1010524-003-AC (PSD-FL-444A) | 4911 | 221112 | 110012581820 | 04/02/2021 &nbsp;ACT | 06/07/2021 &nbsp;ACT | 2021-11-19 | 2022-03-04 | U | https://depedms.dep.state.fl.us:443/Oculus/servlet/shell?command=hitlist&[freeText=]&[folderName=]&[profile=Permitting_Authorization]&[creator=]&[entityType=any]&[createdDateTo=]&[catalog=75]&[searchBy=Profile]&[sortBy=Document Date]&[createdDate=]&{County=_EQ_PASCO}&{District=_EQ_SWD}&{Facility-Site ID=_EQ_AIR_1010524}&{Document Type=_EQ_PERMIT - FINAL}&{Facility Type=_LK_N/A}&{Application Number=_EQ_1010524003} | The Shady Hills Combined Cycle Facility (SHCCF), a new 573-megawatt (MW) (winter) 1-on-1 combined cycle electrical generating facility to be owned and operated by Shady Hills Energy Center, LLC, which will be located at 14350 Merchant Energy Way, Spring Hill, Florida. The proposed work will be conducted on an approximately 14-acre parcel east of and located adjacent to the existing Shady Hills Generating Station (SHGS) power plant, which is owned and operated by Shady Hills Power Company, L.L.C. |  | GE 7HA.02 Combustion Turbine and HRSG with Duct Firing | 15.21 | Natural Gas | 3622.1 | MMBtu/hour | Throughput based on a compressor inlet air temperature of 59Â° F, the higher heating value (HHV) of natural gas, and 100% load | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - Fuel Recordkeeping | (Particulate Matter (PM)) | PM | P | Clean fuels | 1.4 | GR. S/100 SCF NG |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0371 | SHADY HILLS COMBINED CYCLE FACILITY | SHADY HILLS ENERGY CENTER, LLC | PASCO | FL | 34610 | USA | ROY BELDEN |  | ROY.BELDEN@GE.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 1010524-003-AC (PSD-FL-444A) | 4911 | 221112 | 110012581820 | 04/02/2021 &nbsp;ACT | 06/07/2021 &nbsp;ACT | 2021-11-19 | 2022-03-04 | U | https://depedms.dep.state.fl.us:443/Oculus/servlet/shell?command=hitlist&[freeText=]&[folderName=]&[profile=Permitting_Authorization]&[creator=]&[entityType=any]&[createdDateTo=]&[catalog=75]&[searchBy=Profile]&[sortBy=Document Date]&[createdDate=]&{County=_EQ_PASCO}&{District=_EQ_SWD}&{Facility-Site ID=_EQ_AIR_1010524}&{Document Type=_EQ_PERMIT - FINAL}&{Facility Type=_LK_N/A}&{Application Number=_EQ_1010524003} | The Shady Hills Combined Cycle Facility (SHCCF), a new 573-megawatt (MW) (winter) 1-on-1 combined cycle electrical generating facility to be owned and operated by Shady Hills Energy Center, LLC, which will be located at 14350 Merchant Energy Way, Spring Hill, Florida. The proposed work will be conducted on an approximately 14-acre parcel east of and located adjacent to the existing Shady Hills Generating Station (SHGS) power plant, which is owned and operated by Shady Hills Power Company, L.L.C. |  | GE 7HA.02 Combustion Turbine and HRSG with Duct Firing | 15.21 | Natural Gas | 3622.1 | MMBtu/hour | Throughput based on a compressor inlet air temperature of 59Â° F, the higher heating value (HHV) of natural gas, and 100% load | Sulfur Dioxide (SO2) | Other - Fuel Recordkeeping | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Low sulfur fuel | 1.4 | GR. S/100 SCF NG |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1251 | PALMDALE ENERGY PROJECT | PALMDALE ENERGY, LLC | LOS ANGELES | CA | 93551 | USA | TOM CAMERON |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov | Staff Contact: Lisa Beckham beckham.lisa@epa.gov (415) 972-3811 | SE 17-01 | 4911 | 221122 | Not Found | 08/16/2017 &nbsp;ACT | 04/25/2018 &nbsp;ACT | 2018-10-25 | 2020-01-31 | A | https://www.epa.gov/caa-permitting/palmdale-energy-project-prevention-significant-deterioration-psd-permit | 645 MW (nominal) Natural Gas-fired Combined Cycle Power Plant, 2 x 1 configuration, auxiliary boiler for faster startup | See also docket: https://www.regulations.gov/docket?D=EPA-R09-OAR-2017-0473. Permit decision was appealed to EPA's Environmental Appeals Board. Board denied review on October 23, 2018. Information available through www.epa.gov/eab and https://yosemite.epa.gov/oa/EAB_Web_Docket.nsf/f22b4b245fab46c6852570e6004df1bd/ad735c0b822500258525829d004217eb!OpenDocument. 1/31/20 -- SYS MGR -- Link to permit is <https://www.regulations.gov/document?D=EPA-R09-OAR-2017-0473-0028> | Combustion Turbines (GEN1 and GEN2) | 15.21 | Natural Gas | 2217 | MMBTU/H | Each combustion turbine rated at 214 MW, with a maximum heat input rate of 2,217 MMBtu/H (HHV, at ISO conditions); natural gas-fired Siemens SGT6-5000F; each vents to dedicated Heat Recovery Steam Generator and a shared 276 MW Steam Turbine Generator; 160-ft stack height; 22-ft stack diameter | Carbon Monoxide | Other - CEMS | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 1.5 | PPM @ 15% O2 | 1-HR, DEMO LIMIT, W/O DUCT FIRING | BACT-PSD |  | N | 0 | U | 2 | PPM @ 15% O2 | 1-HR W/DUCT FIRING | 0 |  |  | 0 | 0 | N |  | During demonstration period, limit without duct firing is 2.0 ppm Mass Emission Limits: w/o duct firing: 7.8 lb/hr (10.4 lb/hr during demonstration period) w/ ducting firing: 11.3 lb/hr Startup/Shutdown Limits: Cold Start: 416 lb/event, 39 minutes Warm Start: 378 lb/event, 35 minutes Hot Start: 305 lb/event, 30 minutes Shutdown: 75.9 lb/event, 25 minutes NAAQS modeling-based limit: 419 lb/hr during SU/SD
IL-0133 | LINCOLN LAND ENERGY CENTER | LINCOLN LAND ENERGY CENTER (A/K/A EMBERCLEAR) | SANGAMON | IL | 62558 | USA | JIM PALUMBO | 888-582-4460 X 55 | JPALUMBO@EMBERCLEAR.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov |  | 18040008 | 4911 | 221112 | Not Found | 09/30/2021 &nbsp;ACT | 07/29/2022 &nbsp;ACT | 2022-08-26 | 2022-12-06 | A | www2.illinois.gov/epa/public-notices/boa-notices/pages/archive.aspx | The proposed facility is designed to generate baseload power. It will consist of two combined-cycle generating units, with each a Siemens combustion turbine (3,647 mmBtu/hr) and a heat recovery steam generator (HRSG) with duct burners (35 mmBtu/hr); fired by natural gas only. Other units at the facility include an auxiliary boiler, engines, piping and piping components, circuit breakers and roadways. | Additional facility-wide pollutants, in tons/year: PM10/PM 2.5: 131.7 and 131.6 (respectively); sulfuric acid mist (SAM): 17.2; greenhouse gasses (GHG): 3,586,918 | Combined-Cycle Combustion Turbines | 15.21 | Natural Gas | 3647 | mmBtu/hour | Combined-cycle comustion turbines and heat recovery steam generators (HRSG) with a 35 mmBtu/hr duct burner. Turbine inlets would have evaporative cooling systems to cool the inlet air during warm weather to increase power output. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practices | 1.5 | PPMV @ 15% O2 | TURBINE LOAD > OR = 60% W/O DUCT BURNERS | BACT-PSD |  | U | 0 | U | 1.8 | PPMV @ 15% O2 | TURBINE LOAD > OR= 60% WITH DUCT BURNERS | 0 |  |  | 0 | 0 | N |  | Emission Limits 1 and 2 are averaged on a rolling 3-operating hour basis. Emission Limit 3: 2.0 ppmv @ 15% O2 for turbine load < 60% on a rolling 3-operating hour operating basis. Emission Limits 1, 2 and 3 do not include startup, shutdown or breakdown. Emission Limit 4: During any clock hour, including startup, shutdown and breakdown, emissions shall not exceed 923 pounds/hour (cold start/shakedown); 325 pounds/hour (non-cold start); 216 pounds/hour (shutdown). Compliance is demonstrated using a continuous emissions monitoring system (CEMS).
PA-0333 | ESC TIOGA COUNTY POWER LLC/ELEC PWR GEN FAC | ESC TIOGA COUNTY POWER, LLC | TIOGA | PA | 16946 | USA | JOHN BLACK | 2129219239 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | SHELBI MEYNARD | (717)772-3968 | smeynard@pa.gov |  | 59-00034A | 4911 | 221112 | 110070395692 | 10/31/2017 &nbsp;ACT | 08/20/2019 &nbsp;ACT | 2023-02-03 | 2023-05-23 | A |  |  | This plan approval is for the construction and operation of a 635 Megawatt natural gas-fired combustion turbine power plant with ancillary equipment | COMBUSTION TURBINE/DUCT BURNER | 15.21 | Natural Gas | 4469 | MMBtu/Hr |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N |  | 1.5 | PPMVD | @ 15% O2 / 1 HR | BACT-PSD |  | U | 0 | U | 92.5 | TONS | 12 CMP | 0 |  |  | 0 | 0 | N
WI-0300 | NEMADJI TRAIL ENERGY CENTER | NEMADJI TRAIL ENERGY CENTER | DOUGLAS | WI | 54880 | USA |  |  |  | 5 | WI001 | WISCONSIN DEPT OF NATURAL RESOURCES; AIR MGMT. PROGRAM | MS. KRISTIN HART | (608)266-6876 | kristin.hart@wisconsin.gov |  | 18-MMC-168 | 4911 | 221121 | Not Found | 06/30/2020 &nbsp;ACT | 09/01/2020 &nbsp;ACT | 2022-06-27 | 2022-09-16 | A | https://dnr.wi.gov/cias/am/amexternal/AM_DownloadObject.aspx?id=1011796 | Natural gas-fired power plant |  | Natural-Gas-Fired Combined-Cycle Turbine (P01) | 15.21 | Natural Gas | 4671 | MMBTU/H | One Natural-Gas-Fired Siemens SGT6-8000 H Combined-Cycle Turbine with Natural Gas-Fired Duct Burner and Diesel Fuel Oil Back-Up [Maximum continuous rating: 4,671 MMBtu/hr higher heating value (HHV) when combusting natural gas, 4,027 MMBtu/hr, HHV when combusting diesel fuel oil], Selective Catalytic Reduction (SCR) (C01a) and Oxidation Catalyst (C01b) | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation Catalyst and good combustion controls | 1.5 | PPM AT 15% O2 | 168-HR ROLLING AVG., NATURAL GAS | BACT-PSD |  | U | 50 | U | 1.5 | PPM AT 15% O2 | 168-HR ROLLING AVG., DIESEL | 0 |  |  | 0 | 0 | N |  | *Except during start-up and shutdown
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | Siemens Combusion Turbine - Option 2 - Normal Operation | 15.21 | Natural Gas | 35000 | MMCF/YR | Option 2: Two on one configuration: 3,116 MMBtu/hr combustion turbine with 991 MMBtu/hr duct-fired HRSG. Emission limits reflect the operation of one turbine with or without duct firing. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst & good combustion practice | 1.8 | PPMVD @ 15% O2 | 3 H AV/WITH OR WITHOUT DB | BACT-PSD | NSPS , SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Alternative emission limits apply during tuning, water washing, startup and shutdown. CEMS required.
AK-0088 | LIQUEFACTION PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | KENAI PENNINSULA BOROUGH | AK | 99635 | USA | LISA HAAS |  | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - Permit Writer - dave.jones2@alaska.gov | AQ1539CPT01 | 4922 | 488999 | Not Found | 01/14/2020 &nbsp;ACT | 07/07/2022 &nbsp;ACT | 2022-08-04 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Liquefaction Plant is planned to encompass 921 acres, including 901 acres onshore for the liquefied natural gas (LNG) Plant as well as 20 acres offshore for the Marine Terminal. The Liquefaction Plant will be the terminus of an approximately 807-mile gas pipeline, allowing natural gas from Alaskaâ€™s North Slope to be shipped to outside markets. The stationary source will consist of structures and equipment associated with processing, storage, and loading of LNG. There will be three liquefaction trains combining to process up to approximately 20 million metric tons per annun of LNG. |  | Four Combined Cycle Gas-Fired Turbines | 15.21 | Natural Gas | 384 | MMBtu/hr | EUs 7 - 10 are combined cycle gas turbines used for power generation at LNG facility | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst and good combustion practices | 2 | PPMV @ 15% O2 | 3-HOURS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Allowed 40 hours per year per turbine of operation without SCR and OxCat.
IL-0129 | CPV THREE RIVERS ENERGY CENTER | CPV THREE RIVERS, LLC | GRUNDY | IL | 60450 | USA | MIKE BRUNO | 781-817-8972 | MBRUNO@CPV.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Illinois EPA, Bureau of Air Permit Section | 16060032 | 4911 | 221112 | Not Found | 06/10/2018 &nbsp;ACT | 07/30/2018 &nbsp;ACT | 2019-01-02 | 2019-02-19 | A |  | The proposed facility is designed to generate baseload power. It will consist of two combined-cycle generating units, each with a combustion turbine and associated heat recovery steam generator (HRSG). The turbines would burn natural gas and ultra-low sulfur diesel (ULSD) as a backup fuel. Other units include an auxiliary boiler, fuel heater, engines, natural gas piping and components, circuit breakers and roadways. |  | Combined Cycle Combustion Turbines | 15.21 | Natural Gas | 3474 | mmBtu/hr | Throughput of ultra-low sulfur diesel (ULSD) is 3798 mmBtu/hr. Combined cycle combustion turbines w/ heat recovery steam generator (HRSG). Turbine inlets will have inlet evaporative cooling systems to cool inlet air during warm weather to increase power output. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation catalyst | 2 | PPMV @ 15 % O2 | 3 OPERATING-HOUR, ROLLED HOURLY, AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emission Limit 1 is not applicable during periods of startup, shutdown, tuning and commissioning. Permit limits are as follows, applicable on a per-turbine basis: For natural gas: Without duct burner: 15.4 lb/hr With duct burner: 19.0 lb/hr For ULSD: 17.0 lb/hr For periods of startup, shutdown and commissioning: Extended startups using natural gas: 1522 lb/hr Commissioning and other than extended startups using natural gas: 204 lb/hr ULSD: 231 lb/hr For periods of tuning: Natural Gas: 204 lb/hr ULSD: 231 lb/hr Averaging period for the above permit limits is 3-hour average. Also see Condition 2.1.6(a)(iv) of the issued permit for operation during transitions.
IL-0130 | JACKSON ENERGY CENTER | JACKSON GENERATION, LLC | WILL | IL | 60421 | USA | JAMES KIEFER | 847-908-2833 | JKEIFER@POWERUSA.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov |  | 17040013 | 4911 | 221112 | Not Found | 04/04/2017 &nbsp;ACT | 12/31/2018 &nbsp;ACT | 2019-07-23 | 2020-04-16 | A |  | The proposed facility is designed to generate baseload power. It will consist of two combined-cycle generating units, each with a combustion turbine and associated heat recovery steam generator (HRSG). The turbines would only burn natural gas. Other units include an auxiliary boiler, fuel heater, emergency engines, natural gas piping and components, circuit breakers and roadways | Additional pollutants: Sulfuric Acid Mist: 48 tons/year; GHG as CO2e: 4,752,085 tons/year | Combined-Cycle Combustion Turbine | 15.21 | Natural Gas | 3864 | mmBtu/hr | Combined-cycle combustion turbines with heat recovery steam generator (HRSG). Turbines will have inlet evaporative cooling systems to cool inlet air during warm weather to increase power output. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation catalyst | 2 | PPMV | 3 OPERATING HOUR AVERAGE @ 15% O2 | BACT-PSD |  | U | 0 | U | 211.5 | PPMV | 3 OPERATING HOUR AVERAGE @ 15% O2 | 0 |  |  | 0 | 0 | N |  | Emission Limits 1 is applicable when operating with duct burner. Emission Limit 2 is applicable without the duct burner, after 36 months from initial operation. Pounds/hour limit without duct burner is 30.5, 3-hour average. Pounds/hour limit with duct burner is 33,9, 3-hour average. Emission Limits 1 and 2 and pounds/hour limits do not apply during startup/shutdown/commissioning and tuning. Pounds/hour limit for startup/shutdown/commissioning is 483.5. Pounds/hour limit for tuning is 239. Pounds/hour limit for period of very low load is 20.6
LA-0391 | MAGNOLIA POWER GENERATING STATION UNIT 1 | MAGNOLIA POWER LLC | IBERVILLE | LA | 70764 | USA | WILLIAM DAVIS | 609-250-7707 | LEE.DAVIS@KINDLE-ENERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Ms. Lori Pittman, (225)219-3180 | PSD-LA-839 | 4911 | 221112 | Not Found | 09/08/2020 &nbsp;ACT | 06/03/2022 &nbsp;ACT | 2023-03-02 | 2023-05-23 | A | https://edms.deq.louisiana.gov/app/doc/view?doc=13323738 | Magnolia Power LLC (Magnolia Power) is proposing to construct and operate a power plant, Magnolia Power Generating Station Unit 1, consisting of a natural gas-fired combined cycle gas turbine (CCGT Unit) in Iberville Parish, Louisiana. The CCGT Unit (EQT001), which includes a heat recovery steam generator (HRSG) equipped with duct burners, will have a predicted net nominal output of 730 megawatts (MW) |  | Combined Cycle Gas Turbine w/ Duct Burners and HRSG | 15.21 | Natural Gas | 5081 | mm BTU/h | Normal operating rate is 4930 MMBTU/h. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Catalytic oxidation and good combustion practices. | 2 | PPMVD | 24-HR ROLLING AVG BASED ON 1-HR AVG | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | BACT is 2.0 ppmvd @ 15% O2 on a 24-hour rolling average based on a one-hour average.
MI-0432 | NEW COVERT GENERATING FACILITY | NEW COVERT GENERATING COMPANY, LLC | VAN BUREN | MI | 49043 | USA | JOHN REESE | 212-792-0897 | JREESE@EASTERNGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 186-17 | 4911 | 221112 | Not Found | 04/17/2018 &nbsp;ACT | 07/30/2018 &nbsp;ACT | 2018-08-13 | 2019-02-19 | C |  | Power plant | The equipment consists of three advanced firing temperature Mitsubishi 501G combustion turbines, three heat recovery steam generators supplemented with gas-fired duct burners each with a max firing rate of 256 million British thermal units per hour (MMBtu/hr), three steam turbine generators. Auxiliary equipment includes three mechanical draft evaporative cooling towers, one natural gas auxiliary boiler, one diesel emergency generator, one diesel fire water pump, one aqueous parts cleaner, and one gas heater. | FG-TURB/DB1-3 (3 combined cycle combustion turbine and heat recovery steam generator trains) | 15.21 | Natural gas | 1230 | MW | Three (3) combined-cycle combustion turbine (CT) / heat recovery steam generator (HRSG) trains. Each CT is a natural gas fired Mitsubishi model 501G, equipped with dry low NOx combustor and inlet air evaporative cooling. Each HRSG includes a natural gas fired duct burner with a 256 MMBtu/hr heat input capacity and a dry low NOx burner. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst technology and good combustion practices. | 2 | PPMVD | EACH CT/HRSG TRAIN; 24-HR ROLL AVG | BACT-PSD | SIP | N | 0 | N | 357 | T/YR | EACH CT/HRSG TRAIN; 12-MO ROLL TIME PER. | 0 |  |  | 0 | 0 | N |  | Emission limits above are for each individual CT/HRSG train in FG-TURB/DB1-3. Startup/shutdown emissions are not included. They will be identified separately. Emission limit 1 above is 2.0 ppmvd at 15%O2 based on a 24-hour rolling average as determined each operating hour except during startup and shutdown. Emission limit 2 above is 357 ton/year based on a 12-month rolling time period as determined at the end of each calendar month.
MI-0442 | THOMAS TOWNSHIP ENERGY, LLC | THOMAS TOWNSHIP ENERGY, LLC | SAGINAW | MI | 48626-9409 | USA | DAN EWAN | 312-582-1504 | DEWAN@INVENERGYLLC.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions, please contact the permit engineer, Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you! | 210-18 | 4911 | 221112 | Not Found | 06/10/2019 &nbsp;ACT | 08/21/2019 &nbsp;ACT | 2019-11-18 | 2021-08-09 | A |  | New power plant | Thomas Township Energy is proposing to install two combustion turbine generators (CTG). Each CTG is connected to a heat recovery steam generator (HRSG), together referred to as a CTGHRSG. To reduce emissions of nitrogen oxides (NOx), the high-efficiency CTGHRSGs will be equipped with dry low-NOx burners and selective catalytic reduction (SCR). To reduce the emissions of carbon monoxide (CO) and volatile organic compounds (VOCs), each CTGHRSG will be equipped with an oxidation catalyst. | FGCTGHRSG | 15.21 | Natural gas | 625 | MW | Two (2) combined-cycle natural gas-fired combustion turbine generators (CTGs), each with a heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG). Each CTGHRSG has a combined nominal 625 MW electricity production (ISO) and a maximum combined heat input rating of 4,200 MMBTU/hr (HHV). Each HRSG is equipped with a natural gas-fired duct burner with a maximum rating of 560 MMBTU/hr (HHV) (ISO) to provide heat for additional steam production. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practices | 2 | PPM | PPMVD; EACH UNIT; 24-HR AVG, NO START/SH | BACT-PSD |  | N | 0 | U | 2106 | LB/H | HOURLY; INCLUD. START/SHUTDOWN; EACH | 0 |  |  | 0 | 0 | N |  | Emission Limit 1 is 2 ppmvd, applies to each unit, and is based on a 24-hour rolling average as determined each hour, except during startup and shutdown. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from teh lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the combustion process ends at flame-off. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in special condition (SC) III.2 of the permit. Emission Limit 2 is 2,106 lb/hour, applies to each unit, and is hourly including startup and shutdown. NSCR and EMxGT were ruled out as technically infeasible. A oxidation catalysts typically has a reduction of 85-90 percent for CO emissions.
MI-0451 | MEC NORTH, LLC | MARSHALL ENERGY CENTER, LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 9144682402 | WLADD@DEVELOPMENTSPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Janelle Trowhill, at 517-582-5312 or at TrowhillJ1@michigan.gov for technical questions regarding this permit. Thank you. | 167-17B | 4911 | 221112 | Not Found | 12/08/2021 &nbsp;ACT | 06/23/2022 &nbsp;ACT | 2022-12-21 | 2023-04-25 | A |  | Natural gas combined-cycle power plant (two plants: north and south). | The two plants (MEC North, LLC and MEC South, LLC) will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. | EUCTGHRSG (North Plant): A combined cycle natural gas fired combustion turbine generator with heat recovery steam generator | 15.21 | Natural gas | 3064 | MMBTU/H | Throughput Information: Nominal 500 MW electricity production. Turbine rating of 3,064 MMBTU/hr (HHV) and HRSG duct burner rating of 889 MMBTU/Hr (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,064 MMBTU/hr (HHV). The HRSG is equipped with a natural gas fired duct burner, with a maximum heat input rating of 889 MMBTU/hr (HHV) and rated at 874 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst technology and good combustion practices. | 2 | PPM | 24-HR ROLLING AVG | BACT-PSD |  | N | 0 | N | 788.6 | LB/H | OPERATING HR DURING STARTUP/SHUTDOWN | 0 |  |  | 0 | 0 | N |  | Emission limit 1 above is 2 ppmvd based on a 24-hour rolling average as determined each operating hour except during startup and shutdown. Emission limit 2 above is 788.6 lb/hr, operating hour during startup or shutdown. See below for further clarification on startup/shutdown. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in SC III.2. Startup and Shutdown hours are limited to 300 hours per 12 month rolling time period.
MI-0452 | MEC SOUTH, LLC | MARSHALL ENERGY CENTER, LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 9144682402 | WLADD@DEVELOPMENTSPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer, Janelle Trowhill at TrowhillJ1@michigan.gov or at 517-582-5312. Thank you. | 168-17B | 4911 | 221112 | Not Found | 12/08/2021 &nbsp;ACT | 06/23/2022 &nbsp;ACT | 2022-12-22 | 2023-04-25 | A |  | Natural gas combined cycle power plant (Two Plants: North and South) | The two plants (MEC North, LLC and MEC South, LLC) will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. | EUCTGHRSG (South Plant): A combined-cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 3064 | MMBTU/H | Nominal 500 MW electricity production. Turbine rating of 3064 MMBTU/H (HHV) and HRSG duct burner rating of 889 MMBTU/H (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,064 MMBTU/hr (HHV). The HRSG is equipped with a natural gas fired duct burner, with a maximum heat input rating of 889 MMBTU/hr (HHV) and rated at 874 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation Catalyst Technology and Good Combustion Practices | 2 | PPM | 24-HR ROLLING AVG | BACT-PSD | SIP | N | 0 | N | 788.6 | LB/H | OPERATING HR DURING STARTUP/SHUTDOWN | 0 |  |  | 0 | 0 | N |  | Emission limit 1 above = 2 ppmvd based on 24-hour rolling average as determined each operating hour, except during startup and shutdown. The applicable requirement is BACT. Emission limit 2 above = 788.6 lb/hr based on operating hour during startup or shutdown. The applicable requirement is BACT and NAAQS. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in SC III.2. Startup and Shutdown hours are limited to 300 hours per 12 month rolling time period.
MI-0455 | MIDLAND COGENERATION VENTURE LIMITED PARTNERSHIP | MIDLAND COGENERATION VENTURE LIMITED PARTNERSHIP | MIDLAND | MI | 46540 | USA | BRIAN VOKAL | 248-980-1139 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes at 517-648-6339 or at ByrnesM@michigan.gov. Thank you. | 2023-10-23 | 4911 | 221112 | Not found | 10/12/2022 &nbsp;ACT | 02/01/2023 &nbsp;ACT | 2023-05-15 | 2023-05-23 | B |  | Electric and steam generation |  | EUCTGHRSG1 | 15.21 | Natural gas | 4197.6 | MMBTU/H |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation catalyst | 2 | PPM | PPMVD AT 15%O2; 24-HR ROLL AVG EXC SU/SD | BACT-PSD |  | N | 90 | N | 24.2 | LB/H | HOURLY EXCEPT SU/SD | 0 |  |  | 0 | 0 | N |  | There are 3 CO emission limits listed below: Emission limit 1 = 2.0 ppmvd at 15% oxygen on a 24-hour rolling average, except during SU/SD. Emission limit 2 = 24.2 lb/hr on an hourly basis except during SU/SD. Emission limit 3 = 1486.0 lb/hr during SU/SD.
*PA-0319 | RENAISSANCE ENERGY CENTER | APV RENAISSANCE PARTNERS | GREENE | PA | 15320 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | SHELBI MEYNARD | (717)772-3968 | smeynard@pa.gov |  | 30-00235A | 4911 | 221112 | Not Found | 03/17/2017 &nbsp;ACT | 08/27/2018 &nbsp;ACT | 2019-03-26 | 2019-10-11 | U |  | This Plan Approval is to allow the construction and temporary operation of a natural gas-fired combined cycle power plant to be located in Monongahela Township, Greene County. with Two (2) Siemens, SGT6-8000H (or equivalent), natural gas-fired combustion turbines 3,580 MMBtu/hr heat input rating (LHV) each (controlled with low NOx burners), including natural gas-fired duct burners, 914.1 MMBtu/hr heat input rating each; controlled by Ultra-low NOx combustors, SCR, and oxidation catalysts; 1,127 MW total net generating capacity. One (1) natural gas-fired auxiliary boiler, 90 MMBtu/hr heat input rating. One (1) Cummins model #CFP15E-F20 (or equivalent), diesel-fired fire pump engine, 411 bhp rating; including One (1) diesel fuel storage tank, 2,175 gallons One (1) Caterpillar 3516 (or equivalent), diesel-fired emergency generator engine rated at 2000 kW. Miscellaneous components in natural gas service, and circuit breakers; controlled by leak detection and repair (â€œLDARâ€). One (1) aqueous ammonia (19%) storage vessel rated at 19,000 gallons (or as determined during final design). |  | COMBUSTION TURBINE UNIT w/o DUCT BURNERS UNIT | 15.21 | Natural Gas | 2665.9 | MMBtu/hr |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 2 | PPPDV | @15% O2 | BACT-PSD |  | U | 0 | U | 187.44 | TPY |  | 0 |  |  | 0 | 0 | N
*TN-0164 | TVA - JOHNSONVILLE COGENERATION | TENNESSEE VALLEY AUTHORITY | HUMPHREYS | TN | 37134 | USA | JACK BYARS | (423) 751-2666 | JGBYARS@TVA.GOV | 4 | TN001 | TENN.DEPT. OF ENVIRONMENT & CONSERVATION, DIV OF AIR POLLUTION CONTROL | LACEY HARDIN | (615) 532-0545 | Lacey.Hardin@tn.gov |  | 972969 | 4911 | 221112 | 110070502905 | 09/26/2017 &nbsp;ACT | 02/01/2018 &nbsp;ACT | 2019-03-21 | 2019-03-21 | D |  | Combustion turbines and combined cycle plant | Permit 972969 adds startup and shutdown limits to the requirements established in PSD permit 970816F. | Dual-fuel CT and HRSG with duct burner | 15.21 | Natural Gas | 1020 | MMBtu/hr | Rated input capacity is 1020 MMBtu/hr (CT) and 319 MMBtu/hr (duct burner) when burning natural gas and 1084 MMBtu/hr when burning #2 oil. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst, good combustion design & practice | 2 | PPMVD @ 15% O2 | 30-DAY AVG WHEN BURNING NATURAL GAS | BACT-PSD |  | N | 0 | U | 10 | PPMVD @ 15% O2 | 30-DAY AVG WHEN BURNING #2 OIL | 0 |  |  | 0 | 0 | N |  | Startup & Shutdown: 1,760 lb/startup and 22 lb/shutdown when firing natural gas; 3,000 lb/startup and 12.8 lb/shutdown when firing #2 oil
TX-0834 | MONTGOMERY COUNTY POWER STATIOIN | ENTERGY TEXAS INC | MONTGOMERY | TX |  | USA | CHRISTOPHER BURKE | 281-297-3369 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., 512-239-2175 laura.gibson@tceq.texas.gov | N256, PSDTX1510, AND GHGPSDTX1 | 4911 | 221112 | Not Found | 01/18/2018 &nbsp;ACT | 03/30/2018 &nbsp;ACT | 2018-04-26 | 2019-02-19 | A |  |  |  | Combined Cycle Turbine | 15.21 | NATURAL GAS | 2635 | MMBTU/HR/UNIT | Two Mitsubishi M501GAC turbines (without fast start) | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST | 2 | PPMVD | 15% O2 3 HOUR AVERAGE | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK & TTTT, MACT YYYY
TX-0939 | ORANGE COUNTY ADVANCED POWER STATION | ENTERGY TEXAS, INC. | ORANGE | TX |  | USA | JASON WILLIS | 281-297-1937 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Huy Pham, (512) 239-1358, Huy.Pham@tceq.texas.gov | 166032 PSDTX1598 GHGPSDTX210 | 4911 | 221122 | Not found | 06/06/2022 &nbsp;ACT | 03/13/2023 &nbsp;ACT | 2022-06-06 | 2023-05-23 | A |  | Entergy Texas, Inc. proposes construction of a power plant consisting of two natural gas-fired combined cycle turbines with a maximum total nominal output of 1,215 MW. The turbines can also be fired with up to 30% volume hydrogen co-firing (blended fuel). Emergency engines, a cooling tower, storage tanks, and maintenance activities support operation of the turbines. |  | Combined Cycle Turbines | 15.21 | NATURAL GAS | 1215 | MW | 2 Mitsubishi M501JAC combustion turbines 1,215 MW (in a 2x1 configuration) output and 6,762 Btu/kW-hr (with a 9% degradation) gross heat rate. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation Catalyst and good combustion practices | 2 | PPMVD | 15% O2 24-HR AVERAGE | BACT-PSD | NSPS , MACT | N | 0 | U | 2.4 | PPMVD | 15% O2 ON HOURLY AVERAGE | 0 |  |  | 0 | 0 | N
*VA-0335 | PANDA STONEWALL LLC | PANDA STONEWALL LLC | LOUDOUN | VA | 20175 | USA | MARK KKAN | (703) 779-4101 |  | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Mr. Ali Khalilzadeh by phone at (703) 583-3839 or by e-mail: Alireza.Khalilzadeh@deq.virginia.gov | 73826-6 | 4911 | 221112 | 110041353 | &nbsp; | 12/18/2020 &nbsp;ACT | 2021-03-29 | 2022-09-12 | U |  | Panda Stonewall, LLC (Panda) is a combined-cycle electric power generating facility in Loudoun County with a nominal generating capacity increased from 778 to 802 megawatts (MW) â€œgrossâ€ at ISO (International Organization for Standardization) conditions (which is at 15 C or 59 F, 60% relative humidity, and 1 atmosphere or 14.7 psia pressure). The facility is a fossil fuel-fired steam electric plant of more than 250 million British thermal units (MMBtu) heat input capacity, and is located in an ozone nonattainment area. | The original permit dated April 30, 2013 (amended 5/31/2013, 6/11/2014 & 7/15/2014) allowed for either of two alternative combined cycle combustion turbine manufacturers â€“ General Electric or Siemens. The permittee selected the Siemens SGT6-5000F5 combustion turbines. The turbine manufacturer, Siemens, has increased the maximum shaft torque limit between the combustion turbine and the generator that allows for increased gross power output of the SGT6-5000F5 units. The gross power output rating on each combustion turbine generator has increased from 232 megawatt (MW) to 242 MW. This change in output equates to an increase in its maximum fuel heat input rate from 2,276 million British thermal units (MMBtu/hr) to 2,450 MMBtu/hr. This change does not alter the air pollutant concentration (ppm) in the flue gas or the emission factor (in lb/MMBtu) that represent Lowest Achievable Emission Rate (LAER) for NOx and VOC, and Best Available Control Technology (BACT) for CO, CO2, PM-10 and other pollutants, which are state and federally enforceable due to conditions established in the April 30, 2013 permit. The increase in the maximum fuel firing rate results in corresponding increase in lb/hr emission limits (except for PM-10/PM-2.5). This permit increases the two duct burner hours of operation limitations from 1,400 hours/year (each) to 8,760 hours/year (each). This permit also includes installation of ancillary equipment with lower rated capacities than initially permitted and requested updates to the permit for the changes with corresponding lower emissions. | Combustion Turbines, Two (2) and HRSG Duct Burners | 15.21 | Natural Gas | 2.55 | MMBTU/H | 2x1 natural gas-only configuration: Two Siemens SGT6-5000F5 CTs at 2554 MMBtu/hr and two 430 MMBtu/hr duct burners | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Catalytic Oxidizer | 2 | PPMVD @ 15% O2 | NORMAL OPERATION W & W/O DUCT BURNING | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emission Limit 1: 2.0 ppmvd at 15% O2 - normal operations with and w/o duct burner Emission Limit 2: 1900/1700/1200/85 lb/event - cold start/warm start/hot start/shutdown
*WV-0033 | MAIDSVILLE | MOUNTAIN STATE CLEAN ENERGY, LLC | MONONGALIA | WV | 26541 | USA | BRIAN HOYT | 304-559-0930 X2203 | BHOYT@LONGVIEWPOWER.NET | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Mr. Ed Andrews edward.s.andrews@wv.gov | R14-0038 | 4911 | 221112 | 054-061-00134 | 05/05/2020 &nbsp;ACT | 01/05/2022 &nbsp;ACT | 2022-04-01 | 2022-06-28 | U | https://dep.wv.gov/daq/permitting/Pages/NSR-Permit-Applications.aspx | This project consist of constructing two combined cycle combustion turbine with duct burners, two fuel gas heaters, two emergency engines (emergency generator and fire water pump), and cooling tower. The configuration of these combustion turbines with heat recovery steam generators will be a 2X1. This facility will be co-located next to existing EGU (Longview Power LLC). The CCCTs with duct burners and fuel gas heaters will operate only on natural gas. Both emergency engines will be diesel fired units. | A bi-direction steam line between the Mountain State Clean Energy and Longview Power will be use to provide startup steam in lieu of a auxiliary boiler. No limits on operating hours or fuel use for the duct burners. Applicant proposed two different model combustion turbine (GE 7HA.03 and MHPS M501JAC). Gross Generation for the facility is 1275 MWh. | Combustion Turbine &amp; Duct Burner (CT-01/HRSG1 &amp; CT-02/HRSG2) | 15.21 | Pipeline Natural Gas | 1275 | mw | CT - 3,875 MMBtu/hr DB - 586 MMBtu/hr Gross Generation - 1275 MW | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Good Combustion Practices and OxCat | 2 | PPMDV @ 15% O2 | 3-HOUR BLOCK AVERAGE | BACT-PSD | N/A | N | 0 | U | 19.54 | LB/HR | 3-HOUR ROLLING AVERAGE | 0 |  |  | 0 | 0 | N |  | Concentration and Mass limits apply at all times excluding startup and shutdown events.
*WV-0033 | MAIDSVILLE | MOUNTAIN STATE CLEAN ENERGY, LLC | MONONGALIA | WV | 26541 | USA | BRIAN HOYT | 304-559-0930 X2203 | BHOYT@LONGVIEWPOWER.NET | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Mr. Ed Andrews edward.s.andrews@wv.gov | R14-0038 | 4911 | 221112 | 054-061-00134 | 05/05/2020 &nbsp;ACT | 01/05/2022 &nbsp;ACT | 2022-04-01 | 2022-06-28 | U | https://dep.wv.gov/daq/permitting/Pages/NSR-Permit-Applications.aspx | This project consist of constructing two combined cycle combustion turbine with duct burners, two fuel gas heaters, two emergency engines (emergency generator and fire water pump), and cooling tower. The configuration of these combustion turbines with heat recovery steam generators will be a 2X1. This facility will be co-located next to existing EGU (Longview Power LLC). The CCCTs with duct burners and fuel gas heaters will operate only on natural gas. Both emergency engines will be diesel fired units. | A bi-direction steam line between the Mountain State Clean Energy and Longview Power will be use to provide startup steam in lieu of a auxiliary boiler. No limits on operating hours or fuel use for the duct burners. Applicant proposed two different model combustion turbine (GE 7HA.03 and MHPS M501JAC). Gross Generation for the facility is 1275 MWh. | Combustion Turbine &amp; Duct Burner (CT-01/HRSG1 &amp; CT-02/HRSG2) | 15.21 | Pipeline Natural Gas | 1275 | mw | CT - 3,875 MMBtu/hr DB - 586 MMBtu/hr Gross Generation - 1275 MW | Carbon Monoxide | Other - Part 60 CEMs | (InOrganic Compounds) | 630-08-0 | B | Good Combustion Practices and Oxidation catalyst | 2 | PPMDV @ 15% O2 | 3-HOUR BLOCK AVERAGE | BACT-PSD | N/A | N | 0 | U | 20.76 | LB/HR | 3-HOUR ROLLING AVERAGE | 0 |  |  | 0 | 0 | N |  | Concentration and Mass limits apply at all times excluding startup and shutdown events.
*LA-0365 | BIG CAJUN I POWER PLANT | LOUISIANA GENERATING, LLC | POINTE COUPEE | LA | 70749 | USA | JACK LOWERY | 2256184860 | JACK.LOWERY@CLECOCAJUN.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mr. Christopher Smith (225) 219-3439 | PSD-LA-660(M-3) | 4911 | 221112 | 110010565067 | 11/06/2017 &nbsp;ACT | 06/27/2019 &nbsp;ACT | 2020-06-09 | 2021-04-01 | C |  | Electric power generating station using two natural gas fed turbines (120 MW each) |  | Combustion Turbine #1 (EQT0002, CTG-1) | 15.21 | Natural Gas | 1679 | MM BTU/hr |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Dry low NOX Burners & water injection | 23 | PPMV | THREE HOUR ROLLING AVERAGE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 171.4 | LB/HR | HOURLY MAXIMUM | 0 |  |  | 0 | 0 | N |  | Annual Maximum = 175.40 TPY NOX. All PPMV measurements are corrected to 15% oxygen. PPMV limits apply when unit operates at greater than or equal to 70 Megawatt (MW). These limits are not applicable during any clock hour in which the unit operates at a load less than 70 MW.
*LA-0365 | BIG CAJUN I POWER PLANT | LOUISIANA GENERATING, LLC | POINTE COUPEE | LA | 70749 | USA | JACK LOWERY | 2256184860 | JACK.LOWERY@CLECOCAJUN.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mr. Christopher Smith (225) 219-3439 | PSD-LA-660(M-3) | 4911 | 221112 | 110010565067 | 11/06/2017 &nbsp;ACT | 06/27/2019 &nbsp;ACT | 2020-06-09 | 2021-04-01 | C |  | Electric power generating station using two natural gas fed turbines (120 MW each) |  | Combustion Turbine #2 (EQT0003, CTG-2) | 15.21 | Natural Gas | 1679 | MM BTU/hr |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Dry low NOX burners & water injection | 23 | PPMV | THREE HOUR ROLLING AVERAGE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 171.4 | LB/HR | HOURLY MAXIMUM | 0 |  |  | 0 | 0 | N |  | Annual Maximum = 175.40 TPY NOX. All PPMV measurements are corrected to 15% oxygen. PPMV limits apply when unit operates at greater than or equal to 70 Megawatt (MW). These limits are not applicable during any clock hour in which the unit operates at a load less than 70 MW.
*MI-0445 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact Mark Mitchell at 517-582-5293 or at mitchellm7@michigan.gov. Thank you. | 75-16B | 4911 | 221112 | Not found | 08/20/2019 &nbsp;ACT | 11/26/2019 &nbsp;ACT | 2020-12-22 | 2020-12-23 | A |  | Natural gas combined cycle power plant |  | FGCTGHRSG | 15.21 | Natural gas | 3421 | MMBTU/H | 3421 MMBTU/H for each turbine 740 MMBTU/H for each duct burner for a combined throughput of 4161 MMBTU/H or 8322 MMBTU/H for both trains. Two combined-cycle natural gas-fired combustion turbine generators (CTGs) with Heat Recovery Steam Generators (HRSG) (EUCTGHRSG1 & EUCTGHRSG2 in FGCTGHRSG). The total hours for startup and shutdown for each train shall not exceed 500 hours per 12-month rolling time period. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR with DLNB (Selective Catalytic Reduction with Dry Low NOx Burners) | 2 | PPM | PPMVD @15% O2. 24HR ROLL AVG EXCEPT SS | BACT-PSD | NSPS | N | 80 | N | 15 | PPM | 30 DAY ROLL AVG DET. EACH OPERATING DAY | 0 |  |  | 0 | 0 | N |  | There are 4 emission limits for EACH CTGHRSG within FGCTGHRSG as follows: Emission Limit 1 = 2 ppmvd at 15%O2 based on a 24-hour rolling average as determined each operating hour, except during startup/shutdown (SS). Emission Limit 2 = 15 ppmvd at 15%O2 based on a 30-day rolling average as determined each operating day. Emission Limit 3 = 27.4 lb/h based on a 24-hour rolling average as determined each operating hour, except during startup/shutdown (SS). Emission Limit 4 = 286 lb/h based on each operating hour during startup or shutdown. Startup and shutdown operations are limited to 500 hours per 12-month rolling time period for each CTGHRSG train. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the startup and shutdown emission minimization plan. The efficiency range is 80-90 percent.
*TN-0164 | TVA - JOHNSONVILLE COGENERATION | TENNESSEE VALLEY AUTHORITY | HUMPHREYS | TN | 37134 | USA | JACK BYARS | (423) 751-2666 | JGBYARS@TVA.GOV | 4 | TN001 | TENN.DEPT. OF ENVIRONMENT & CONSERVATION, DIV OF AIR POLLUTION CONTROL | LACEY HARDIN | (615) 532-0545 | Lacey.Hardin@tn.gov |  | 972969 | 4911 | 221112 | 110070502905 | 09/26/2017 &nbsp;ACT | 02/01/2018 &nbsp;ACT | 2019-03-21 | 2019-03-21 | D |  | Combustion turbines and combined cycle plant | Permit 972969 adds startup and shutdown limits to the requirements established in PSD permit 970816F. | Dual-fuel CT and HRSG with duct burner | 15.21 | Natural Gas | 1020 | MMBtu/hr | Rated input capacity is 1020 MMBtu/hr (CT) and 319 MMBtu/hr (duct burner) when burning natural gas and 1084 MMBtu/hr when burning #2 oil. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | SCR, good combustion design & practices | 2 | PPMVD @ 15% O2 | 30-DAY AVG WHEN BURNING NATURAL GAS | BACT-PSD | NSPS | N | 0 | U | 8 | PPMVD @ 15% O2 | 30-DAY AVG WHEN BURNING #2 OIL | 0 |  |  | 0 | 0 | N |  | BACT limits exclude startup and shutdown. NSPS KKKK limits apply to NOX emissions during startup and shutdown
*WV-0029 | HARRISON COUNTY POWER PLANT | ESC HARRISON COUNTY POWER, LLC | HARRISON | WV | 26301 | USA | ANDREW DORN | 7163121042 | DREWDORN@ENSOLCONSORTIUM.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Engineer: Mr. Steve Pursley 304-926-0499 x1218 steven.r.pursley@wv.gov | R14-0036 | 4911 | 221112 | Not Found | 04/26/2017 &nbsp;ACT | 03/27/2018 &nbsp;ACT | 2018-06-25 | 2022-06-28 | A | https://dep.wv.gov/daq/Documents/March 2018 Permits and Evals/033-00264_PERM_R14-0036.pdf | Nominal 640 mWe natural gas-fired combined-cycle power plant. Small sources: Emergency Generator, Fire Water Pump, Fuel Gas Heater not included in RBLC - may request info or see permit for details. |  | GE 7HA.02 Turbine | 15.21 | Natural Gas | 3496.2 | mmBtu/hr | Nominal 640 mWe All emission limits steady-state and include 1000 mmBtu/hr Duct Burner in operation Short Term startup and shutdown limits in lb/event given in permit. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry-Low NOx Burners, SCR | 32.9 | LB/HR | 1-HOUR AVERAGE | BACT-PSD | NSPS | U | 0 | U | 156.2 | TONS/YEAR |  | 2 | PPM |  | 0 | 0 | N
*WV-0032 | BROOKE COUNTY POWER PLANT | ESC BROOKE COUNTY POWER I, LLC | BROOKE | WV | 26035 | USA | ANDREW DORN | 7163121042 | DREW.DORN@ENSOLCONSORTIUM.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Engineer: Mr. Steve Pursley 304-926-0499 x1218 Steven.R.Pursley@wv.gov | R14-0035 | 4911 | 221112 | Not Found | 03/30/2018 &nbsp;ACT | 09/18/2018 &nbsp;ACT | 2018-12-20 | 2022-06-28 | A |  | Nominal 925 mWe natural gas-fired combined-cycle power plant. Small sources: Emergency Generator, Fire Water Pump, Fuel Gas Heater not included in RBLC - may request info or see permit for details. |  | GE 7HA.01 Turbine | 15.21 | Natural Gas/Ethane | 2737.7 | mmBtu/hr | Facility has 2 identical units, only 1 entry in RBLC. Nominal 462.5 mWe. All emission limits steady-state and include 424 mmBtu/hr Duct Burner in operation. Short Term startup and shutdown limits in lb/event given in permit. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry-Low NOx Burners, SCR | 23.2 | LB/HR |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 2 | PPM |  | 0 | 0 | N
*WV-0033 | MAIDSVILLE | MOUNTAIN STATE CLEAN ENERGY, LLC | MONONGALIA | WV | 26541 | USA | BRIAN HOYT | 304-559-0930 X2203 | BHOYT@LONGVIEWPOWER.NET | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Mr. Ed Andrews edward.s.andrews@wv.gov | R14-0038 | 4911 | 221112 | 054-061-00134 | 05/05/2020 &nbsp;ACT | 01/05/2022 &nbsp;ACT | 2022-04-01 | 2022-06-28 | U | https://dep.wv.gov/daq/permitting/Pages/NSR-Permit-Applications.aspx | This project consist of constructing two combined cycle combustion turbine with duct burners, two fuel gas heaters, two emergency engines (emergency generator and fire water pump), and cooling tower. The configuration of these combustion turbines with heat recovery steam generators will be a 2X1. This facility will be co-located next to existing EGU (Longview Power LLC). The CCCTs with duct burners and fuel gas heaters will operate only on natural gas. Both emergency engines will be diesel fired units. | A bi-direction steam line between the Mountain State Clean Energy and Longview Power will be use to provide startup steam in lieu of a auxiliary boiler. No limits on operating hours or fuel use for the duct burners. Applicant proposed two different model combustion turbine (GE 7HA.03 and MHPS M501JAC). Gross Generation for the facility is 1275 MWh. | Combustion Turbine &amp; Duct Burner (CT-01/HRSG1 &amp; CT-02/HRSG2) | 15.21 | Pipeline Natural Gas | 1275 | mw | CT - 3,875 MMBtu/hr DB - 586 MMBtu/hr Gross Generation - 1275 MW | Nitrogen Oxides (NOx) | Other - Part 75 CEMs | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry Low NOx Combustion w/ SCR | 2 | PPMDV @ 15% O2 | 3-HOUR ROLLING AVERAGE | BACT-PSD | NSPS | U | 0 | U | 32.09 | LB/HR | 3-HOUR ROLLING AVERAGE | 0.43 | LB/MWH GROSS | 30 OPERATING DAY ROLLING AVG. | 0 | 0 | N |  | Concentration and Mass limits apply at all times excluding startup and shutdown events.
*WV-0033 | MAIDSVILLE | MOUNTAIN STATE CLEAN ENERGY, LLC | MONONGALIA | WV | 26541 | USA | BRIAN HOYT | 304-559-0930 X2203 | BHOYT@LONGVIEWPOWER.NET | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Mr. Ed Andrews edward.s.andrews@wv.gov | R14-0038 | 4911 | 221112 | 054-061-00134 | 05/05/2020 &nbsp;ACT | 01/05/2022 &nbsp;ACT | 2022-04-01 | 2022-06-28 | U | https://dep.wv.gov/daq/permitting/Pages/NSR-Permit-Applications.aspx | This project consist of constructing two combined cycle combustion turbine with duct burners, two fuel gas heaters, two emergency engines (emergency generator and fire water pump), and cooling tower. The configuration of these combustion turbines with heat recovery steam generators will be a 2X1. This facility will be co-located next to existing EGU (Longview Power LLC). The CCCTs with duct burners and fuel gas heaters will operate only on natural gas. Both emergency engines will be diesel fired units. | A bi-direction steam line between the Mountain State Clean Energy and Longview Power will be use to provide startup steam in lieu of a auxiliary boiler. No limits on operating hours or fuel use for the duct burners. Applicant proposed two different model combustion turbine (GE 7HA.03 and MHPS M501JAC). Gross Generation for the facility is 1275 MWh. | Combustion Turbine &amp; Duct Burner (CT-01/HRSG1 &amp; CT-02/HRSG2) | 15.21 | Pipeline Natural Gas | 1275 | mw | CT - 3,875 MMBtu/hr DB - 586 MMBtu/hr Gross Generation - 1275 MW | Nitrogen Oxides (NOx) | Other - Part 75 CEMs | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry Low NOx Combustor with SCR | 2 | PPMDV @ 15% O2 | 3-HOUR ROLLING AVERAGE | BACT-PSD | NSPS | N | 97 | U | 34.09 | LB/HR | 3-HOUR ROLLING AVERAGE | 0.43 | LB/MWH GROSS | 30 OPERATING DAY ROLLING AVG. | 0 | 0 | N |  | Concentration and Mass limits apply at all times excluding startup and shutdown events.
AK-0085 | GAS TREATMENT PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | NORTH SLOPE BOROUGH | AK | 99734 | USA | LISA HAAS | 907.947.9353 | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - 907.465.5122 - dave.jones2@alaska.gov | AQ1524CPT01 | 4922 | 486210 | None Found | 01/25/2019 &nbsp;ACT | 08/13/2020 &nbsp;ACT | 2020-08-14 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Gas Treatment Plant (GTP) is part of one integrated liquefied natural gas (LNG) project to bring natural gas from Alaskaâ€™s North Slope to international markets in the form of LNG, as well as for in-state deliveries in the form of natural gas. The GTP will take gas from the Prudhoe Bay Unit and the Point Thomson Unit and treat/process the gas, before it is sent 807 miles through a 42-inch diameter pipeline to a liquefaction facility in Nikiski on Alaskaâ€™s Kenai Peninsula for export in foreign commerce. The emissions units at the stationary source will include cogeneration gas-fired turbines with supplemental firing duct burners for gas compression, simple cycle gas-fired turbines for power generation, gas-fired heaters for building and process heat, as well as flares for control of excess gas. In addition, the GTP will include a diesel-fired black start generator, several diesel-fired firewater pumps and emergency generators, and storage tanks for diesel and gasoline fuels. |  | Six (6) Cogeneration Gas-Fired Turbines (Treated Gas Compressor Turbines) | 15.21 | Natural Gas | 576 | MMBtu/hr | 576 MMBtu/hr includes turbine and supplemental duct burner for waste heat recovery unit for cogeneration. EUs 1-6, Treat Gas Compressor Turbines. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | DLN combustors and Good Combustion Practices | 17 | PPMV @ 15% O2 | 3-HOUR AVERAGE | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Potential NOx emissions of 105.24 tpy for each cogeneration turbine including supplemental firing duct burner for WHRU.
AK-0085 | GAS TREATMENT PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | NORTH SLOPE BOROUGH | AK | 99734 | USA | LISA HAAS | 907.947.9353 | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - 907.465.5122 - dave.jones2@alaska.gov | AQ1524CPT01 | 4922 | 486210 | None Found | 01/25/2019 &nbsp;ACT | 08/13/2020 &nbsp;ACT | 2020-08-14 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Gas Treatment Plant (GTP) is part of one integrated liquefied natural gas (LNG) project to bring natural gas from Alaskaâ€™s North Slope to international markets in the form of LNG, as well as for in-state deliveries in the form of natural gas. The GTP will take gas from the Prudhoe Bay Unit and the Point Thomson Unit and treat/process the gas, before it is sent 807 miles through a 42-inch diameter pipeline to a liquefaction facility in Nikiski on Alaskaâ€™s Kenai Peninsula for export in foreign commerce. The emissions units at the stationary source will include cogeneration gas-fired turbines with supplemental firing duct burners for gas compression, simple cycle gas-fired turbines for power generation, gas-fired heaters for building and process heat, as well as flares for control of excess gas. In addition, the GTP will include a diesel-fired black start generator, several diesel-fired firewater pumps and emergency generators, and storage tanks for diesel and gasoline fuels. |  | Six (6) Cogeneration Gas-Fired Turbines (CO2 Compressor Turbines)) | 15.21 | Natural Gas | 431 | MMBtu/hr | 431 MMBtu/hr includes turbine and supplemental duct burner for waste heat recovery unit for cogeneration. EUs 7-12, CO2 Compressor Turbines. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | DLN combustors and good combustion practices | 17 | PPMV @ 15% O2 | 3-HOUR AVERAGE | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Potential NOx emissions of 80.46 tpy for each cogeneration turbine including supplemental firing duct burner for WHRU.
AK-0088 | LIQUEFACTION PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | KENAI PENNINSULA BOROUGH | AK | 99635 | USA | LISA HAAS |  | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - Permit Writer - dave.jones2@alaska.gov | AQ1539CPT01 | 4922 | 488999 | Not Found | 01/14/2020 &nbsp;ACT | 07/07/2022 &nbsp;ACT | 2022-08-04 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Liquefaction Plant is planned to encompass 921 acres, including 901 acres onshore for the liquefied natural gas (LNG) Plant as well as 20 acres offshore for the Marine Terminal. The Liquefaction Plant will be the terminus of an approximately 807-mile gas pipeline, allowing natural gas from Alaskaâ€™s North Slope to be shipped to outside markets. The stationary source will consist of structures and equipment associated with processing, storage, and loading of LNG. There will be three liquefaction trains combining to process up to approximately 20 million metric tons per annun of LNG. |  | Four Combined Cycle Gas-Fired Turbines | 15.21 | Natural Gas | 384 | MMBtu/hr | EUs 7 - 10 are combined cycle gas turbines used for power generation at LNG facility | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR, DLN combustors, and good combustion practices | 2 | PPMV @ 15% O2 | 3-HOURS | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Allowed 40 hours per year per turbine of operation without SCR and OxCat.
AL-0328 | PLANT BARRY | ALABAMA POWER COMPANY | MOBILE | AL | 36512 | USA | TYLER PHILLIPS |  | TYLER.PHILLIPS@ADEM.ALABAMA.GOV | 4 | AL001 | ALABAMA DEPT OF ENVIRONMENTAL MGMT | MR. DALE HURST | (334) 271-7882 | ADH@ADEM.STATE.AL.US |  | 503-1001 | 4911 | 221112 | 110000741270 | 05/01/2020 &nbsp;ACT | 11/09/2020 &nbsp;ACT | 2021-09-30 | 2022-03-04 | B |  |  |  | Two 744 MW Combined Cycle Units | 15.21 | Natural Gas | 744 | MW |  | Nitrogen Oxides (NOx) | Other - CEMS | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 2 | PPM | 3 HOUR AVG / @15% O2 | BACT-PSD | NSPS , SIP , OPERATING PERMIT | U | 0 | N | 39.1 | LB/HR | 3 HOUR AVG | 0 |  |  | 0 | 0 | N
CA-1251 | PALMDALE ENERGY PROJECT | PALMDALE ENERGY, LLC | LOS ANGELES | CA | 93551 | USA | TOM CAMERON |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov | Staff Contact: Lisa Beckham beckham.lisa@epa.gov (415) 972-3811 | SE 17-01 | 4911 | 221122 | Not Found | 08/16/2017 &nbsp;ACT | 04/25/2018 &nbsp;ACT | 2018-10-25 | 2020-01-31 | A | https://www.epa.gov/caa-permitting/palmdale-energy-project-prevention-significant-deterioration-psd-permit | 645 MW (nominal) Natural Gas-fired Combined Cycle Power Plant, 2 x 1 configuration, auxiliary boiler for faster startup | See also docket: https://www.regulations.gov/docket?D=EPA-R09-OAR-2017-0473. Permit decision was appealed to EPA's Environmental Appeals Board. Board denied review on October 23, 2018. Information available through www.epa.gov/eab and https://yosemite.epa.gov/oa/EAB_Web_Docket.nsf/f22b4b245fab46c6852570e6004df1bd/ad735c0b822500258525829d004217eb!OpenDocument. 1/31/20 -- SYS MGR -- Link to permit is <https://www.regulations.gov/document?D=EPA-R09-OAR-2017-0473-0028> | Combustion Turbines (GEN1 and GEN2) | 15.21 | Natural Gas | 2217 | MMBTU/H | Each combustion turbine rated at 214 MW, with a maximum heat input rate of 2,217 MMBtu/H (HHV, at ISO conditions); natural gas-fired Siemens SGT6-5000F; each vents to dedicated Heat Recovery Steam Generator and a shared 276 MW Steam Turbine Generator; 160-ft stack height; 22-ft stack diameter | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction, Dry Low NOx Burners | 2 | PPM @ 15% O2 | 1-HOUR | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Mass Emission Limits During Normal Operation: 18.5 lb/hr with duct burner (1-hr average) 17.1 lb/hr without duct burner (1-hr average) Startup and Shutdown Limits: Cold Start: 51.5 lb/event, 39 minutes Warm Start: 46.8 lb/event, 35 minutes Hot Start: 43.2 lb/event, 30 minutes Shutdown: 33.0 lb/event, 25 minutes Startup/Shutdown: 53.6 lb/hr (1-hr average) (used in modeling analysis)
FL-0367 | SHADY HILLS COMBINED CYCLE FACILITY | SHADY HILLS ENERGY CENTER, LLC | PASCO | FL | 36410 | USA | ROY BELDEN | (203) 357-6820 | ROY.BELDEN@GE.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 1010524-001-AC | 4911 | 221112 | 110012581820 | 02/16/2018 &nbsp;ACT | 07/27/2018 &nbsp;ACT | 2019-03-19 | 2022-03-04 | B | https://arm-permit2k.dep.state.fl.us/nontv/1010524.001.AC.F.ZIP | A 573-megawatt (MW) (winter) 1-on-1 combined cycle plant which includes a heat recovery steam generator with duct firing, along with supporting equipment. Natural gas is the only permitted fuel for the combined cycle unit. | THIS PROJECT WAS SUPERSEDED BY PERMIT NO. 1010524-003-AC UNDER RBLC ID FL-0371 | 1-on-1 combined cycle unit (GE 7HA) | 15.21 | Natural Gas | 3266.9 | MMBtu/hour | One nominal 385 MW GE 7HA.02 CTG and one HRSG with duct firing [approximately 210 MMBtu/hour], and one nominal 210 MW steam turbine generator (STG) | Nitrogen Oxides (NOx) | Other - Continous Emissions Monitoring System | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry low-NOX combustors and Selective Catalytic Reduction (SCR) | 2 | PPMVD AT 15% O2 | 24-HOUR BLOCK AVERAGE BASIS (BACT) | BACT-PSD | NSPS , SIP , OTHER | U | 0 | U | 15 | PPMVD AT 15% O2 | 30-OPERATING-DAY ROLLING AVG. (NSPS) | 0 |  |  | 0 | 0 | N |  | 2nd Limit of 15 ppmvd @ 15% O2 (for turbine loads â‰¥ 75%), 30-operating-day rolling avg. (NSPS Subpart KKKK) 3rd Limit: 96 ppmvd @15% O2 (for turbine loads < 75%), 30-operating-day rolling avg. (NSPS Subpart KKKK)
FL-0371 | SHADY HILLS COMBINED CYCLE FACILITY | SHADY HILLS ENERGY CENTER, LLC | PASCO | FL | 34610 | USA | ROY BELDEN |  | ROY.BELDEN@GE.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 1010524-003-AC (PSD-FL-444A) | 4911 | 221112 | 110012581820 | 04/02/2021 &nbsp;ACT | 06/07/2021 &nbsp;ACT | 2021-11-19 | 2022-03-04 | U | https://depedms.dep.state.fl.us:443/Oculus/servlet/shell?command=hitlist&[freeText=]&[folderName=]&[profile=Permitting_Authorization]&[creator=]&[entityType=any]&[createdDateTo=]&[catalog=75]&[searchBy=Profile]&[sortBy=Document Date]&[createdDate=]&{County=_EQ_PASCO}&{District=_EQ_SWD}&{Facility-Site ID=_EQ_AIR_1010524}&{Document Type=_EQ_PERMIT - FINAL}&{Facility Type=_LK_N/A}&{Application Number=_EQ_1010524003} | The Shady Hills Combined Cycle Facility (SHCCF), a new 573-megawatt (MW) (winter) 1-on-1 combined cycle electrical generating facility to be owned and operated by Shady Hills Energy Center, LLC, which will be located at 14350 Merchant Energy Way, Spring Hill, Florida. The proposed work will be conducted on an approximately 14-acre parcel east of and located adjacent to the existing Shady Hills Generating Station (SHGS) power plant, which is owned and operated by Shady Hills Power Company, L.L.C. |  | GE 7HA.02 Combustion Turbine and HRSG with Duct Firing | 15.21 | Natural Gas | 3622.1 | MMBtu/hour | Throughput based on a compressor inlet air temperature of 59Â° F, the higher heating value (HHV) of natural gas, and 100% load | Nitrogen Oxides (NOx) | Other - CEMS | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry low-NOX combustors and Selective Catalytic Reduction (SCR) | 2 | PPMVD AT 15% O2 | 24-HOUR BLOCK AVERAGE BASIS (BACT) | BACT-PSD | NSPS | U | 0 | U | 15 | PPMVD AT 15% O2 | 30-OPERATING-DAY ROLLING AVG. (NSPS) | 0 |  |  | 0 | 0 | N |  | 2nd Limit of 15 ppmvd @ 15% O2 (for turbine loads â‰¥ 75%), 30-operating-day rolling avg. (NSPS Subpart KKKK) 3rd Limit: 96 ppmvd @15% O2 (for turbine loads < 75%), 30-operating-day rolling avg. (NSPS Subpart KKKK)
IL-0133 | LINCOLN LAND ENERGY CENTER | LINCOLN LAND ENERGY CENTER (A/K/A EMBERCLEAR) | SANGAMON | IL | 62558 | USA | JIM PALUMBO | 888-582-4460 X 55 | JPALUMBO@EMBERCLEAR.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov |  | 18040008 | 4911 | 221112 | Not Found | 09/30/2021 &nbsp;ACT | 07/29/2022 &nbsp;ACT | 2022-08-26 | 2022-12-06 | A | www2.illinois.gov/epa/public-notices/boa-notices/pages/archive.aspx | The proposed facility is designed to generate baseload power. It will consist of two combined-cycle generating units, with each a Siemens combustion turbine (3,647 mmBtu/hr) and a heat recovery steam generator (HRSG) with duct burners (35 mmBtu/hr); fired by natural gas only. Other units at the facility include an auxiliary boiler, engines, piping and piping components, circuit breakers and roadways. | Additional facility-wide pollutants, in tons/year: PM10/PM 2.5: 131.7 and 131.6 (respectively); sulfuric acid mist (SAM): 17.2; greenhouse gasses (GHG): 3,586,918 | Combined-Cycle Combustion Turbines | 15.21 | Natural Gas | 3647 | mmBtu/hour | Combined-cycle comustion turbines and heat recovery steam generators (HRSG) with a 35 mmBtu/hr duct burner. Turbine inlets would have evaporative cooling systems to cool the inlet air during warm weather to increase power output. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry low-NOx combustion with ultra-low NOx combustors; low-NOx duct burners; and selective catalytic reduction (SCR) | 2 | PPMV @ 15% O2 | SEE NOTES | BACT-PSD | NSPS | U | 0 | U | 0 |  | SEE NOTES | 0 |  |  | 0 | 0 | N |  | Emission limit 1 is applicable during normal operation, excluding startup and shutdown; averaging time: 3-operating hour, rolled hourly. Beginning 36 months after completion of shakedown, the averaging time: 1-operating hour. Emission Limit 2 is applicable during startup and shutdown: 130 pounds/hour (cold start/shakedown); 71 pounds/hour (non-cold start); 55 pounds/hour (shutdown). Limits for startup and shutdown are applicable for each clock hour that includes a startup, shutdown or shakedown. Compliance demonstrated using a continuous emissions monitoring system (CEMS)
KS-0041 | HOLLYFRONTIER EL DORADO REFINERY | HOLLYFRONTIER EL DORADO REFINING LLC | BUTLER | KS | 67042 | USA | RACHEL HENRY | 316-321-8283 | RACHEL.HENRY@HOLLYFRONTIER.COM | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov |  | CSD00080 V1.0 | 2911 | 324110 | 110000446134 | 04/29/2019 &nbsp;ACT | 10/30/2019 &nbsp;ACT | 2020-08-25 | 2023-03-27 | D |  | Petroleum Refinery located in Butler County, KS. Facility processes include distillation, cracking, reforming, isomerization, alkylation, hydrotreating, and coking. Products include a variety of grades of gasoline, fuel oils, and other fuels, along with petroleum coke and commercial grade sulfur. Products stored on-site and transported through pipeline, and by railcar and commercial trucking. By-products include petroleum coke and asphalt. The facility operates a cogeneration system that fires sweet natual gas to produce electric power and steam primarily for consumption within the facility. | This permit is for planned debottle-necking operations. Facility plans to remove operational constraints in order to operate at an increased rate and produce additional product. The following new equipment will be installed: charge heater and boiler for fluid catalytic creacking unit (FCCU), auxiliary air heater for the cogeneration plant, crude heater, crude tank, gasoline storage tank, slop oil tank, gas oil tank, and fugitive components. Modifications will be made to seven process heaters and boilers, four compressor engines, the FCCU, and the cogeneration combustion turbine. There will also be modifications made to four stationary engines subject to NSPS JJJJ (4J). The Tail Gas Treatment Unit 2, will not be physically changed but will be operated continuously (increase in operational hours). Lastly, an increase in maximum-fired duty of 70 MMBtu/hr will be made to units B306 and B307 and have been added to the PSD permit as modified heaters. Facility proposed a single heat input limit for the units B306, B307, and B-NewCrudeHeater (B308) of 381.3 MMBtu/hr. | L3804 | 15.21 | Refinery Fuel Gas | 456.5 | MMBTU/H | Cogeneration Combustion Turbine, equipped with Heat Recovery Steam Generator and steam/water injection. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Steam/water injection | 25 | PPMVD | 1-HOUR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 185.25 | PPMVD | 12-MONTH ROLLING AVERAGE | 0 |  |  | 0 | 0 | N |  | Emissions of NOx for this unit shall not exceed 25 PPMVD corrected to 15% O2. They shall also not exceed 185.25 PPMVD corrected to 15% O2 during periods of startup, shutdown, or low load, for up to 60 hours per 12-month rolling period, where these periods are defined as when the unit is operating, and the output is less than 20 MW.
LA-0331 | CALCASIEU PASS LNG PROJECT | VENTURE GLOBAL CALCASIEU PASS, LLC | CAMERON | LA | 70631 | USA | GRAHAM MCARTHUR | 202-759-6741 | GMCARTHUR@VGLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Ms. Mei Wu, (225)219-3180 | PDS-LA-805 | 4925 | 221210 | Not Found | 06/25/2018 &nbsp;ACT | 09/21/2018 &nbsp;ACT | 2019-02-14 | 2019-06-19 | A |  | New Liquefied Natural Gas (LNG) production, storage, and export terminal. | Application Received September 2, 2015. | Combined Cycle Combustion Turbines (CCCT1 to CCCT5) | 15.21 | Natural Gas | 921 | MM BTU/h |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Low NOx Burners, SCR, and Good Combustion Practices | 2.5 | PPMV | 30 DAY ROLLING AVERAGE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Units are in ppmv @ 15% O2; Averaging time is 30 Day Rolling Average during Normal Operations.
LA-0364 | FG LA COMPLEX | FG LA LLC | ST. JAMES | LA | 70086 | USA | KUAN-MING PEMG | 2813026850 | KMPEMG@FPCC.COM.TW | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mr. Anthony Randall, (225)219-3180 | PSD-LA-812 | 2869 | 325110 | Not Found | 01/14/2019 &nbsp;ACT | 01/06/2020 &nbsp;ACT | 2020-05-05 | 2021-08-09 | A | https://edms.deq.louisiana.gov/app/doc/view.aspx?doc=11998450&ob=yes&child=yes | The FG LA complex will produce ethylene, propylene, ethylene glycol, high density polyethylene, low density polyethylene, linear low-density polyethylene and polypropylene. To support the operation of these production plants, the complex will also include electric power and steam generating units (Utility), wastewater treatment (Central Wastewater Treatment Plant), storage and loading operations (Logistics), and associated flare systems. | FG LA was issued PSD-LA-812 to construct the FG LA Complex which involves the construction of fourteen facilities permitted under fourteen Title V Permits to manufacture ethylene and propylene, ultimately producing high and low density polyethylene, propylene, and ethylene glycol. | Cogeneration Units | 15.21 | Natural Gas | 2222 | mm btu/h | Throughput is maximum operating rate. 2139 MM BTU/hr normal operating rate. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry low NOx combustor design along with SCR. | 2 | PPMVD | 12-MONTH ROLLING AVERAGE | BACT-PSD | NESHAP , NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | BACT limit is corrected to 15% oxygen.
LA-0391 | MAGNOLIA POWER GENERATING STATION UNIT 1 | MAGNOLIA POWER LLC | IBERVILLE | LA | 70764 | USA | WILLIAM DAVIS | 609-250-7707 | LEE.DAVIS@KINDLE-ENERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Ms. Lori Pittman, (225)219-3180 | PSD-LA-839 | 4911 | 221112 | Not Found | 09/08/2020 &nbsp;ACT | 06/03/2022 &nbsp;ACT | 2023-03-02 | 2023-05-23 | A | https://edms.deq.louisiana.gov/app/doc/view?doc=13323738 | Magnolia Power LLC (Magnolia Power) is proposing to construct and operate a power plant, Magnolia Power Generating Station Unit 1, consisting of a natural gas-fired combined cycle gas turbine (CCGT Unit) in Iberville Parish, Louisiana. The CCGT Unit (EQT001), which includes a heat recovery steam generator (HRSG) equipped with duct burners, will have a predicted net nominal output of 730 megawatts (MW) |  | Combined Cycle Gas Turbine w/ Duct Burners and HRSG | 15.21 | Natural Gas | 5081 | mm BTU/h | Normal operating rate is 4930 MMBTU/h. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry low-NOx combustor design, selective catalytic reduction (SCR), and good combustion practices. | 2 | PPMVD | 24-HR ROLLING AVG BASED ON 1-HR AVG | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Units are ppmvd@15% O2 on a 24-hour rolling average based on a one-hour average.
LA-0391 | MAGNOLIA POWER GENERATING STATION UNIT 1 | MAGNOLIA POWER LLC | IBERVILLE | LA | 70764 | USA | WILLIAM DAVIS | 609-250-7707 | LEE.DAVIS@KINDLE-ENERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Ms. Lori Pittman, (225)219-3180 | PSD-LA-839 | 4911 | 221112 | Not Found | 09/08/2020 &nbsp;ACT | 06/03/2022 &nbsp;ACT | 2023-03-02 | 2023-05-23 | A | https://edms.deq.louisiana.gov/app/doc/view?doc=13323738 | Magnolia Power LLC (Magnolia Power) is proposing to construct and operate a power plant, Magnolia Power Generating Station Unit 1, consisting of a natural gas-fired combined cycle gas turbine (CCGT Unit) in Iberville Parish, Louisiana. The CCGT Unit (EQT001), which includes a heat recovery steam generator (HRSG) equipped with duct burners, will have a predicted net nominal output of 730 megawatts (MW) |  | Combined Cycle Gas Turbine Startup and Shutdown | 15.21 | Natural Gas | 5081 | mm BTU/h | Startup and shutdown emissions from the combined cycle gas turbine. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Good combustion practices. | 260 | LB/HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0431 | INDECK NILES LLC | INDECK NILES LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer Melissa Byrnes at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 75-16A | 4911 | 221112 | Not Found | 06/07/2018 &nbsp;ACT | 06/26/2018 &nbsp;ACT | 2018-08-13 | 2019-02-19 | A |  | Natural gas combined cycle power plant | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. Also, the permit revises the concentration-based NOx emission limit applied to the two combined-cycle natural gas-fired combustion turbines with heat recovery steam generators (identifed as EUCTGHRSG1 and EUCTGHRSG2) in the original permit 75-16. | FGCTGHRSG (2 Combined Cycle CTG with HRSGs) | 15.21 | Natural gas | 3421 | MMBTU/H | 3421 MMBTU/H for each turbine and 740 MMBTU/H for each duct burner for a combined throughput of 4161 MMBTU/H or 8322 MMBTU/H for both trains. Two combined-cycle natural gas-fired combustion turbine generators (CTGs) with Heat Recovery Steam Generators (HRSG) (EUCTGHRSG1 & EUCTGHRSG2). The total hours for startup and shutdown for each train shall not exceed 500 hours per 12-month rolling time period. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR with DLNB (Selective Catalytic Reduction with Dry Low NOx Burners) | 2 | PPM | AT 15%O2; 24-HR ROLL AVG | BACT-PSD | NSPS , SIP | N | 80 | N | 38.1 | LB/H | 24-HR ROLL AVG. | 0 |  |  | 0 | 0 | N |  | The concentration-based NOx emission limit above is the only BACT limit changed in PTI 75-16A. All other BACT limits remain as in PTI 75-16 (RBLC ID MI 0423). Emission Limit 1 above is 2 ppmvd at 15% O2 based on a 24-hour rolling average as determined each operating hour except during startup and shutdown. The limit is for EACH CTGHRSG. Emission Limit 2 above is 38.1 lb/hour and is based on a 24-hour rolling average as determined each operating hour except during startup and shutdown. The limit is for EACH CTGHRSG. The permit contains two additional NOx emission limits that apply to EACH CTGHRSG-- 1. 15 ppmvd at 15%O2 based on a 30-day rolling average as determined each operating day. This is per NSPS KKKK. 2. 286 lb/hour for each operating hour during startup or shutdown. This is also a BACT emission limit. Startup and shutdown operations are limited to 500 hours per 12-month rolling time period for each CTGHRSG train. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the startup and shutdown emission minimization plan. The efficiency range is 80-90 percent.
MI-0432 | NEW COVERT GENERATING FACILITY | NEW COVERT GENERATING COMPANY, LLC | VAN BUREN | MI | 49043 | USA | JOHN REESE | 212-792-0897 | JREESE@EASTERNGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 186-17 | 4911 | 221112 | Not Found | 04/17/2018 &nbsp;ACT | 07/30/2018 &nbsp;ACT | 2018-08-13 | 2019-02-19 | C |  | Power plant | The equipment consists of three advanced firing temperature Mitsubishi 501G combustion turbines, three heat recovery steam generators supplemented with gas-fired duct burners each with a max firing rate of 256 million British thermal units per hour (MMBtu/hr), three steam turbine generators. Auxiliary equipment includes three mechanical draft evaporative cooling towers, one natural gas auxiliary boiler, one diesel emergency generator, one diesel fire water pump, one aqueous parts cleaner, and one gas heater. | FG-TURB/DB1-3 (3 combined cycle combustion turbine and heat recovery steam generator trains) | 15.21 | Natural gas | 1230 | MW | Three (3) combined-cycle combustion turbine (CT) / heat recovery steam generator (HRSG) trains. Each CT is a natural gas fired Mitsubishi model 501G, equipped with dry low NOx combustor and inlet air evaporative cooling. Each HRSG includes a natural gas fired duct burner with a 256 MMBtu/hr heat input capacity and a dry low NOx burner. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Good combustion practices, DLN burners and SCR. | 2 | PPMVD | AT 15%O2; EACH INDIV. CT/HRSG TRAIN | BACT-PSD | NSPS , SIP | N | 0 | N | 22.4 | LB/H | EACH INDIV. CT/HRSG TRAIN; 24-H ROLL AVG | 0 |  |  | 0 | 0 | N |  | Each emission limit is per each individual CT/HRSG train in FG-TURB/DB1-3. The emission limits above DO NOT include startup/shutdown. There are 4 NOx emission limits, including an NSPS limit. They are all as follows: Em. Limit 1 = 2.0 ppmvd at 15%O2 based on a 24-hour rolling average as determined each operating hour. Em. Limit 2 = 22.4 lb/h based on a 24-hour rolling average as determined each operating hour. Em Limit 3 = 15 ppmvd at 15%O2 based on a 30-day rolling average as determined each operating day. This limit is per NSPS KKKK. Em Limit 4 = 116 ton/yr based on a 12-month rolling time period as determined at the end of each calendar month.
MI-0432 | NEW COVERT GENERATING FACILITY | NEW COVERT GENERATING COMPANY, LLC | VAN BUREN | MI | 49043 | USA | JOHN REESE | 212-792-0897 | JREESE@EASTERNGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 186-17 | 4911 | 221112 | Not Found | 04/17/2018 &nbsp;ACT | 07/30/2018 &nbsp;ACT | 2018-08-13 | 2019-02-19 | C |  | Power plant | The equipment consists of three advanced firing temperature Mitsubishi 501G combustion turbines, three heat recovery steam generators supplemented with gas-fired duct burners each with a max firing rate of 256 million British thermal units per hour (MMBtu/hr), three steam turbine generators. Auxiliary equipment includes three mechanical draft evaporative cooling towers, one natural gas auxiliary boiler, one diesel emergency generator, one diesel fire water pump, one aqueous parts cleaner, and one gas heater. | FG-TURB/DB1-3--Startup/Shutdown Operations | 15.21 | Natural gas | 1230 | MW | Three (3) combined-cycle combustion turbine (CT) / heat recovery steam generator (HRSG) trains. Each CT is a natural gas fired Mitsubishi model 501G, equipped with dry low NOx combustor and inlet air evaporative cooling. Each HRSG includes a natural gas fired duct burner with a 256 MMBTU/Hr heat input capacity and a dry low NOx burner. This scenario identifies the emission limits applicable during startup and shutdown operations. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Good combustion practices, DLN burners and SCR. | 249 | LB/H | EACH CT/HRSG TRAIN;STARTUP/SHUTDOWN | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emission limit 1 above is 249 lb/h for each operating hour during startup or shutdown for each individual CT/HRSG train in the flexible group. Startup is defined as the period of time from detection of a flame signal until the unit reaches steady state operation (i.e. loads greater than 50 percent). Shutdown is defined as beginning when the turbine output is lowered to the point that steady state operation can no longer be assured (i.e. loads less than 50 percent), and ending when a flame-off signal is detected.
AK-0088 | LIQUEFACTION PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | KENAI PENNINSULA BOROUGH | AK | 99635 | USA | LISA HAAS |  | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - Permit Writer - dave.jones2@alaska.gov | AQ1539CPT01 | 4922 | 488999 | Not Found | 01/14/2020 &nbsp;ACT | 07/07/2022 &nbsp;ACT | 2022-08-04 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Liquefaction Plant is planned to encompass 921 acres, including 901 acres onshore for the liquefied natural gas (LNG) Plant as well as 20 acres offshore for the Marine Terminal. The Liquefaction Plant will be the terminus of an approximately 807-mile gas pipeline, allowing natural gas from Alaskaâ€™s North Slope to be shipped to outside markets. The stationary source will consist of structures and equipment associated with processing, storage, and loading of LNG. There will be three liquefaction trains combining to process up to approximately 20 million metric tons per annun of LNG. |  | Four Combined Cycle Gas-Fired Turbines | 15.21 | Natural Gas | 384 | MMBtu/hr | EUs 7 - 10 are combined cycle gas turbines used for power generation at LNG facility | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation catalyst and good combustion practices | 2 | PPMV @ 15% O2 | 3-HOURS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Allowed 40 hours per year per turbine of operation without SCR and OxCat.
MI-0451 | MEC NORTH, LLC | MARSHALL ENERGY CENTER, LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 9144682402 | WLADD@DEVELOPMENTSPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Janelle Trowhill, at 517-582-5312 or at TrowhillJ1@michigan.gov for technical questions regarding this permit. Thank you. | 167-17B | 4911 | 221112 | Not Found | 12/08/2021 &nbsp;ACT | 06/23/2022 &nbsp;ACT | 2022-12-21 | 2023-04-25 | A |  | Natural gas combined-cycle power plant (two plants: north and south). | The two plants (MEC North, LLC and MEC South, LLC) will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. | EUCTGHRSG (North Plant): A combined cycle natural gas fired combustion turbine generator with heat recovery steam generator | 15.21 | Natural gas | 3064 | MMBTU/H | Throughput Information: Nominal 500 MW electricity production. Turbine rating of 3,064 MMBTU/hr (HHV) and HRSG duct burner rating of 889 MMBTU/Hr (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,064 MMBTU/hr (HHV). The HRSG is equipped with a natural gas fired duct burner, with a maximum heat input rating of 889 MMBTU/hr (HHV) and rated at 874 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst technology and good combustion practices. | 2 | PPM | HOURLY | BACT-PSD | SIP | N | 85 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit above is 2 ppmvd at 15% O2 with an underlying applicable requirement of BACT. The limit does not include startup and shutdown. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in SC III.2. Startup and Shutdown hours are limited to 300 hours per 12 month rolling time period.
MI-0452 | MEC SOUTH, LLC | MARSHALL ENERGY CENTER, LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 9144682402 | WLADD@DEVELOPMENTSPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer, Janelle Trowhill at TrowhillJ1@michigan.gov or at 517-582-5312. Thank you. | 168-17B | 4911 | 221112 | Not Found | 12/08/2021 &nbsp;ACT | 06/23/2022 &nbsp;ACT | 2022-12-22 | 2023-04-25 | A |  | Natural gas combined cycle power plant (Two Plants: North and South) | The two plants (MEC North, LLC and MEC South, LLC) will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. | EUCTGHRSG (South Plant): A combined-cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 3064 | MMBTU/H | Nominal 500 MW electricity production. Turbine rating of 3064 MMBTU/H (HHV) and HRSG duct burner rating of 889 MMBTU/H (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,064 MMBTU/hr (HHV). The HRSG is equipped with a natural gas fired duct burner, with a maximum heat input rating of 889 MMBTU/hr (HHV) and rated at 874 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation Catalyst Technology and Good Combustion Practices | 2 | PPM | HOURLY | BACT-PSD | SIP | N | 85 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emission limit 1 above = 2 ppmvd at 15% O2 on an hourly basis. The applicable requirement is BACT. The limit does not include startup and shutdown. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in SC III.2. Startup and Shutdown hours are limited to 300 hours per 12 month rolling time period.
TX-0878 | LNG EXPORT TERMINAL | PORT ARTHUR LNG, LLC | JEFFERSON | TX |  | USA | J.D. MORRIS | 713-298-5476 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Benjamin Hansen, Ph.D., P.E., (512) 239-4578, Benjamin.Hansen@tceq.texas.gov | 158420, PSDTX1572, GHGPSDTX198 | 4922 | 486210 | Not FOUND | 05/27/2020 &nbsp;ACT | 09/15/2022 &nbsp;ACT | 2019-11-07 | 2023-05-23 | A |  | Liquefied natural gas (LNG) export terminal. |  | Refrigeration Compression Turbines | 15.21 | NATURAL GAS | 26.92 | MMTON/Y | Eight GE Frame 7E gas turbines for refrigeration and compression at the site. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices. | 2 | PPM | 3-HR AVG | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0908 | NEWMAN POWER STATION | EL PASO ELECTRIC COMPANY | EL PASO | TX |  | USA | DANIEL PEREZ | 915-543-4166 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | N284, PSDTX1090M1, GHGPSDTX199 | 3511 | 221112 | not found | 08/26/2020 &nbsp;ACT | 08/27/2021 &nbsp;ACT | 2020-10-26 | 2022-03-08 | D |  | a new natural gas simple cycle turbine along with ancillary equipment. |  | Simple Cycle Turbine | 15.21 | natural gas | 230 | MW | Mitsubishi 501 G Series | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Use of Natural gas, good combustion practices, and oxidation catalyst | 2 | PPMVD |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0939 | ORANGE COUNTY ADVANCED POWER STATION | ENTERGY TEXAS, INC. | ORANGE | TX |  | USA | JASON WILLIS | 281-297-1937 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Huy Pham, (512) 239-1358, Huy.Pham@tceq.texas.gov | 166032 PSDTX1598 GHGPSDTX210 | 4911 | 221122 | Not found | 06/06/2022 &nbsp;ACT | 03/13/2023 &nbsp;ACT | 2022-06-06 | 2023-05-23 | A |  | Entergy Texas, Inc. proposes construction of a power plant consisting of two natural gas-fired combined cycle turbines with a maximum total nominal output of 1,215 MW. The turbines can also be fired with up to 30% volume hydrogen co-firing (blended fuel). Emergency engines, a cooling tower, storage tanks, and maintenance activities support operation of the turbines. |  | Combined Cycle Turbines | 15.21 | NATURAL GAS | 1215 | MW | 2 Mitsubishi M501JAC combustion turbines 1,215 MW (in a 2x1 configuration) output and 6,762 Btu/kW-hr (with a 9% degradation) gross heat rate. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation Catalyst and good combustion practices | 2 | PPMVD | 15% O2 3-HR AVERAGE | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0455 | MIDLAND COGENERATION VENTURE LIMITED PARTNERSHIP | MIDLAND COGENERATION VENTURE LIMITED PARTNERSHIP | MIDLAND | MI | 46540 | USA | BRIAN VOKAL | 248-980-1139 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes at 517-648-6339 or at ByrnesM@michigan.gov. Thank you. | 2023-10-23 | 4911 | 221112 | Not found | 10/12/2022 &nbsp;ACT | 02/01/2023 &nbsp;ACT | 2023-05-15 | 2023-05-23 | B |  | Electric and steam generation |  | EUCTGHRSG1 | 15.21 | Natural gas | 4197.6 | MMBTU/H |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation catalyst | 2.4 | PPM | PPMVD AT 15%O2; HOURLY EXC SU/SD | BACT-PSD | SIP | N | 90 | N | 11.4 | LB/H | HOURLY EXCEPT DURING SU/SD | 0 |  |  | 0 | 0 | N
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (South Plant): A combined cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/H (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/H (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR and an oxidation catalyst. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR with DLNB (Selective catalytic reduction with dry low NOx burners). | 2 | PPMV | AT 15%O2; 24-HR ROLL AVG NOT S.S. | BACT-PSD | NSPS , SIP | N | 80 | N | 29.7 | LB/H | 24-H ROLL AVG NOT S.S. | 0 |  |  | 0 | 0 | N |  | The estimated efficiency of SCR with DLNB is a range of 80-90%. There are 4 NOx emission limits in the permit, as follows: Emission Limit 1 = 2 ppmvd at 15%O2 based on a 24-hour rolling average as determined each operating hour except during startup and shutdown (S.S.). Emission limit 2 - 15 ppmvd at 15%O2 based on a 30-day rolling average as determined each operating day (not including startup and shutdown) per NSPS KKKK. Emission limit 3 = 29.7 LB/H based on a 24-hour rolling average as determined each operating hour except during startup and shutdown. Emission limit 4 = 126.5 LB/H based on each operating hour during startup or shutdown. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in Special Condition III.2 in the permit. Startup and Shutdown hours are limited to 300 hours per 12 month rolling time period.
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (North Plant): A combined-cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | Nominal 500 MW electricity production. Turbine rating of 3,080 MMBTU/hr (HHV) and HRSG duct burner rating of 755 MMBTU/hr (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/hr (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR with DLNB (Selective catalytic reduction with Dry Low NOx burners). | 2 | PPMVD | AT 15%O2; 24-H ROLL AVG; NOT S.S. | BACT-PSD | NSPS , SIP | N | 80 | N | 29.7 | LB/H | 24-H ROLL AVG; NOT STARTUP/SHUTDOWN (SS) | 0 |  |  | 0 | 0 | N |  | There are 4 NOx emission limits for EUCTGHRSG as follows: Emission limit 1 = 2 ppmvd at 15%O2 based on a 24-hour rolling average as determined each operating hour except during startup and shutdown. Emission Limit 2 = 29.7 lb/h based on a 24-hour rolling average as determined each operating hour except during startup and shutdown. Emission Limit 3 = 15 ppmvd at 15%O2 based on a 30-day rolling average as determined each operating day. This limit is from NSPS KKKK. Emission limit 4 = 126.5 lb/h each operating hour during startup or shutdown. Estimated efficiency of SCR with DLNB is a range of 80-90% Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level shall be described in the plan required by Special Condition III.2. Startup and shutdown hours are limited to 300 hours per 12-month rolling time period.
MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2019-02-19 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | FGCTGHRSG (EUCTGHRSG1 &amp; EUCTGHRSG2) | 15.21 | Natural gas | 0 |  | Two (2) combined-cycle natural gas-fired combustion turbine generators, each with a heat recovery steam generator (CTGHRSG). Plant nominal 1,150 MW electricity production. Turbines are each rated at 3,658 MMBTU/H and HRSG duct burners are each rated at 800 MMBTU/H. The HRSGs are not capable of operating independently from the CTGs. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR with DLNB (Selective catalytic reduction with dry low NOx burners). | 2 | PPMVD | AT 15%O2; 24-H ROLL AVG; EACH UNIT; | BACT-PSD | NSPS , SIP | N | 80 | N | 28.9 | LB/H | 24-H ROLL AVG; EACH UNIT; NOT S.S. | 0 |  |  | 0 | 0 | N |  | There are 4 NOx emission limits in the permit, described below: Emission limit 1 = 2 ppmvd at 15% O2 based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown (S.S.). The limit applies to each unit. Emission limit 2 = 28.90 LB/H based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown (S.S.). The limit applies to each unit. Emission limit 3 = 15 ppmvd at 15% O2 based on a 30-day rolling average as determined each operating day. The limit applies to each unit and is from NSPS KKKK. Emission limit 4 = 262.4 LB/H each operating hour during startup or shutdown (S.S.). The limit applies to each unit. The estimated efficiency of SCR with DLNB is a range of 80-90%. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in Special Condition III.2 in the permit.
WI-0300 | NEMADJI TRAIL ENERGY CENTER | NEMADJI TRAIL ENERGY CENTER | DOUGLAS | WI | 54880 | USA |  |  |  | 5 | WI001 | WISCONSIN DEPT OF NATURAL RESOURCES; AIR MGMT. PROGRAM | MS. KRISTIN HART | (608)266-6876 | kristin.hart@wisconsin.gov |  | 18-MMC-168 | 4911 | 221121 | Not Found | 06/30/2020 &nbsp;ACT | 09/01/2020 &nbsp;ACT | 2022-06-27 | 2022-09-16 | A | https://dnr.wi.gov/cias/am/amexternal/AM_DownloadObject.aspx?id=1011796 | Natural gas-fired power plant |  | Natural-Gas-Fired Combined-Cycle Turbine (P01) | 15.21 | Natural Gas | 4671 | MMBTU/H | One Natural-Gas-Fired Siemens SGT6-8000 H Combined-Cycle Turbine with Natural Gas-Fired Duct Burner and Diesel Fuel Oil Back-Up [Maximum continuous rating: 4,671 MMBtu/hr higher heating value (HHV) when combusting natural gas, 4,027 MMBtu/hr, HHV when combusting diesel fuel oil], Selective Catalytic Reduction (SCR) (C01a) and Oxidation Catalyst (C01b) | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation Catalyst, good combustion control | 2.7 | PPM AT 15% O2 | 168-HR AVG., NAT. GAS, DUCT FIRING | BACT-PSD |  | U | 50 | U | 0.6 | PPM AT 15% O2 | 168-HR AVG., NAT. GAS, W/O DUCT FIRING | 0 |  |  | 0 | 0 | N |  | *Except during start-up and shutdown. VOC may not exceed 2.7 ppm at 15% O2 based on a 168-hour rolling average when firing natural gas and with duct firing. and may not exceed 0.6 ppm at 15% O2 based on a 168-hour rolling average when firing natural gas and without duct firing. VOC may not exceed 3.3 ppm at 15% O2 based on a 168-hour rolling average when firing diesel fuel oil and with duct firing and may not exceed 0.6 ppm at 15% O2 based on a 168-hour rolling average when firing diesel fuel oil and without duct firing
TX-0908 | NEWMAN POWER STATION | EL PASO ELECTRIC COMPANY | EL PASO | TX |  | USA | DANIEL PEREZ | 915-543-4166 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | N284, PSDTX1090M1, GHGPSDTX199 | 3511 | 221112 | not found | 08/26/2020 &nbsp;ACT | 08/27/2021 &nbsp;ACT | 2020-10-26 | 2022-03-08 | D |  | a new natural gas simple cycle turbine along with ancillary equipment. |  | Simple Cycle Turbine | 15.21 | natural gas | 230 | MW | Mitsubishi 501 G Series | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation catalyst | 3 | PPMVD |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2019-02-19 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | FGCTGHRSG (EUCTGHRSG1 &amp; EUCTGHRSG2)--Startup &amp; Shutdown | 15.21 | Natural gas | 0 |  | This section is the startup and shutdown emission limits for FGCTGHRSG. Two 3,658 MMBTU/H natural gas-fired combustion turbine generators (CTGs) coupled with heat recovery steam generators (HRSGs). The HRSGs are equipped with natural gas-fired duct burners rated at 800 MMBTU/H to provide heat for additional steam production. The HRSGs are not capable of operating independently from the CTGs. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR with DLNB (Selective catalytic reduction with dry low NOx burners). | 262.4 | LB/H | EACH UNIT; OPERATING HOUR DURING S.S. | BACT-PSD | SIP | N | 80 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit above is 262.4 LB/H for each unit and is per operating hour during startup or shutdown. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in Special Condition III.2 in the permit.
MI-0439 | JACKSON GENERATING STATION | CONSUMERS ENERGY COMPANY | JACKSON | MI | 49203-2174 | USA | BRIAN LABBY | 989-667-5008 | BRIAN.LABBY@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, at 517-284-6790 or at byrnesm@michigan.gov, for technical questions regarding this permit. Thank you. | 118-18 | 4911 | 221112 | 110015804511 | 11/29/2018 &nbsp;ACT | 04/02/2019 &nbsp;ACT | 2019-05-20 | 2019-06-19 | C |  | Natural gas combined-cycle power plant |  | FGLMDB1-6 (6 combined cycle natural gas fired CTG each equipped with a HRSG) | 15.21 | natural gas | 420 | MW | FGLMDB1-6 is 6 combined cycle natural gas fired combustion turbine generators (CTG) each equipped with a heat recovery steam generator (HRSG). Nominal rating 420 MW. Each combustion turbine (CT) is a GE LM6000 with a rating of 440 MMBTU/HR (HHV) and a duct burner rating of 222 MMBTU/HR (HHV). A combined cycle natural gas fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 420 MW electricity production. The HRSG is not capable of operating independently from the CTG. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Steam injection, good combustion practices and only combust natural gas. | 25 | PPM | AT 15% O2; 30 DAY ROLLING AVG; EACH UNIT | BACT-PSD | NSPS | N | 0 | U | 22 | PPM | AT 15%O2; 12-MO ROLL AVG; ALL UNITS COMB | 0 |  |  | 0 | 0 | N |  | There are 3 NOx emission limits, two of which are listed in the table above. For clarity, all 3 limits are listed here: Emission limit 1 = 25 ppmv at 15% O2 on a dry gas basis for each unit during periods with no duct firing on a 30-day rolling average as determined at the end of each calendar day. This limit is from NSPS GG and NSPS Db. The limit does not apply during startup and shutdown. Emission limit 2 = 22 ppmv at 15% O2 on a dry gas basis excluding periods for each turbine when it operates in conjunction with its respective duct burner on a 12-month rolling average as determined at the end of each calendar month. This limit is for all units combined and does not apply during periods of startup and shutdown. Emission limit 3 = 54.0 lb/hr (equates to approximately 0.09 lb/MMBTU) when the turbine operates alone and when the turbine operates in conjunction with its respective duct burner on a 30-day rolling average as determined at the end of each calendar day. These limits apply during periods of startup and shutdown. Physical constraints came into BACT decision due to modification to an existing facility.
MI-0441 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, for technical questions regarding this permit. She may be reached at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 74-18 | 4911 | 221112 | 110040958425 | 10/16/2018 &nbsp;ACT | 12/21/2018 &nbsp;ACT | 2019-10-18 | 2021-08-09 | D |  | Natural gas combined-cycle power plant. | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG2--A 667 MMBTU/H natural gas fired CTG with a HRSG. | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG2 is a nominally rated 667 MMBTU/H natural gas fired CTG coupled with a HRSG. The HRSG is equipped with a natural gas fired duct burner rated at 204 MMBTU/h to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a DLNB, SCR and oxidation catalyst. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry low NOx burners and selective catalytic reduction for NOx control. | 3 | PPM | PPMVD@15%O2; 24-H AVG; SEE NOTES | BACT-PSD | SIP | N | 0 | U | 25 | PPM | PPMVD@15%O2; 4-H AVG; SEE NOTES | 0 |  |  | 15924 | 0 | N | 2018 | There are 4 NOx emission limits in the permit for this emission unit. Emission limit 1 is 3.0 ppmvd at 15% O2 based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown. This limit is when the unit is in combined cycle mode. Emission limit 2 is 25 ppmvd at 15% O2 based on a 4-hour rolling average, except during operation less than 75% peak load. This limit is when the unit is in HRSG bypass mode. Emission limit 3 is 60.0 lb/h when the unit is in combined cycle mode. It is hourly including startup or shutdown. Emission limit 4 is 60.0 lb/h when the unit is in HRSG bypass mode. It is based on a 24-hour rolling average as determined each operating hour. The use of SCR with DLNB is the highest ranked control system and was selected as BACT; therefore, an economic analysis was not performed.
MI-0441 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, for technical questions regarding this permit. She may be reached at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 74-18 | 4911 | 221112 | 110040958425 | 10/16/2018 &nbsp;ACT | 12/21/2018 &nbsp;ACT | 2019-10-18 | 2021-08-09 | D |  | Natural gas combined-cycle power plant. | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG1--A 667 MMBTU/H NG fired combustion turbine generator coupled with a heat recovery steam generator (HRSG) | 15.21 | Natural gas | 667 | MMBTU/H | A nominally rated 667 MMBTU/hr natural gas-fired combustion turbine generator (CTG) coupled with a heat recovery steam generator (HRSG). The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBTU/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a dry low NOx burner (DLNB), selective catalytic reduction (SCR) and oxidation catalyst. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry low NOx burners and selective catalytic reduction for NOx control. | 3 | PPM | PPMVD@15%O2; 24-H ROLL AVG; SEE NOTES | BACT-PSD | SIP | N | 0 | U | 25 | PPM | PPMVD@15%O2; 4-HR ROLL AVG; SEE NOTES | 0 |  |  | 15924 | 0 | N | 2018 | NOx emission limit 1 is 3.0 ppmvd at 15%O2 based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown. The limit applies when the unit is in combined cycle mode. NOx emission limit 2 is 25 ppmvd at 15%O2 based on a 4-hour rolling average, except during operation less than 75% of peak load. The limit applies to the unit in HRSG bypass mode. **There are two additional NOx limits in the permit**************** NOx emission limit 3 is 60.0 lb/h when the unit is in combined cycle mode. The limit is hourly including startup or shutdown. NOx emission limit 4 is 60.0 lb/h when the unit is in HRSG bypass mode. The limit is based on a 24-hour rolling average as determined each operating hour. The use of SCR with the DLNB is the highest ranked control system and was selected as BACT; therefore, an economic analysis was not performed.
MI-0441 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, for technical questions regarding this permit. She may be reached at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 74-18 | 4911 | 221112 | 110040958425 | 10/16/2018 &nbsp;ACT | 12/21/2018 &nbsp;ACT | 2019-10-18 | 2021-08-09 | D |  | Natural gas combined-cycle power plant. | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG2--A 667 MMBTU/H natural gas fired CTG with a HRSG. | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG2 is a nominally rated 667 MMBTU/H natural gas fired CTG coupled with a HRSG. The HRSG is equipped with a natural gas fired duct burner rated at 204 MMBTU/h to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a DLNB, SCR and oxidation catalyst. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | An oxidation catalyst for VOC control and good combustion practices. | 3 | PPM | PPMVD@15%O2; HOURLY; SEE NOTES | BACT-PSD |  | N | 0 | U | 5 | LB/H | HOURLY EXCEPT STARTUP/SHUTDOWN; SEE NOTE | 0 |  |  | 17102 | 0 | N | 2017 | Emission limit 1 is 3 ppmvd at 15% O2 and is an hourly limit except during startup and shutdown. The limit applies when the unit is in combined cycle mode. Emission limit 2 is 5 lb/h and is an hourly limit except during startup and shutdown. The limit applies when the unit is in HRSG bypass mode.
MI-0441 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, for technical questions regarding this permit. She may be reached at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 74-18 | 4911 | 221112 | 110040958425 | 10/16/2018 &nbsp;ACT | 12/21/2018 &nbsp;ACT | 2019-10-18 | 2021-08-09 | D |  | Natural gas combined-cycle power plant. | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG1--A 667 MMBTU/H NG fired combustion turbine generator coupled with a heat recovery steam generator (HRSG) | 15.21 | Natural gas | 667 | MMBTU/H | A nominally rated 667 MMBTU/hr natural gas-fired combustion turbine generator (CTG) coupled with a heat recovery steam generator (HRSG). The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBTU/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a dry low NOx burner (DLNB), selective catalytic reduction (SCR) and oxidation catalyst. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | An oxidation catalyst for VOC control for each CTG/HRSG unit, good combustion practices. | 3 | PPM | PPMVD@15%O2; HOURLY EXC.START/SHUT; NOTE | BACT-PSD |  | N | 0 | U | 5 | LB/H | HOURLY EXCEPT STARTUP/SHUTDOWN; SEE NOTE | 0 |  |  | 17102 | 0 | N | 2017 | VOC Emission Limit 1 above is 3 ppmvd at 15%O2 when the unit is in combined cycle mode. The limit is hourly except during startup and shutdown. VOC Emission Limit 2 above is 5 lb/h when the unit is in HRSG bypass mode and is hourly except during startup and shutdown.
MI-0447 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-648-6339 or at ByrnesM@michigan.gov for technical questions related to this permit. Thank you. | 74-18A | 4911 | 221112 | 110040958425 | 09/22/2020 &nbsp;ACT | 01/07/2021 &nbsp;ACT | 2021-06-28 | 2021-09-10 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG1 | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG1--A nominally rated 667 MMBTU/hr natural gas-fired combustion turbine generator (CTG) coupled with a heat recovery steam generator (HRSG). The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBTU/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a dry low NOx burner (DLNB), selective catalytic reduction (SCR), and oxidation catalyst. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | An oxidation catalyst for VOC control for each CTG/HRSG unit, good combustion practices. | 3 | PPM | HOURLY EXCEPT STARTUP SHUTDOWN | BACT-PSD |  | N | 0 | U | 5 | LB/H | HOURLY EXCEPT STARTUP SHUTDOWN | 0 |  |  | 17102 | 0 | N |  | There are two emission limits listed above and are described here in more detail. Emission limit 1 = 3 ppmvd at 15% O2; hourly except during startup and shutdown. Applies in combined cycle mode. Emission limit 2 = 5 lb/hr; hourly except during startup and shutdown. Applies in HRSG bypass mode.
MI-0447 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-648-6339 or at ByrnesM@michigan.gov for technical questions related to this permit. Thank you. | 74-18A | 4911 | 221112 | 110040958425 | 09/22/2020 &nbsp;ACT | 01/07/2021 &nbsp;ACT | 2021-06-28 | 2021-09-10 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG2 | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG2--A nominally rated 667 MMBTU/hr natural gas-fired CTG coupled with a HRSG. The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBTU/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a DLNB, SCR, and oxidation catalyst. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | An oxidation catalyst for VOC control for each CTG/HRSG unit, good combustion practices. | 3 | PPM | HOURLY; EXCEPT DURING STARTUP/SHUTDOWN | BACT-PSD |  | N | 0 | U | 5 | LB/H | HOURLY EXCEPT DURING STARTUP/SHUTDOWN | 0 |  |  | 17102 | 0 | N |  | Emission limit 1 (above) = 3 ppmvd at 15% O2; hourly except during startup and shutdown. Applies in combined cycle mode. Emission limit 2 (above) = 5 lb/hr; hourly except during startup and shutdown. Applies in HRSG bypass mode.
MI-0454 | LBWL-ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions about this permit, please contact the permit engineer, Lauren Magirl, at 517-582-5345, or at MagirlL@michigan.gov. Thank you. | 74-18D | 4911 | 221112 | Not Found | 10/25/2022 &nbsp;ACT | 12/20/2022 &nbsp;ACT | 2022-12-29 | 2023-05-23 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWLâ€™s existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG1 | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG1- A nominally rated 667 MMBtu/hr natural gas-fired combustion turbine generator (CTG) coupled with a heat recovery steam generator (HRSG). The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBtu/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a dry low NOx burner (DLNB), selective catalytic reduction (SCR), and oxidation catalyst. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | An oxidation catalyst for VOC control for each CTG/HRSG unit, good combustion practices. | 3 | PPM | PPMVD AT 15%O2; HOURLY EXC SU/SD | BACT-PSD |  | N | 0 | N | 5 | LB/H | HOURLY EXCEPT SU/SD | 0 |  |  | 0 | 0 | N |  | Emission limit 1 above = 3 ppmvd at 15% O2 on an hourly basis except during startup and shutdown. Applies in combined cycle mode. Emission limit 2 above is 5 lbs/hr on an hourly basis except during startup and shutdown. Applies in HRSG bypass mode.
MI-0454 | LBWL-ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions about this permit, please contact the permit engineer, Lauren Magirl, at 517-582-5345, or at MagirlL@michigan.gov. Thank you. | 74-18D | 4911 | 221112 | Not Found | 10/25/2022 &nbsp;ACT | 12/20/2022 &nbsp;ACT | 2022-12-29 | 2023-05-23 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWLâ€™s existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG2 | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG2- A nominally rated 667 MMBtu/hr natural gas-fired CTG coupled with a HRSG. The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBtu/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a DLNB, SCR, and oxidation catalyst. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | An oxidation catalyst for VOC control for each CTG/HRSG unit, good combustion practices. | 3 | PPM | PPMVD AT 15%O2; HOURLY EXC SU/SD. CC MOD | BACT-PSD |  | N | 0 | U | 5 | LB/H | HOURLY, EXC. SU/SD; APPLY IN HRSG BYPASS | 0 |  |  | 0 | 0 | N |  | There are 2 VOC emission limits, both listed below. Emission limit 1 = 3 ppmvd at 15% O2 on an hourly basis, except during startup and shutdown. Applies in combined cycle mode. Emission limit 2 = 5 lb/hr on an hourly basis except during startup and shutdown. Applies in HRSG bypass mode.
LA-0364 | FG LA COMPLEX | FG LA LLC | ST. JAMES | LA | 70086 | USA | KUAN-MING PEMG | 2813026850 | KMPEMG@FPCC.COM.TW | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mr. Anthony Randall, (225)219-3180 | PSD-LA-812 | 2869 | 325110 | Not Found | 01/14/2019 &nbsp;ACT | 01/06/2020 &nbsp;ACT | 2020-05-05 | 2021-08-09 | A | https://edms.deq.louisiana.gov/app/doc/view.aspx?doc=11998450&ob=yes&child=yes | The FG LA complex will produce ethylene, propylene, ethylene glycol, high density polyethylene, low density polyethylene, linear low-density polyethylene and polypropylene. To support the operation of these production plants, the complex will also include electric power and steam generating units (Utility), wastewater treatment (Central Wastewater Treatment Plant), storage and loading operations (Logistics), and associated flare systems. | FG LA was issued PSD-LA-812 to construct the FG LA Complex which involves the construction of fourteen facilities permitted under fourteen Title V Permits to manufacture ethylene and propylene, ultimately producing high and low density polyethylene, propylene, and ethylene glycol. | Cogeneration Units | 15.21 | Natural Gas | 2222 | mm btu/h | Throughput is maximum operating rate. 2139 MM BTU/hr normal operating rate. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Good combustion practices and catalytic oxidation | 4 | PPMVD |  | BACT-PSD | NSPS , NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | BACT limit is 4 ppmvd at 15% O2.
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (South Plant): A combined cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/H (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/H (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR and an oxidation catalyst. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst technology and good combustion practices. | 4 | PPMV | AT 15%O2; 240HR ROLL AVG; NOT S.S. | BACT-PSD | SIP | N | 0 | N | 788.6 | LB/H | OPERATING HR DURING STARTUP OR SHUTDOWN | 0 |  |  | 0 | 0 | N |  | The first emission limit above is 4 PPMVD at 15%O2 based on a 24-hour rolling average as determined each operating hour EXCEPT during startup and shutdown. Emission limit 2 above is 788.6 LB/H during each operating hour during startup or shutdown (S.S.). Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in Special Condition III.2 in the permit. Startup and Shutdown hours are limited to 300 hours per 12 month rolling time period.
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (North Plant): A combined-cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | Nominal 500 MW electricity production. Turbine rating of 3,080 MMBTU/hr (HHV) and HRSG duct burner rating of 755 MMBTU/hr (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/hr (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst technology and good combustion practices. | 4 | PPMVD | AT 15%O2; 24-H ROLL AVG; NOT INCL ST/SH | BACT-PSD | SIP | N | 0 | N | 788.6 | LB/H | OPERATING HR DURING STARTUP OR SHUTDOWN | 0 |  |  | 0 | 0 | N |  | There are two emission limits: Emission limit 1 = 4 ppmvd at 15%O2 based on a 24-hr rolling average as determined each operating hour, except during startup or shutdown. Emission limit 2 = 788.6 lb/h each operating hour during startup or shutdown. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from teh lowering of teh turbine output below the demonstrated steady state level, with teh intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in Special Condition III.2. Startup and shutdown hours are limits to 300 hours per 12-month rolling time period.
MI-0441 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, for technical questions regarding this permit. She may be reached at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 74-18 | 4911 | 221112 | 110040958425 | 10/16/2018 &nbsp;ACT | 12/21/2018 &nbsp;ACT | 2019-10-18 | 2021-08-09 | D |  | Natural gas combined-cycle power plant. | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG2--A 667 MMBTU/H natural gas fired CTG with a HRSG. | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG2 is a nominally rated 667 MMBTU/H natural gas fired CTG coupled with a HRSG. The HRSG is equipped with a natural gas fired duct burner rated at 204 MMBTU/h to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a DLNB, SCR and oxidation catalyst. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | An oxidation catalyst for CO control for each CTG/HRSG unit, good combustion practices. | 4 | PPM | PPMVD@15%O2; 24-H AVG; SEE NOTES | BACT-PSD | SIP | N | 0 | U | 9 | LB/H | HOURLY EXCEPT STARTUP/SHUTDOWN; SEE NOTE | 0 |  |  | 17102 | 0 | N | 2017 | There are 3 CO emission limits in the permit. Emission limit 1 is 4 ppmvd at 15%O2 based on a 24-hour rolling average as determined each operating hour except during startup and shutdown. The limit applies when the unit is in combined cycle mode. Emission limit 2 is 9 lb/h and is an hourly limit except during startup and shutdown. The limit applies when the unit is in HRSG bypass mode. Emission limit 3 is 289 lb/h and is an hourly limit including startup and shutdown. The limit applies when the unit is in combined cycle mode. Thermal oxidation and NSCR were considered not technically feasible for these applications.
MI-0441 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, for technical questions regarding this permit. She may be reached at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 74-18 | 4911 | 221112 | 110040958425 | 10/16/2018 &nbsp;ACT | 12/21/2018 &nbsp;ACT | 2019-10-18 | 2021-08-09 | D |  | Natural gas combined-cycle power plant. | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG1--A 667 MMBTU/H NG fired combustion turbine generator coupled with a heat recovery steam generator (HRSG) | 15.21 | Natural gas | 667 | MMBTU/H | A nominally rated 667 MMBTU/hr natural gas-fired combustion turbine generator (CTG) coupled with a heat recovery steam generator (HRSG). The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBTU/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a dry low NOx burner (DLNB), selective catalytic reduction (SCR) and oxidation catalyst. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | An oxidation catalyst for CO control for each CTG/HRSG unit; good combustion practices. | 4 | PPM | PPMVD@15%O2;24-H ROLL AVG; SEE NOTES | BACT-PSD | SIP | N | 0 | U | 9 | LB/H | HOURLY EXCEPT STARTUP/SHUTDOWN; SEE NOTE | 0 |  |  | 17102 | 0 | N | 2017 | There are 3 CO emission limits in the permit as follows: Emission limit 1 is 4 ppmvd at 15%O2 based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown. Applies when the unit is in combined cycle mode. Emission limit 2 is 9 lb/h when the unit is in HRSG bypass mode. The limit is hourly except during startup and shutdown. Emission limit 3 is 289 lb/h when the unit is in combined cycle mode and is hourly including startup and shutdown. Thermal oxidation and NSCR were considered not technically feasible for these applications.
*MI-0445 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact Mark Mitchell at 517-582-5293 or at mitchellm7@michigan.gov. Thank you. | 75-16B | 4911 | 221112 | Not found | 08/20/2019 &nbsp;ACT | 11/26/2019 &nbsp;ACT | 2020-12-22 | 2020-12-23 | A |  | Natural gas combined cycle power plant |  | FGCTGHRSG | 15.21 | Natural gas | 3421 | MMBTU/H | 3421 MMBTU/H for each turbine 740 MMBTU/H for each duct burner for a combined throughput of 4161 MMBTU/H or 8322 MMBTU/H for both trains. Two combined-cycle natural gas-fired combustion turbine generators (CTGs) with Heat Recovery Steam Generators (HRSG) (EUCTGHRSG1 & EUCTGHRSG2 in FGCTGHRSG). The total hours for startup and shutdown for each train shall not exceed 500 hours per 12-month rolling time period. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst technology and good combustion practices. | 4 | PPM | PPMVD @15% O2. 24HR ROLL AVG EXCEPT SS | BACT-PSD | SIP | N | 85 | U | 24.7 | LB/H | 24-HR ROLL AVG EXCEPT SS | 0 |  |  | 0 | 0 | N |  | There are 3 emission limits for each CTGHRSG in the flexible group (FGCTGHRSG). Emission limit 1 = 4 ppmvd @15%O2 based on a 24-hour rolling average as determined each operating hour except during startup/shutdown (SS). Emission limit 2 = 24.7 lb/h based on a 24-hour rolling average as determined each operating hour, except during startup/shutdown (SS). Emission limit 3 = 3537 lb/h based on operating hour during startup or shutdown. Startup and shutdown operations are limited to 500 hours per 12-month rolling time period for each CTGHRSG train. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the startup and shutdown emission minimization plan. The efficiency range is 85-90 percent.
MI-0447 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-648-6339 or at ByrnesM@michigan.gov for technical questions related to this permit. Thank you. | 74-18A | 4911 | 221112 | 110040958425 | 09/22/2020 &nbsp;ACT | 01/07/2021 &nbsp;ACT | 2021-06-28 | 2021-09-10 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG1 | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG1--A nominally rated 667 MMBTU/hr natural gas-fired combustion turbine generator (CTG) coupled with a heat recovery steam generator (HRSG). The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBTU/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a dry low NOx burner (DLNB), selective catalytic reduction (SCR), and oxidation catalyst. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | An oxidation catalyst for CO control for each CTG/HRSG unit, good combustion practices. | 4 | PPM | 24-HR ROLL AVG EXCEPT STARTUP/SHUTDOWN | BACT-PSD | SIP | N | 0 | U | 9 | LB/H | HOURLY | 0 |  |  | 17102 | 0 | N |  | There are 3 CO emission limits. Two are listed above but all 3 will also be listed here. Emission limit 1 = 4 ppmvd at 15% O2, based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown. Applies in combined cycle mode. Emission limit 2 = 9 lb/hr; hourly except during startup and shutdown. Applies in HRSG bypass mode. Emission limit 3 = 389 lb/hr; hourly including startup and shutdown. Applies in combined cycle mode. Thermal oxidation and NSCR were considered not technically feasible for the application.
MI-0447 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-648-6339 or at ByrnesM@michigan.gov for technical questions related to this permit. Thank you. | 74-18A | 4911 | 221112 | 110040958425 | 09/22/2020 &nbsp;ACT | 01/07/2021 &nbsp;ACT | 2021-06-28 | 2021-09-10 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG2 | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG2--A nominally rated 667 MMBTU/hr natural gas-fired CTG coupled with a HRSG. The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBTU/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a DLNB, SCR, and oxidation catalyst. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | An oxidation catalyst for CO control for each CTG/HRSG unit, good combustion practices. | 4 | PPM | 24-HR ROLL AVG EXCEPT STARTUP/SHUTDOWN | BACT-PSD | SIP | N | 0 | U | 9 | LB/H | HOURLY EXCEPT STARTUP SHUTDOWN | 0 |  |  | 17102 | 0 | N |  | There are 3 CO emission limits. Emission limit 1 = 4 ppmvd at 15% O2 based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown. Applies in combined cycle mode. Emission limit 2 = 9 lb/hr; hourly except during startup and shutdown. Applies in HRSG bypass mode. Emission limit 3 = 289 lb/hr; hourly including startup and shutdown. Applies in combined cycle mode. Thermal oxidation and NSCR were considered not technically feasible for these applications.
MI-0454 | LBWL-ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions about this permit, please contact the permit engineer, Lauren Magirl, at 517-582-5345, or at MagirlL@michigan.gov. Thank you. | 74-18D | 4911 | 221112 | Not Found | 10/25/2022 &nbsp;ACT | 12/20/2022 &nbsp;ACT | 2022-12-29 | 2023-05-23 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWLâ€™s existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG2 | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG2- A nominally rated 667 MMBtu/hr natural gas-fired CTG coupled with a HRSG. The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBtu/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a DLNB, SCR, and oxidation catalyst. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | An oxidation catalyst for CO control for each CTG/HRSG unit, good combustion practices. | 4 | PPM | PPMVD AT 15%O2; 24-HR ROLL AVG EXC SU/SD | BACT-PSD | SIP | N | 0 | U | 9 | LB/H | HOURLY, EXC. SU/SD; APPLY IN HRSG BYPASS | 0 |  |  | 17102 | 0 | N | 2017 | There are 3 CO emission limits, all listed below: Emission limit 1 = 4 ppmvd at 15%O2 on a 24-hour rolling average as determined each operating hour, except during startup (SU) and shutdown (SD). Applies in combined cycle mode. Emission limit 2 = 9 lb/hr on an hourly basis except during startup and shutdown. Applies in HRSG bypass mode. Emission limit 3 = 289 lb/hr on an hourly basis including startup and shutdown. Applies in combined cycle mode. Thermal oxidation and NSCR were considered not technically feasible for these applications.
TX-0915 | UNIT 5 | NRG CEDAR BAYOU LLC | CHAMBERS | TX |  | USA | CRAIG ECKBERG | 713-537-2776 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Ruth Alvirez, (512) 239-5220, Ruth.Alvirez@tceq.texas.gov | 160538, PSDTX1528, GHGPSDTX204 | 4911 | 221112 | Not Found | 11/05/2020 &nbsp;ACT | 03/17/2021 &nbsp;ACT | 2020-12-08 | 2022-03-08 | U |  | UNIT 5 |  | COMBINED CYCLE TURBINE | 15.21 | NATURAL GAS | 0 |  |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST | 4 | PPMVD | 3-HR ROLLING | BACT-PSD | NSPS , MACT , SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0331 | CALCASIEU PASS LNG PROJECT | VENTURE GLOBAL CALCASIEU PASS, LLC | CAMERON | LA | 70631 | USA | GRAHAM MCARTHUR | 202-759-6741 | GMCARTHUR@VGLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Ms. Mei Wu, (225)219-3180 | PDS-LA-805 | 4925 | 221210 | Not Found | 06/25/2018 &nbsp;ACT | 09/21/2018 &nbsp;ACT | 2019-02-14 | 2019-06-19 | A |  | New Liquefied Natural Gas (LNG) production, storage, and export terminal. | Application Received September 2, 2015. | Combined Cycle Combustion Turbines (CCCT1 to CCCT5) | 15.21 | Natural Gas | 921 | MM BTU/h |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Exclusive Combustion of Low Sulfur Fuel and Proper Engineering Practices | 4 | PPMV | ANNUAL AVERAGE | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | BACT limit is 4 PPMV H2S; Annual Average Content in Fuel.
LA-0364 | FG LA COMPLEX | FG LA LLC | ST. JAMES | LA | 70086 | USA | KUAN-MING PEMG | 2813026850 | KMPEMG@FPCC.COM.TW | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mr. Anthony Randall, (225)219-3180 | PSD-LA-812 | 2869 | 325110 | Not Found | 01/14/2019 &nbsp;ACT | 01/06/2020 &nbsp;ACT | 2020-05-05 | 2021-08-09 | A | https://edms.deq.louisiana.gov/app/doc/view.aspx?doc=11998450&ob=yes&child=yes | The FG LA complex will produce ethylene, propylene, ethylene glycol, high density polyethylene, low density polyethylene, linear low-density polyethylene and polypropylene. To support the operation of these production plants, the complex will also include electric power and steam generating units (Utility), wastewater treatment (Central Wastewater Treatment Plant), storage and loading operations (Logistics), and associated flare systems. | FG LA was issued PSD-LA-812 to construct the FG LA Complex which involves the construction of fourteen facilities permitted under fourteen Title V Permits to manufacture ethylene and propylene, ultimately producing high and low density polyethylene, propylene, and ethylene glycol. | Cogeneration Units | 15.21 | Natural Gas | 2222 | mm btu/h | Throughput is maximum operating rate. 2139 MM BTU/hr normal operating rate. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | B | Good combustion practices and catalytic oxidation | 4 | PPMVD |  | BACT-PSD | NSPS , NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | BACT limit is 4 ppmvd at 15% O2.
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (South Plant): A combined cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/H (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/H (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR and an oxidation catalyst. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst technology and good combustion practices. | 4 | PPMVD | AT 15%O2; NOT INCL. STARTUP/SHUTDOWN | BACT-PSD | SIP | N | 85 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in Special Condition III.2 in the permit. Startup and Shutdown hours are limited to 300 hours per 12 month rolling time period.
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (North Plant): A combined-cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | Nominal 500 MW electricity production. Turbine rating of 3,080 MMBTU/hr (HHV) and HRSG duct burner rating of 755 MMBTU/hr (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/hr (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst technology and good combustion practices. | 4 | PPMVD | AT 15%O2; HOURLY | BACT-PSD | SIP | N | 85 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emission limit 1 above does not include startup and shutdown. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in Special Condition III.2. Startup and Shutdown hours are limited to 300 hours per 12 month rolling time period.
*MI-0445 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact Mark Mitchell at 517-582-5293 or at mitchellm7@michigan.gov. Thank you. | 75-16B | 4911 | 221112 | Not found | 08/20/2019 &nbsp;ACT | 11/26/2019 &nbsp;ACT | 2020-12-22 | 2020-12-23 | A |  | Natural gas combined cycle power plant |  | FGCTGHRSG | 15.21 | Natural gas | 3421 | MMBTU/H | 3421 MMBTU/H for each turbine 740 MMBTU/H for each duct burner for a combined throughput of 4161 MMBTU/H or 8322 MMBTU/H for both trains. Two combined-cycle natural gas-fired combustion turbine generators (CTGs) with Heat Recovery Steam Generators (HRSG) (EUCTGHRSG1 & EUCTGHRSG2 in FGCTGHRSG). The total hours for startup and shutdown for each train shall not exceed 500 hours per 12-month rolling time period. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices, inlet air conditioning, and the use of pipeline quality natural gas. | 4 | PPM | PPMVD@15%O2, HOURLY; EACH | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit above is 4 ppmvd at 15% O2, hourly basis, for each CTGHRSG. Startup and shutdown operations are limited to 500 hours per 12-month rolling time period for each CTGHRSG train. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the startup and shutdown emission minimization plan. The efficiency range is 85-90 percent.
FL-0367 | SHADY HILLS COMBINED CYCLE FACILITY | SHADY HILLS ENERGY CENTER, LLC | PASCO | FL | 36410 | USA | ROY BELDEN | (203) 357-6820 | ROY.BELDEN@GE.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 1010524-001-AC | 4911 | 221112 | 110012581820 | 02/16/2018 &nbsp;ACT | 07/27/2018 &nbsp;ACT | 2019-03-19 | 2022-03-04 | B | https://arm-permit2k.dep.state.fl.us/nontv/1010524.001.AC.F.ZIP | A 573-megawatt (MW) (winter) 1-on-1 combined cycle plant which includes a heat recovery steam generator with duct firing, along with supporting equipment. Natural gas is the only permitted fuel for the combined cycle unit. | THIS PROJECT WAS SUPERSEDED BY PERMIT NO. 1010524-003-AC UNDER RBLC ID FL-0371 | 1-on-1 combined cycle unit (GE 7HA) | 15.21 | Natural Gas | 3266.9 | MMBtu/hour | One nominal 385 MW GE 7HA.02 CTG and one HRSG with duct firing [approximately 210 MMBtu/hour], and one nominal 210 MW steam turbine generator (STG) | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | Clean burning fuel with good combustion practices | 4.3 | PPMVD @15% O2 | (TURBINE LOADS â‰¥ 90%); THREE 1-HR RUNS | BACT-PSD | SIP | U | 0 | U | 7.1 | PPMVD @15% O2 | (TURBINE LOADS < 90%); THREE 1-HR RUNS | 6.5 | PPMVD @15% O2 | (WHEN DUCT FIRING); THREE 1-HR RUNS | 0 | 0 | N |  | Initial and annual stack testing required.
FL-0371 | SHADY HILLS COMBINED CYCLE FACILITY | SHADY HILLS ENERGY CENTER, LLC | PASCO | FL | 34610 | USA | ROY BELDEN |  | ROY.BELDEN@GE.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 1010524-003-AC (PSD-FL-444A) | 4911 | 221112 | 110012581820 | 04/02/2021 &nbsp;ACT | 06/07/2021 &nbsp;ACT | 2021-11-19 | 2022-03-04 | U | https://depedms.dep.state.fl.us:443/Oculus/servlet/shell?command=hitlist&[freeText=]&[folderName=]&[profile=Permitting_Authorization]&[creator=]&[entityType=any]&[createdDateTo=]&[catalog=75]&[searchBy=Profile]&[sortBy=Document Date]&[createdDate=]&{County=_EQ_PASCO}&{District=_EQ_SWD}&{Facility-Site ID=_EQ_AIR_1010524}&{Document Type=_EQ_PERMIT - FINAL}&{Facility Type=_LK_N/A}&{Application Number=_EQ_1010524003} | The Shady Hills Combined Cycle Facility (SHCCF), a new 573-megawatt (MW) (winter) 1-on-1 combined cycle electrical generating facility to be owned and operated by Shady Hills Energy Center, LLC, which will be located at 14350 Merchant Energy Way, Spring Hill, Florida. The proposed work will be conducted on an approximately 14-acre parcel east of and located adjacent to the existing Shady Hills Generating Station (SHGS) power plant, which is owned and operated by Shady Hills Power Company, L.L.C. |  | GE 7HA.02 Combustion Turbine and HRSG with Duct Firing | 15.21 | Natural Gas | 3622.1 | MMBtu/hour | Throughput based on a compressor inlet air temperature of 59Â° F, the higher heating value (HHV) of natural gas, and 100% load | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | Clean burning fuel with good combustion practices | 4.3 | PPMVD AT 15% O2 | (TURBINE LOADS â‰¥ 90%); THREE 1-HR | BACT-PSD |  | U | 0 | U | 7.1 | PPMVD AT 15% O2 | (TURBINE LOADS < 90%); THREE 1-HR | 6.5 | PPMVD AT 15% O2 | (WHEN DUCT FIRING); THREE 1-HR RUNS | 0 | 0 | N |  | Initial and annual stack testing required.
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | General Electric (GE) Combustion Turbines (P005 &amp; P006) | 15.21 | Natural gas | 3459.6 | MMBTU/H | Two identical GE Combustion Turbines 1 and 2; GE model 7HA.02 natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,459.6 MMBtu/hr (HHV) at 100% load and -2Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 570.45 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate additional electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | B | Good combustion practices and oxidation catalyst | 4.36 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 49.1 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen on a 24-hr block averaging period and 10.3 lb/h with duct burner, except startup and shutdown. 1.0 ppm by volume dry basis (ppmvd) at 15% oxygen on a 24-hr block averaging period and 4.36 lb/h without duct burner, except startup and shutdown. 49.1 tons per rolling 12 month period for all operating modes, including startup and shutdown. 4.81 tons per rolling 12 month period for startup and shutdown periods.
MI-0439 | JACKSON GENERATING STATION | CONSUMERS ENERGY COMPANY | JACKSON | MI | 49203-2174 | USA | BRIAN LABBY | 989-667-5008 | BRIAN.LABBY@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, at 517-284-6790 or at byrnesm@michigan.gov, for technical questions regarding this permit. Thank you. | 118-18 | 4911 | 221112 | 110015804511 | 11/29/2018 &nbsp;ACT | 04/02/2019 &nbsp;ACT | 2019-05-20 | 2019-06-19 | C |  | Natural gas combined-cycle power plant |  | FGLMDB1-6 (6 combined cycle natural gas fired CTG each equipped with a HRSG) | 15.21 | natural gas | 420 | MW | FGLMDB1-6 is 6 combined cycle natural gas fired combustion turbine generators (CTG) each equipped with a heat recovery steam generator (HRSG). Nominal rating 420 MW. Each combustion turbine (CT) is a GE LM6000 with a rating of 440 MMBTU/HR (HHV) and a duct burner rating of 222 MMBTU/HR (HHV). A combined cycle natural gas fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 420 MW electricity production. The HRSG is not capable of operating independently from the CTG. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Combustion inlet air filters, good combustion practices and only combust natural gas. | 4.9 | LB/H | 24-HR AVG, EACH HR UNIT OPERATES, EACH | BACT-PSD | SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit is 4.9 lb/hr on a 24-hr rolling average determined each hour the unit operates and applies to each unit. The limit is also per stack during periods when the turbine operates alone and when the turbine operates in conjunction with its respective duct burner. The limits do not apply during startup and shutdown. This limit equates to approximately 0.0078 lb/MMBTU.
MI-0439 | JACKSON GENERATING STATION | CONSUMERS ENERGY COMPANY | JACKSON | MI | 49203-2174 | USA | BRIAN LABBY | 989-667-5008 | BRIAN.LABBY@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, at 517-284-6790 or at byrnesm@michigan.gov, for technical questions regarding this permit. Thank you. | 118-18 | 4911 | 221112 | 110015804511 | 11/29/2018 &nbsp;ACT | 04/02/2019 &nbsp;ACT | 2019-05-20 | 2019-06-19 | C |  | Natural gas combined-cycle power plant |  | FGLMDB1-6 (6 combined cycle natural gas fired CTG each equipped with a HRSG) | 15.21 | natural gas | 420 | MW | FGLMDB1-6 is 6 combined cycle natural gas fired combustion turbine generators (CTG) each equipped with a heat recovery steam generator (HRSG). Nominal rating 420 MW. Each combustion turbine (CT) is a GE LM6000 with a rating of 440 MMBTU/HR (HHV) and a duct burner rating of 222 MMBTU/HR (HHV). A combined cycle natural gas fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 420 MW electricity production. The HRSG is not capable of operating independently from the CTG. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Combustion inlet air filters, good combustion practices and only combust natural gas. | 4.9 | LB/HR | 24 HR AVG DET.EACH OPERATING HR; EACH | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit above is 4.9 lb/hr on a 24-hour rolling average determined each hour the unit operates and applies to each unit. The limit is also per stack during periods when the turbine operates alone and when the turbine operates in conjunction with its respective duct burner. The limits do not apply during startup and shutdown. This limit equates to approximately 0.0078 lb/MMBTU.
AK-0085 | GAS TREATMENT PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | NORTH SLOPE BOROUGH | AK | 99734 | USA | LISA HAAS | 907.947.9353 | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - 907.465.5122 - dave.jones2@alaska.gov | AQ1524CPT01 | 4922 | 486210 | None Found | 01/25/2019 &nbsp;ACT | 08/13/2020 &nbsp;ACT | 2020-08-14 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Gas Treatment Plant (GTP) is part of one integrated liquefied natural gas (LNG) project to bring natural gas from Alaskaâ€™s North Slope to international markets in the form of LNG, as well as for in-state deliveries in the form of natural gas. The GTP will take gas from the Prudhoe Bay Unit and the Point Thomson Unit and treat/process the gas, before it is sent 807 miles through a 42-inch diameter pipeline to a liquefaction facility in Nikiski on Alaskaâ€™s Kenai Peninsula for export in foreign commerce. The emissions units at the stationary source will include cogeneration gas-fired turbines with supplemental firing duct burners for gas compression, simple cycle gas-fired turbines for power generation, gas-fired heaters for building and process heat, as well as flares for control of excess gas. In addition, the GTP will include a diesel-fired black start generator, several diesel-fired firewater pumps and emergency generators, and storage tanks for diesel and gasoline fuels. |  | Six (6) Cogeneration Gas-Fired Turbines (Treated Gas Compressor Turbines) | 15.21 | Natural Gas | 576 | MMBtu/hr | 576 MMBtu/hr includes turbine and supplemental duct burner for waste heat recovery unit for cogeneration. EUs 1-6, Treat Gas Compressor Turbines. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation catalyst and good combustion practices | 5 | PPMV @ 15% O2 | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Potential CO emissions of 18.84 tpy per turbine including supplemental firing duct burner for WHRU.
AK-0085 | GAS TREATMENT PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | NORTH SLOPE BOROUGH | AK | 99734 | USA | LISA HAAS | 907.947.9353 | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - 907.465.5122 - dave.jones2@alaska.gov | AQ1524CPT01 | 4922 | 486210 | None Found | 01/25/2019 &nbsp;ACT | 08/13/2020 &nbsp;ACT | 2020-08-14 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Gas Treatment Plant (GTP) is part of one integrated liquefied natural gas (LNG) project to bring natural gas from Alaskaâ€™s North Slope to international markets in the form of LNG, as well as for in-state deliveries in the form of natural gas. The GTP will take gas from the Prudhoe Bay Unit and the Point Thomson Unit and treat/process the gas, before it is sent 807 miles through a 42-inch diameter pipeline to a liquefaction facility in Nikiski on Alaskaâ€™s Kenai Peninsula for export in foreign commerce. The emissions units at the stationary source will include cogeneration gas-fired turbines with supplemental firing duct burners for gas compression, simple cycle gas-fired turbines for power generation, gas-fired heaters for building and process heat, as well as flares for control of excess gas. In addition, the GTP will include a diesel-fired black start generator, several diesel-fired firewater pumps and emergency generators, and storage tanks for diesel and gasoline fuels. |  | Six (6) Cogeneration Gas-Fired Turbines (CO2 Compressor Turbines)) | 15.21 | Natural Gas | 431 | MMBtu/hr | 431 MMBtu/hr includes turbine and supplemental duct burner for waste heat recovery unit for cogeneration. EUs 7-12, CO2 Compressor Turbines. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation catalyst and good combustion control practices | 5 | PPMV @ 15% O2 | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Potential particulate matter emissions of 14.41 tpy per turbine including supplemental firing duct burners for WHRU.
LA-0331 | CALCASIEU PASS LNG PROJECT | VENTURE GLOBAL CALCASIEU PASS, LLC | CAMERON | LA | 70631 | USA | GRAHAM MCARTHUR | 202-759-6741 | GMCARTHUR@VGLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Ms. Mei Wu, (225)219-3180 | PDS-LA-805 | 4925 | 221210 | Not Found | 06/25/2018 &nbsp;ACT | 09/21/2018 &nbsp;ACT | 2019-02-14 | 2019-06-19 | A |  | New Liquefied Natural Gas (LNG) production, storage, and export terminal. | Application Received September 2, 2015. | Combined Cycle Combustion Turbines (CCCT1 to CCCT5) | 15.21 | Natural Gas | 921 | MM BTU/h |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation Catalyst, Proper Design, Good Combustion Practices. | 5 | PPMV | 30 DAY ROLLING AVERAGE | BACT-PSD | OPERATING PERMIT , NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Units are ppmv @15% O2; Averaging time is 30 Day Rolling Average During Normal Operations.
IL-0133 | LINCOLN LAND ENERGY CENTER | LINCOLN LAND ENERGY CENTER (A/K/A EMBERCLEAR) | SANGAMON | IL | 62558 | USA | JIM PALUMBO | 888-582-4460 X 55 | JPALUMBO@EMBERCLEAR.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov |  | 18040008 | 4911 | 221112 | Not Found | 09/30/2021 &nbsp;ACT | 07/29/2022 &nbsp;ACT | 2022-08-26 | 2022-12-06 | A | www2.illinois.gov/epa/public-notices/boa-notices/pages/archive.aspx | The proposed facility is designed to generate baseload power. It will consist of two combined-cycle generating units, with each a Siemens combustion turbine (3,647 mmBtu/hr) and a heat recovery steam generator (HRSG) with duct burners (35 mmBtu/hr); fired by natural gas only. Other units at the facility include an auxiliary boiler, engines, piping and piping components, circuit breakers and roadways. | Additional facility-wide pollutants, in tons/year: PM10/PM 2.5: 131.7 and 131.6 (respectively); sulfuric acid mist (SAM): 17.2; greenhouse gasses (GHG): 3,586,918 | Combined-Cycle Combustion Turbines | 15.21 | Natural Gas | 3647 | mmBtu/hour | Combined-cycle comustion turbines and heat recovery steam generators (HRSG) with a 35 mmBtu/hr duct burner. Turbine inlets would have evaporative cooling systems to cool the inlet air during warm weather to increase power output. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Good combustion practices and use of natural gas with a sulfur content of no more than 0.5 grains (gr)/100 standard cubic feet (scf). | 5.5 | POUNDS/HOUR | ROLLING 3-OPERATING HOUR | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Compliance is determined by performance testing.
MI-0451 | MEC NORTH, LLC | MARSHALL ENERGY CENTER, LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 9144682402 | WLADD@DEVELOPMENTSPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Janelle Trowhill, at 517-582-5312 or at TrowhillJ1@michigan.gov for technical questions regarding this permit. Thank you. | 167-17B | 4911 | 221112 | Not Found | 12/08/2021 &nbsp;ACT | 06/23/2022 &nbsp;ACT | 2022-12-21 | 2023-04-25 | A |  | Natural gas combined-cycle power plant (two plants: north and south). | The two plants (MEC North, LLC and MEC South, LLC) will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. | EUCTGHRSG (North Plant): A combined cycle natural gas fired combustion turbine generator with heat recovery steam generator | 15.21 | Natural gas | 3064 | MMBTU/H | Throughput Information: Nominal 500 MW electricity production. Turbine rating of 3,064 MMBTU/hr (HHV) and HRSG duct burner rating of 889 MMBTU/Hr (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,064 MMBTU/hr (HHV). The HRSG is equipped with a natural gas fired duct burner, with a maximum heat input rating of 889 MMBTU/hr (HHV) and rated at 874 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, inlet air conditioning, and the use of pipeline quality natural gas. | 5.7 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N | 2017 | (5.7 pph is equivalent to 0.002 lb/MMBTU, which is about 30 percent of PM10 and PM2.5) The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. Pulse Jet Fabric Filter Baghouse: average of $334,000 per ton Mechanical Shaker Fabric Filter Baghouse: average of $370,500 per ton Reverse-Air Fabric Filter Baghouse: average of $437,000 per ton Dry ESP (Wire-Plate Type): average of $438,500 per ton Dry ESP (Wire-Pipe Type): average of $278,500 per ton Wet ESP (Wire-Plate Type): average of $528,500 per ton Wet ESP (Wire-Pipe Type): average of $403,000 per ton Venturi Scrubber: average of $1,321,000 per ton
MI-0452 | MEC SOUTH, LLC | MARSHALL ENERGY CENTER, LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 9144682402 | WLADD@DEVELOPMENTSPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer, Janelle Trowhill at TrowhillJ1@michigan.gov or at 517-582-5312. Thank you. | 168-17B | 4911 | 221112 | Not Found | 12/08/2021 &nbsp;ACT | 06/23/2022 &nbsp;ACT | 2022-12-22 | 2023-04-25 | A |  | Natural gas combined cycle power plant (Two Plants: North and South) | The two plants (MEC North, LLC and MEC South, LLC) will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. | EUCTGHRSG (South Plant): A combined-cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 3064 | MMBTU/H | Nominal 500 MW electricity production. Turbine rating of 3064 MMBTU/H (HHV) and HRSG duct burner rating of 889 MMBTU/H (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,064 MMBTU/hr (HHV). The HRSG is equipped with a natural gas fired duct burner, with a maximum heat input rating of 889 MMBTU/hr (HHV) and rated at 874 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion Practices, inlet air conditioning, and the use of pipeline quality natural gas | 5.7 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N | 2017 | (5.7 pph is equivalent to 0.002 lb/MMBTU, which is about 30 percent of PM10 and PM2.5) The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. Pulse Jet Fabric Filter Baghouse: average of $334,000 per ton Mechanical Shaker Fabric Filter Baghouse: average of $370,500 per ton Reverse-Air Fabric Filter Baghouse: average of $437,000 per ton Dry ESP (Wire-Plate Type): average of $438,500 per ton Dry ESP (Wire-Pipe Type): average of $278,500 per ton Wet ESP (Wire-Plate Type): average of $528,500 per ton Wet ESP (Wire-Pipe Type): average of $403,000 per ton Venturi Scrubber: average of $1,321,000 per ton
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (South Plant): A combined cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/H (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/H (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR and an oxidation catalyst. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, inlet air conditioning, and the use of pipeline quality natural gas. | 5.8 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N | 2017 | 5.8 pph is equivalent to 0.002 lb/MMBTU, which is about 30 percent of PM10 and PM2.5. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. Pulse Jet Fabric Filter Baghouse: average of $334,000 per ton Mechanical Shaker Fabric Filter Baghouse: average of $370,500 per ton Reverse-Air Fabric Filter Baghouse: average of $437,000 per ton Dry ESP (Wire-Plate Type): average of $438,500 per ton Dry ESP (Wire-Pipe Type): average of $278,500 per ton Wet ESP (Wire-Plate Type): average of $528,500 per ton Wet ESP (Wire-Pipe Type): average of $403,000 per ton Venturi Scrubber: average of $1,321,000 per ton
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (North Plant): A combined-cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | Nominal 500 MW electricity production. Turbine rating of 3,080 MMBTU/hr (HHV) and HRSG duct burner rating of 755 MMBTU/hr (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/hr (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, inlet air conditioning, and the use of pipeline quality natural gas. | 5.8 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N | 2017 | (5.8 lb/hr is equivalent to 0.002 lb/MMBTU which is about 30 percent of PM10 and PM2.5) The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10 which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. Pulse jet fabric filter baghouse: average of $334,000 per ton. Mechanical shaker fabric filter baghouse: average of $370,500 per ton Reverse-Air fabric filter baghouse: average of $437,000 per ton Dry ESP (Wire-plate type): average of $438,500 per ton Dry ESP (Wire-pipe type): average of $278,500 per ton Wet ESP (Wire-plate type): average of $528,500 per ton Wet ESP (Wire-pipe type): average of $403,000 per ton Venturi Scrubber: average of $1,321,000 per ton.
MI-0441 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, for technical questions regarding this permit. She may be reached at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 74-18 | 4911 | 221112 | 110040958425 | 10/16/2018 &nbsp;ACT | 12/21/2018 &nbsp;ACT | 2019-10-18 | 2021-08-09 | D |  | Natural gas combined-cycle power plant. | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG2--A 667 MMBTU/H natural gas fired CTG with a HRSG. | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG2 is a nominally rated 667 MMBTU/H natural gas fired CTG coupled with a HRSG. The HRSG is equipped with a natural gas fired duct burner rated at 204 MMBTU/h to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a DLNB, SCR and oxidation catalyst. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas, inlet air conditioning, and good combustion practices. | 6.02 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emission limit 1 of 6.02 lb/h applies during all operating modes. Add-on control technology was not technically feasible; however, options were evaluated and it was determined they were not economically feasible.
MI-0441 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, for technical questions regarding this permit. She may be reached at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 74-18 | 4911 | 221112 | 110040958425 | 10/16/2018 &nbsp;ACT | 12/21/2018 &nbsp;ACT | 2019-10-18 | 2021-08-09 | D |  | Natural gas combined-cycle power plant. | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG1--A 667 MMBTU/H NG fired combustion turbine generator coupled with a heat recovery steam generator (HRSG) | 15.21 | Natural gas | 667 | MMBTU/H | A nominally rated 667 MMBTU/hr natural gas-fired combustion turbine generator (CTG) coupled with a heat recovery steam generator (HRSG). The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBTU/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a dry low NOx burner (DLNB), selective catalytic reduction (SCR) and oxidation catalyst. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas, inlet air conditioning, and good combustion practices. | 6.02 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit above is during all operating modes. Add-on control technology was not technically feasible; however, options were evaluated and it was determined they were not economically feasible.
MI-0447 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-648-6339 or at ByrnesM@michigan.gov for technical questions related to this permit. Thank you. | 74-18A | 4911 | 221112 | 110040958425 | 09/22/2020 &nbsp;ACT | 01/07/2021 &nbsp;ACT | 2021-06-28 | 2021-09-10 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG1 | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG1--A nominally rated 667 MMBTU/hr natural gas-fired combustion turbine generator (CTG) coupled with a heat recovery steam generator (HRSG). The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBTU/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a dry low NOx burner (DLNB), selective catalytic reduction (SCR), and oxidation catalyst. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas, inlet air conditioning, and good combustion practices. | 6.02 | LB/H | HOURLY; APPLIES DURING ALL OPERAT. MODES | BACT-PSD | SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Add-on control technology was not technically feasible; however, options were evaluated, and it was determined they were not economically feasible.
MI-0447 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-648-6339 or at ByrnesM@michigan.gov for technical questions related to this permit. Thank you. | 74-18A | 4911 | 221112 | 110040958425 | 09/22/2020 &nbsp;ACT | 01/07/2021 &nbsp;ACT | 2021-06-28 | 2021-09-10 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG2 | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG2--A nominally rated 667 MMBTU/hr natural gas-fired CTG coupled with a HRSG. The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBTU/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a DLNB, SCR, and oxidation catalyst. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas, inlet air conditioning, and good combustion practices. | 6.02 | LB/H | HOURLY; APPLIES DURING ALL OPERAT. MODES | BACT-PSD | SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Add-on control technology was not technically feasible; however, options were evaluated, and it was determined they were not economically feasible.
MI-0454 | LBWL-ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions about this permit, please contact the permit engineer, Lauren Magirl, at 517-582-5345, or at MagirlL@michigan.gov. Thank you. | 74-18D | 4911 | 221112 | Not Found | 10/25/2022 &nbsp;ACT | 12/20/2022 &nbsp;ACT | 2022-12-29 | 2023-05-23 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWLâ€™s existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG1 | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG1- A nominally rated 667 MMBtu/hr natural gas-fired combustion turbine generator (CTG) coupled with a heat recovery steam generator (HRSG). The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBtu/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a dry low NOx burner (DLNB), selective catalytic reduction (SCR), and oxidation catalyst. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas, inlet air conditioning, and good combustion practices. | 6.02 | LB/H | HOURLY; APPLIES DURING ALL OPER. MODES | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Add-on control technology was not technically feasible; however, options were evaluated, and it was determined they were not economically feasible.
MI-0454 | LBWL-ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions about this permit, please contact the permit engineer, Lauren Magirl, at 517-582-5345, or at MagirlL@michigan.gov. Thank you. | 74-18D | 4911 | 221112 | Not Found | 10/25/2022 &nbsp;ACT | 12/20/2022 &nbsp;ACT | 2022-12-29 | 2023-05-23 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWLâ€™s existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG2 | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG2- A nominally rated 667 MMBtu/hr natural gas-fired CTG coupled with a HRSG. The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBtu/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a DLNB, SCR, and oxidation catalyst. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas, inlet air conditioning, and good combustion practices. | 6.02 | LB/H | HOURLY; APPLIES DURING ALL MODES | BACT-PSD | SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Add-on control technology was not technically feasible; however, options were evaluated, and it was determined they were not economically feasible.
MI-0441 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, for technical questions regarding this permit. She may be reached at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 74-18 | 4911 | 221112 | 110040958425 | 10/16/2018 &nbsp;ACT | 12/21/2018 &nbsp;ACT | 2019-10-18 | 2021-08-09 | D |  | Natural gas combined-cycle power plant. | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG2--A 667 MMBTU/H natural gas fired CTG with a HRSG. | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG2 is a nominally rated 667 MMBTU/H natural gas fired CTG coupled with a HRSG. The HRSG is equipped with a natural gas fired duct burner rated at 204 MMBTU/h to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a DLNB, SCR and oxidation catalyst. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas, inlet air conditioning, and good combustion practices. | 6.02 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emission limit 1 of 6.02 lb/h applies during all operating modes. Add-on control technology was not technically feasible; however options were evaluated, and it was determined they were not economically feasible.
MI-0441 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, for technical questions regarding this permit. She may be reached at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 74-18 | 4911 | 221112 | 110040958425 | 10/16/2018 &nbsp;ACT | 12/21/2018 &nbsp;ACT | 2019-10-18 | 2021-08-09 | D |  | Natural gas combined-cycle power plant. | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG1--A 667 MMBTU/H NG fired combustion turbine generator coupled with a heat recovery steam generator (HRSG) | 15.21 | Natural gas | 667 | MMBTU/H | A nominally rated 667 MMBTU/hr natural gas-fired combustion turbine generator (CTG) coupled with a heat recovery steam generator (HRSG). The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBTU/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a dry low NOx burner (DLNB), selective catalytic reduction (SCR) and oxidation catalyst. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas, inlet air conditioning and good combustion practices. | 6.02 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit above is during all operating modes. Add-on control technology was not technically feasible; however, options were evaluated and it was determined they were not economically feasible.
MI-0447 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-648-6339 or at ByrnesM@michigan.gov for technical questions related to this permit. Thank you. | 74-18A | 4911 | 221112 | 110040958425 | 09/22/2020 &nbsp;ACT | 01/07/2021 &nbsp;ACT | 2021-06-28 | 2021-09-10 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG1 | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG1--A nominally rated 667 MMBTU/hr natural gas-fired combustion turbine generator (CTG) coupled with a heat recovery steam generator (HRSG). The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBTU/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a dry low NOx burner (DLNB), selective catalytic reduction (SCR), and oxidation catalyst. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas, inlet air conditioning, and good combustion practices. | 6.02 | LB/H | HOURLY; APPLIES DURING ALL OPERAT. MODES | BACT-PSD | SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Add-on control technology was not technically feasible; however, options were evaluated, and it was determined they were not economically feasible.
MI-0447 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-648-6339 or at ByrnesM@michigan.gov for technical questions related to this permit. Thank you. | 74-18A | 4911 | 221112 | 110040958425 | 09/22/2020 &nbsp;ACT | 01/07/2021 &nbsp;ACT | 2021-06-28 | 2021-09-10 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG2 | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG2--A nominally rated 667 MMBTU/hr natural gas-fired CTG coupled with a HRSG. The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBTU/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a DLNB, SCR, and oxidation catalyst. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas, inlet air conditioning, and good combustion practices. | 6.02 | LB/H | HOURLY; APPLIES DURING ALL OPERAT. MODES | BACT-PSD | SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Add-on control technology was not technically feasible; however, options were evaluated, and it was determined they were not economically feasible.
MI-0454 | LBWL-ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions about this permit, please contact the permit engineer, Lauren Magirl, at 517-582-5345, or at MagirlL@michigan.gov. Thank you. | 74-18D | 4911 | 221112 | Not Found | 10/25/2022 &nbsp;ACT | 12/20/2022 &nbsp;ACT | 2022-12-29 | 2023-05-23 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWLâ€™s existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG1 | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG1- A nominally rated 667 MMBtu/hr natural gas-fired combustion turbine generator (CTG) coupled with a heat recovery steam generator (HRSG). The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBtu/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a dry low NOx burner (DLNB), selective catalytic reduction (SCR), and oxidation catalyst. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas, inlet air conditioning, and good combustion practices. | 6.02 | LB/H | HOURLY; APPLIES DURING ALL OPERAT. MODES | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Add-on control technology was not technically feasible; however, options were evaluated, and it was determined they were not economically feasible.
MI-0454 | LBWL-ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions about this permit, please contact the permit engineer, Lauren Magirl, at 517-582-5345, or at MagirlL@michigan.gov. Thank you. | 74-18D | 4911 | 221112 | Not Found | 10/25/2022 &nbsp;ACT | 12/20/2022 &nbsp;ACT | 2022-12-29 | 2023-05-23 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWLâ€™s existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG2 | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG2- A nominally rated 667 MMBtu/hr natural gas-fired CTG coupled with a HRSG. The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBtu/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a DLNB, SCR, and oxidation catalyst. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas, inlet air conditioning, and good combustion practices. | 6.02 | LB/H | HOURLY, APPLY DURING ALL OPERATING MODES | BACT-PSD | SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Add-on control technology was not technically feasible; however, options were evaluated, and it was determined they were not economically feasible.
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (South Plant): A combined cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/H (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/H (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR and an oxidation catalyst. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Good combustion practices and the use of pipeline quality natural gas. | 6.6 | LB/H | HOURLY | BACT-PSD | NSPS , SIP | N | 0 | N | 0.6 | GR S/100 SCF | FUEL SUPPLIER RECORDS | 0 |  |  | 0 | 0 | N |  | There are 3 emission limits and one material limit in the permit as follows: Emission Limit 1 = 6.6 LB/H Emission Limit 2 = 0.6 GR Sulfur/100 scf Emission Limit 3 = 0.060 LB/MMBTU from the NSPS Emission Limit 4 is a NSPS natural gas material limit of 20 grains of sulfur per 100 scf. Even though MEC determined FGD to be technically infeasible due to the low SO2 content in the flue gas, they also provided an economic analysis. The use of pipeline quality natural gas and good combustion practices were used for the emission calculations. All reductions in emissions were with these potential control options already incorporated as baseline conditions. They concluded that with costs of over $200,000 per ton of controlled SO2 and H2SO4 combined, FGD also would not be economically feasible.
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (North Plant): A combined-cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | Nominal 500 MW electricity production. Turbine rating of 3,080 MMBTU/hr (HHV) and HRSG duct burner rating of 755 MMBTU/hr (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/hr (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Good combustion practices and the use of pipeline quality natural gas. | 6.6 | LB/H | HOURLY | BACT-PSD | NSPS , SIP | N | 0 | N | 0.6 | GR S/100 SCF | FUEL SUPPLIER RECORDS | 0 |  |  | 0 | 0 | N |  | There is a 3rd emission limit which is 0.060 lb/MMBTU based on the NSPS. There is also a NSPS natural gas material limit of 20 grains of sulfur per 100 scf. Even though MEC determined FGD to be technically infeasible due to the low SO2 content in the flue gas, they also provided an economic analysis. The use of pipeline quality natural gas and good combustion practices were used for the emission calculations. All reductions in emissions were with these potential control options already incorporated as baseline conditions. They concluded that with costs of over $200,000 per ton of controlled SO2 and H2SO4 combined, FGD also would not be economically feasible.
MI-0451 | MEC NORTH, LLC | MARSHALL ENERGY CENTER, LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 9144682402 | WLADD@DEVELOPMENTSPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Janelle Trowhill, at 517-582-5312 or at TrowhillJ1@michigan.gov for technical questions regarding this permit. Thank you. | 167-17B | 4911 | 221112 | Not Found | 12/08/2021 &nbsp;ACT | 06/23/2022 &nbsp;ACT | 2022-12-21 | 2023-04-25 | A |  | Natural gas combined-cycle power plant (two plants: north and south). | The two plants (MEC North, LLC and MEC South, LLC) will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. | EUCTGHRSG (North Plant): A combined cycle natural gas fired combustion turbine generator with heat recovery steam generator | 15.21 | Natural gas | 3064 | MMBTU/H | Throughput Information: Nominal 500 MW electricity production. Turbine rating of 3,064 MMBTU/hr (HHV) and HRSG duct burner rating of 889 MMBTU/Hr (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,064 MMBTU/hr (HHV). The HRSG is equipped with a natural gas fired duct burner, with a maximum heat input rating of 889 MMBTU/hr (HHV) and rated at 874 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Good combustion practices and the use of pipeline quality natural gas. | 6.6 | LB/H | HOURLY | BACT-PSD | NSPS , SIP | N | 0 | N | 0.6 | GR/SCF | 0.6 GR SULFUR/100 SCF; FUEL SUPPLIER REC | 0 |  |  | 0 | 0 | N |  | There are 3 SO2 emission limits, see below: Emission limit 1 is 6.6 lbs/hr, hourly with underlying applicable requirements of BACT, NAAQS and PSD increment. Emission limit 2 is 0.060 lb/MMBTU, hourly, with an underlying applicable requirement of NSPS. Emission limit 3 is 0.6 gr sulfur/100 scf, based on fuel supplier records, with applicable requirements of BACT, NAAQS and PSD increment. There is also a NSPS natural gas material limit of 20 grains of sulfur per 100 scf. Even though MEC determined FGD to be technically infeasible due to the low SO2 content in the flue gas, they also provided an economic analysis. The use of pipeline quality natural gas and good combustion practices were used for the emission calculations. All reductions in emissions were with these potential control options already incorporated as baseline conditions. They concluded that with costs of over $200,000 per ton of controlled SO2 and H2SO4 combined, FGD also would not be economically feasible.
MI-0452 | MEC SOUTH, LLC | MARSHALL ENERGY CENTER, LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 9144682402 | WLADD@DEVELOPMENTSPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer, Janelle Trowhill at TrowhillJ1@michigan.gov or at 517-582-5312. Thank you. | 168-17B | 4911 | 221112 | Not Found | 12/08/2021 &nbsp;ACT | 06/23/2022 &nbsp;ACT | 2022-12-22 | 2023-04-25 | A |  | Natural gas combined cycle power plant (Two Plants: North and South) | The two plants (MEC North, LLC and MEC South, LLC) will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. | EUCTGHRSG (South Plant): A combined-cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 3064 | MMBTU/H | Nominal 500 MW electricity production. Turbine rating of 3064 MMBTU/H (HHV) and HRSG duct burner rating of 889 MMBTU/H (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,064 MMBTU/hr (HHV). The HRSG is equipped with a natural gas fired duct burner, with a maximum heat input rating of 889 MMBTU/hr (HHV) and rated at 874 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Good Combustion Practices and the use of pipeline quality natural gas | 6.6 | LB/H | HOURLY | BACT-PSD | NSPS , SIP | N | 0 | N | 0.6 | GR/SCF | FUEL SUPPLIER RECORDS | 0 |  |  | 0 | 0 | N |  | There are 3 SO2 emission limits described below: Emission limit 1 = 6.6 lbs/hr on an hourly basis. The applicable requirements are BACT, NAAQS and PSD increment Emission limit 2 = 0.6 gr sulfur/100 scf based on fuel supplier records. The applicable requirements are BACT, NAAQS and PSD increment. Emission limit 3 = 0.060 lb/MMBTU on an hourly basis. The applicable requirement is the NSPS. There is also a NSPS natural gas material limit of 20 grains of sulfur per 100 scf. Even though MEC determined FGD to be technically infeasible due to the low SO2 content in the flue gas, they also provided an economic analysis. The use of pipeline quality natural gas and good combustion practices were used for the emission calculations. All reductions in emissions were with these potential control options already incorporated as baseline conditions. They concluded that with costs of over $200,000 per ton of controlled SO2 and H2SO4 combined, FGD also would not be economically feasible.
*WV-0032 | BROOKE COUNTY POWER PLANT | ESC BROOKE COUNTY POWER I, LLC | BROOKE | WV | 26035 | USA | ANDREW DORN | 7163121042 | DREW.DORN@ENSOLCONSORTIUM.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Engineer: Mr. Steve Pursley 304-926-0499 x1218 Steven.R.Pursley@wv.gov | R14-0035 | 4911 | 221112 | Not Found | 03/30/2018 &nbsp;ACT | 09/18/2018 &nbsp;ACT | 2018-12-20 | 2022-06-28 | A |  | Nominal 925 mWe natural gas-fired combined-cycle power plant. Small sources: Emergency Generator, Fire Water Pump, Fuel Gas Heater not included in RBLC - may request info or see permit for details. |  | GE 7HA.01 Turbine | 15.21 | Natural Gas/Ethane | 2737.7 | mmBtu/hr | Facility has 2 identical units, only 1 entry in RBLC. Nominal 462.5 mWe. All emission limits steady-state and include 424 mmBtu/hr Duct Burner in operation. Short Term startup and shutdown limits in lb/event given in permit. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Oxidation Catalyst, Good Combustion Practices | 8.1 | LB/HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 2 | PPM |  | 0 | 0 | N |  | VOC BACT is different for no Duct Firing = 1ppm
MI-0454 | LBWL-ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions about this permit, please contact the permit engineer, Lauren Magirl, at 517-582-5345, or at MagirlL@michigan.gov. Thank you. | 74-18D | 4911 | 221112 | Not Found | 10/25/2022 &nbsp;ACT | 12/20/2022 &nbsp;ACT | 2022-12-29 | 2023-05-23 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWLâ€™s existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG1 | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG1- A nominally rated 667 MMBtu/hr natural gas-fired combustion turbine generator (CTG) coupled with a heat recovery steam generator (HRSG). The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBtu/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a dry low NOx burner (DLNB), selective catalytic reduction (SCR), and oxidation catalyst. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | An oxidation catalyst for CO control for each CTG/HRSG unit, good combustion practices. | 9 | LB/H | HOURLY EXCEPT DURING SU/SD | BACT-PSD | SIP | N | 0 | N | 289 | LB/H | HOURLY INCL SU/SD IN COMB CYC MODE | 0 |  |  | 0 | 0 | N |  | There are 3 CO emission limits and all 3 will be listed below. Emission limit 1 (above) = 9 lbs/hr on an hourly basis except during startup (SU) and shutdown (SD). Applies in HRSG bypass mode. Emission limit 2 (above) = 289 lbs/hr on an hourly basis including startup and shutdown. Applies in combined cycle mode. Emission limit 3 = 4 ppmvd at 15%O2 on a 24-hour rolling average as determined each operating hour, except during startup and shutdown. Applies in combined cycle mode. Thermal oxidation and NSCR were considered not technically feasible for these applications.
NJ-0088 | COGEN TECH LINDEN VENTURE LP | COGEN TECH LINDEN VENTURE LP | UNION | NJ | 7036 | USA | NATALIE SESTO | (908) 523-4320 | NATALIE.SESTO@NAES.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Permit Writer: Eleonora Kats (Eleonora.kats@dep.nj.gov) Supervisor: Yogesh Doshi (yogesh.doshi@dep.nj.gov) | 41809 / BOP170001 | 4932 | 221112 | 110066826019 | 06/08/2017 &nbsp;ACT | 07/30/2019 &nbsp;ACT | 2019-09-30 | 2021-08-09 | B |  | 1182 megawatts (MW) electric and steam generating plant | New 250 MW General Electric (GE) 7F.05 CCCT with unfired heat recovery steam generator combusting natural gas (primary fuel) and back up ULSD equivalent to 800 hours per year. | 250 MW COMBINED CYCLE COMBUSTION TURBINE FIRING NATURAL GAS | 15.21 | Natural Gas | 21042 | MMCubic ft/yr | One New 250 MW General Electric 7F.05 Combined cycle combustion turbine with a Maximum heat Input rate of Size: 2517 MMBtu/hr (HHV) at 10 degrees F, equipped with add-on controls and SCR and Oxidation Catalyst. | Particulate matter, filterable (FPM) | Other - NJ TEST METHOD | (Particulate Matter (PM)) | PM | P | USE OF CLEAN NATURAL GAS AND ULSD CLEAN BURNING FUELS | 9.3 | LB/H | AV OF THREE ONE H STACK TESTS EVERY 5 YR | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0331 | CALCASIEU PASS LNG PROJECT | VENTURE GLOBAL CALCASIEU PASS, LLC | CAMERON | LA | 70631 | USA | GRAHAM MCARTHUR | 202-759-6741 | GMCARTHUR@VGLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Ms. Mei Wu, (225)219-3180 | PDS-LA-805 | 4925 | 221210 | Not Found | 06/25/2018 &nbsp;ACT | 09/21/2018 &nbsp;ACT | 2019-02-14 | 2019-06-19 | A |  | New Liquefied Natural Gas (LNG) production, storage, and export terminal. | Application Received September 2, 2015. | Combined Cycle Combustion Turbines (CCCT1 to CCCT5) | 15.21 | Natural Gas | 921 | MM BTU/h |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Exclusive Combustion of Fuel Gas and Good Combustion Practices. | 9.53 | LB/H | 3 HOUR AVERAGE | BACT-PSD | OPERATING PERMIT , NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Averaging time 3-hour Average during duct burner and turbine operations.
LA-0331 | CALCASIEU PASS LNG PROJECT | VENTURE GLOBAL CALCASIEU PASS, LLC | CAMERON | LA | 70631 | USA | GRAHAM MCARTHUR | 202-759-6741 | GMCARTHUR@VGLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Ms. Mei Wu, (225)219-3180 | PDS-LA-805 | 4925 | 221210 | Not Found | 06/25/2018 &nbsp;ACT | 09/21/2018 &nbsp;ACT | 2019-02-14 | 2019-06-19 | A |  | New Liquefied Natural Gas (LNG) production, storage, and export terminal. | Application Received September 2, 2015. | Combined Cycle Combustion Turbines (CCCT1 to CCCT5) | 15.21 | Natural Gas | 921 | MM BTU/h |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Exclusive Combustion of Fuel Gas and Good Combustion Practices. | 9.53 | LB/H | 3 HOUR AVERAGE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Averaging time 3-hour Average during duct burner and turbine operations.
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | Mitsubishi Hitachi Power Systems (MHPS) Combustion Turbines (P007 &amp; P008) | 15.21 | Natural gas | 3231 | MMBTU/H | Two identical MHPS Combustion Turbines 1 and 2; Mitsubishi Model M501JAC natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,231 MMBtu/hr (HHV) at 100% load and 51Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 306 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | B | Good combustion practices and oxidation catalyst | 9.8 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 84.7 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen and 9.8 lb/h with duct burner, except startup and shutdown. 1.0 ppm by volume dry basis (ppmvd) at 15% oxygen and 4.7 lb/h without duct burner, except startup and shutdown. 84.7 tons per rolling 12 month period for all operating modes, including startup and shutdown. 42.50 tons per rolling 12 month period for startup and shutdown periods.
*MI-0445 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact Mark Mitchell at 517-582-5293 or at mitchellm7@michigan.gov. Thank you. | 75-16B | 4911 | 221112 | Not found | 08/20/2019 &nbsp;ACT | 11/26/2019 &nbsp;ACT | 2020-12-22 | 2020-12-23 | A |  | Natural gas combined cycle power plant |  | FGCTGHRSG | 15.21 | Natural gas | 3421 | MMBTU/H | 3421 MMBTU/H for each turbine 740 MMBTU/H for each duct burner for a combined throughput of 4161 MMBTU/H or 8322 MMBTU/H for both trains. Two combined-cycle natural gas-fired combustion turbine generators (CTGs) with Heat Recovery Steam Generators (HRSG) (EUCTGHRSG1 & EUCTGHRSG2 in FGCTGHRSG). The total hours for startup and shutdown for each train shall not exceed 500 hours per 12-month rolling time period. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, inlet air conditioning, and the use of pipeline quality natural gas. | 9.9 | LB/H | HOURLY; EACH CTGHRSG | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit above is for each CTGHRSG in the flexible group FGCTGHRSG. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. The dollar value year used was 2014. â€¢ Pulse Jet Fabric Filter Baghouse: minimum of $364,528 per ton â€¢ Mechanical Shaker Fabric Filter Baghouse: minimum of $404,724 per ton â€¢ Reverse-Air Fabric Filter Baghouse: minimum of $476,689 per ton â€¢ Dry ESP (Wire-Plate Type): minimum of $478,806 per ton â€¢ Dry ESP (Wire-Pipe Type): minimum of $303,809 per ton â€¢ Wet ESP (Wire-Plate Type): minimum of $576,763 per ton â€¢ Wet ESP (Wire-Pipe Type): minimum of $440,047 per ton â€¢ Venturi Scrubber: minimum of $1,445,564 per ton
MI-0432 | NEW COVERT GENERATING FACILITY | NEW COVERT GENERATING COMPANY, LLC | VAN BUREN | MI | 49043 | USA | JOHN REESE | 212-792-0897 | JREESE@EASTERNGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 186-17 | 4911 | 221112 | Not Found | 04/17/2018 &nbsp;ACT | 07/30/2018 &nbsp;ACT | 2018-08-13 | 2019-02-19 | C |  | Power plant | The equipment consists of three advanced firing temperature Mitsubishi 501G combustion turbines, three heat recovery steam generators supplemented with gas-fired duct burners each with a max firing rate of 256 million British thermal units per hour (MMBtu/hr), three steam turbine generators. Auxiliary equipment includes three mechanical draft evaporative cooling towers, one natural gas auxiliary boiler, one diesel emergency generator, one diesel fire water pump, one aqueous parts cleaner, and one gas heater. | FG-TURB/DB1-3 (3 combined cycle combustion turbine and heat recovery steam generator trains) | 15.21 | Natural gas | 1230 | MW | Three (3) combined-cycle combustion turbine (CT) / heat recovery steam generator (HRSG) trains. Each CT is a natural gas fired Mitsubishi model 501G, equipped with dry low NOx combustor and inlet air evaporative cooling. Each HRSG includes a natural gas fired duct burner with a 256 MMBtu/hr heat input capacity and a dry low NOx burner. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Use clean fuel (natural gas) and good combustion practices. | 10.7 | LB/H | HOURLY; EACH CT/HRSG TRAIN | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0432 | NEW COVERT GENERATING FACILITY | NEW COVERT GENERATING COMPANY, LLC | VAN BUREN | MI | 49043 | USA | JOHN REESE | 212-792-0897 | JREESE@EASTERNGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 186-17 | 4911 | 221112 | Not Found | 04/17/2018 &nbsp;ACT | 07/30/2018 &nbsp;ACT | 2018-08-13 | 2019-02-19 | C |  | Power plant | The equipment consists of three advanced firing temperature Mitsubishi 501G combustion turbines, three heat recovery steam generators supplemented with gas-fired duct burners each with a max firing rate of 256 million British thermal units per hour (MMBtu/hr), three steam turbine generators. Auxiliary equipment includes three mechanical draft evaporative cooling towers, one natural gas auxiliary boiler, one diesel emergency generator, one diesel fire water pump, one aqueous parts cleaner, and one gas heater. | FG-TURB/DB1-3 (3 combined cycle combustion turbine and heat recovery steam generator trains) | 15.21 | Natural gas | 1230 | MW | Three (3) combined-cycle combustion turbine (CT) / heat recovery steam generator (HRSG) trains. Each CT is a natural gas fired Mitsubishi model 501G, equipped with dry low NOx combustor and inlet air evaporative cooling. Each HRSG includes a natural gas fired duct burner with a 256 MMBtu/hr heat input capacity and a dry low NOx burner. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Use clean fuel (natural gas) and good combustion practices. | 10.7 | LB/H | HOURLY; EACH CT/HRSG TRAIN | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0878 | LNG EXPORT TERMINAL | PORT ARTHUR LNG, LLC | JEFFERSON | TX |  | USA | J.D. MORRIS | 713-298-5476 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Benjamin Hansen, Ph.D., P.E., (512) 239-4578, Benjamin.Hansen@tceq.texas.gov | 158420, PSDTX1572, GHGPSDTX198 | 4922 | 486210 | Not FOUND | 05/27/2020 &nbsp;ACT | 09/15/2022 &nbsp;ACT | 2019-11-07 | 2023-05-23 | A |  | Liquefied natural gas (LNG) export terminal. |  | Refrigeration Compression Turbines | 15.21 | NATURAL GAS | 26.92 | MMTON/Y | Eight GE Frame 7E gas turbines for refrigeration and compression at the site. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Dry low NOx burners and good combustion practices. | 11 | LB/HR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*WV-0029 | HARRISON COUNTY POWER PLANT | ESC HARRISON COUNTY POWER, LLC | HARRISON | WV | 26301 | USA | ANDREW DORN | 7163121042 | DREWDORN@ENSOLCONSORTIUM.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Engineer: Mr. Steve Pursley 304-926-0499 x1218 steven.r.pursley@wv.gov | R14-0036 | 4911 | 221112 | Not Found | 04/26/2017 &nbsp;ACT | 03/27/2018 &nbsp;ACT | 2018-06-25 | 2022-06-28 | A | https://dep.wv.gov/daq/Documents/March 2018 Permits and Evals/033-00264_PERM_R14-0036.pdf | Nominal 640 mWe natural gas-fired combined-cycle power plant. Small sources: Emergency Generator, Fire Water Pump, Fuel Gas Heater not included in RBLC - may request info or see permit for details. |  | GE 7HA.02 Turbine | 15.21 | Natural Gas | 3496.2 | mmBtu/hr | Nominal 640 mWe All emission limits steady-state and include 1000 mmBtu/hr Duct Burner in operation Short Term startup and shutdown limits in lb/event given in permit. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation Catalyst, Good Combustion Practices | 11.4 | LB/HR |  | BACT-PSD |  | U | 0 | U | 54.8 | TONS/YEAR |  | 2 | PPM |  | 0 | 0 | N |  | VOC BACT is different for no Duct Firing = 1ppm
NJ-0088 | COGEN TECH LINDEN VENTURE LP | COGEN TECH LINDEN VENTURE LP | UNION | NJ | 7036 | USA | NATALIE SESTO | (908) 523-4320 | NATALIE.SESTO@NAES.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Permit Writer: Eleonora Kats (Eleonora.kats@dep.nj.gov) Supervisor: Yogesh Doshi (yogesh.doshi@dep.nj.gov) | 41809 / BOP170001 | 4932 | 221112 | 110066826019 | 06/08/2017 &nbsp;ACT | 07/30/2019 &nbsp;ACT | 2019-09-30 | 2021-08-09 | B |  | 1182 megawatts (MW) electric and steam generating plant | New 250 MW General Electric (GE) 7F.05 CCCT with unfired heat recovery steam generator combusting natural gas (primary fuel) and back up ULSD equivalent to 800 hours per year. | 250 MW COMBINED CYCLE COMBUSTION TURBINE FIRING NATURAL GAS | 15.21 | Natural Gas | 21042 | MMCubic ft/yr | One New 250 MW General Electric 7F.05 Combined cycle combustion turbine with a Maximum heat Input rate of Size: 2517 MMBtu/hr (HHV) at 10 degrees F, equipped with add-on controls and SCR and Oxidation Catalyst. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | USE OF NATURAL GAS AND ULSD; BOTH CLEAN BURNING FUELS | 11.58 | LB/H | AV OF THREE ONE H STACK TESTS EVERY 5 YR | BACT-PSD | OPERATING PERMIT | U | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0088 | COGEN TECH LINDEN VENTURE LP | COGEN TECH LINDEN VENTURE LP | UNION | NJ | 7036 | USA | NATALIE SESTO | (908) 523-4320 | NATALIE.SESTO@NAES.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Permit Writer: Eleonora Kats (Eleonora.kats@dep.nj.gov) Supervisor: Yogesh Doshi (yogesh.doshi@dep.nj.gov) | 41809 / BOP170001 | 4932 | 221112 | 110066826019 | 06/08/2017 &nbsp;ACT | 07/30/2019 &nbsp;ACT | 2019-09-30 | 2021-08-09 | B |  | 1182 megawatts (MW) electric and steam generating plant | New 250 MW General Electric (GE) 7F.05 CCCT with unfired heat recovery steam generator combusting natural gas (primary fuel) and back up ULSD equivalent to 800 hours per year. | 250 MW COMBINED CYCLE COMBUSTION TURBINE FIRING NATURAL GAS | 15.21 | Natural Gas | 21042 | MMCubic ft/yr | One New 250 MW General Electric 7F.05 Combined cycle combustion turbine with a Maximum heat Input rate of Size: 2517 MMBtu/hr (HHV) at 10 degrees F, equipped with add-on controls and SCR and Oxidation Catalyst. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and Mthd 202 | (Particulate Matter (PM)) | PM | P | USE OF NATURAL GAS AND ULSD; BOTH CLEAN BURNING FUELS | 11.58 | LB/H | AV OF THREE ONE H STACK TESTS EVERY 5 YR | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*MI-0445 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact Mark Mitchell at 517-582-5293 or at mitchellm7@michigan.gov. Thank you. | 75-16B | 4911 | 221112 | Not found | 08/20/2019 &nbsp;ACT | 11/26/2019 &nbsp;ACT | 2020-12-22 | 2020-12-23 | A |  | Natural gas combined cycle power plant |  | FGCTGHRSG | 15.21 | Natural gas | 3421 | MMBTU/H | 3421 MMBTU/H for each turbine 740 MMBTU/H for each duct burner for a combined throughput of 4161 MMBTU/H or 8322 MMBTU/H for both trains. Two combined-cycle natural gas-fired combustion turbine generators (CTGs) with Heat Recovery Steam Generators (HRSG) (EUCTGHRSG1 & EUCTGHRSG2 in FGCTGHRSG). The total hours for startup and shutdown for each train shall not exceed 500 hours per 12-month rolling time period. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Good combustion practices, inlet air conditioning and the use of pipeline quality natural gas. | 11.7 | LB/H | HOURLY; EACH CTGHRSG | BACT-PSD | NSPS | N | 0 | U | 0.06 | LB/MMBTU | HOURLY; EACH CTGHRSG | 0 |  |  | 0 | 0 | N |  | There is also a NSPS natural gas material limit of 20 grains of sulfur per 100 scf.
LA-0364 | FG LA COMPLEX | FG LA LLC | ST. JAMES | LA | 70086 | USA | KUAN-MING PEMG | 2813026850 | KMPEMG@FPCC.COM.TW | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mr. Anthony Randall, (225)219-3180 | PSD-LA-812 | 2869 | 325110 | Not Found | 01/14/2019 &nbsp;ACT | 01/06/2020 &nbsp;ACT | 2020-05-05 | 2021-08-09 | A | https://edms.deq.louisiana.gov/app/doc/view.aspx?doc=11998450&ob=yes&child=yes | The FG LA complex will produce ethylene, propylene, ethylene glycol, high density polyethylene, low density polyethylene, linear low-density polyethylene and polypropylene. To support the operation of these production plants, the complex will also include electric power and steam generating units (Utility), wastewater treatment (Central Wastewater Treatment Plant), storage and loading operations (Logistics), and associated flare systems. | FG LA was issued PSD-LA-812 to construct the FG LA Complex which involves the construction of fourteen facilities permitted under fourteen Title V Permits to manufacture ethylene and propylene, ultimately producing high and low density polyethylene, propylene, and ethylene glycol. | Cogeneration Units | 15.21 | Natural Gas | 2222 | mm btu/h | Throughput is maximum operating rate. 2139 MM BTU/hr normal operating rate. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | P | Use of pipeline quality natural gas or fuel gas and good combustion practices. | 12.46 | LB/H |  | BACT-PSD | NSPS , NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0364 | FG LA COMPLEX | FG LA LLC | ST. JAMES | LA | 70086 | USA | KUAN-MING PEMG | 2813026850 | KMPEMG@FPCC.COM.TW | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mr. Anthony Randall, (225)219-3180 | PSD-LA-812 | 2869 | 325110 | Not Found | 01/14/2019 &nbsp;ACT | 01/06/2020 &nbsp;ACT | 2020-05-05 | 2021-08-09 | A | https://edms.deq.louisiana.gov/app/doc/view.aspx?doc=11998450&ob=yes&child=yes | The FG LA complex will produce ethylene, propylene, ethylene glycol, high density polyethylene, low density polyethylene, linear low-density polyethylene and polypropylene. To support the operation of these production plants, the complex will also include electric power and steam generating units (Utility), wastewater treatment (Central Wastewater Treatment Plant), storage and loading operations (Logistics), and associated flare systems. | FG LA was issued PSD-LA-812 to construct the FG LA Complex which involves the construction of fourteen facilities permitted under fourteen Title V Permits to manufacture ethylene and propylene, ultimately producing high and low density polyethylene, propylene, and ethylene glycol. | Cogeneration Units | 15.21 | Natural Gas | 2222 | mm btu/h | Throughput is maximum operating rate. 2139 MM BTU/hr normal operating rate. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of pipeline quality natural gas or fuel gas and good combustion practices. | 12.46 | LB/H |  | BACT-PSD | NSPS , NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AL-0328 | PLANT BARRY | ALABAMA POWER COMPANY | MOBILE | AL | 36512 | USA | TYLER PHILLIPS |  | TYLER.PHILLIPS@ADEM.ALABAMA.GOV | 4 | AL001 | ALABAMA DEPT OF ENVIRONMENTAL MGMT | MR. DALE HURST | (334) 271-7882 | ADH@ADEM.STATE.AL.US |  | 503-1001 | 4911 | 221112 | 110000741270 | 05/01/2020 &nbsp;ACT | 11/09/2020 &nbsp;ACT | 2021-09-30 | 2022-03-04 | B |  |  |  | Two 744 MW Combined Cycle Units | 15.21 | Natural Gas | 744 | MW |  | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation Catalyst | 13.6 | LB/HR | 3 HOUR AVG | BACT-PSD |  | U | 0 | N | 0.003 | LB/MMBTU | 3 HOUR AVG | 0 |  |  | 0 | 0 | N
*WV-0032 | BROOKE COUNTY POWER PLANT | ESC BROOKE COUNTY POWER I, LLC | BROOKE | WV | 26035 | USA | ANDREW DORN | 7163121042 | DREW.DORN@ENSOLCONSORTIUM.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Engineer: Mr. Steve Pursley 304-926-0499 x1218 Steven.R.Pursley@wv.gov | R14-0035 | 4911 | 221112 | Not Found | 03/30/2018 &nbsp;ACT | 09/18/2018 &nbsp;ACT | 2018-12-20 | 2022-06-28 | A |  | Nominal 925 mWe natural gas-fired combined-cycle power plant. Small sources: Emergency Generator, Fire Water Pump, Fuel Gas Heater not included in RBLC - may request info or see permit for details. |  | GE 7HA.01 Turbine | 15.21 | Natural Gas/Ethane | 2737.7 | mmBtu/hr | Facility has 2 identical units, only 1 entry in RBLC. Nominal 462.5 mWe. All emission limits steady-state and include 424 mmBtu/hr Duct Burner in operation. Short Term startup and shutdown limits in lb/event given in permit. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Oxidation Catalyst, Good Combustion Practices | 14.1 | LB/HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 2 | PPM |  | 0 | 0 | N
MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2019-02-19 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | FGCTGHRSG (EUCTGHRSG1 &amp; EUCTGHRSG2) | 15.21 | Natural gas | 0 |  | Two (2) combined-cycle natural gas-fired combustion turbine generators, each with a heat recovery steam generator (CTGHRSG). Plant nominal 1,150 MW electricity production. Turbines are each rated at 3,658 MMBTU/H and HRSG duct burners are each rated at 800 MMBTU/H. The HRSGs are not capable of operating independently from the CTGs. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, inlet air conditioning, and the use of pipeline quality natural gas. | 16 | LB/H | HOURLY; EACH UNIT | BACT-PSD | SIP | N | 0 | N | 12.2 | LB/H | HOURLY; EACH UNIT W/O DUCT BURNER FIRING | 0 |  |  | 0 | 0 | N |  | The cost analysis was for the best scenario: 100 percent capture of PM2.5, where PM and PM10 calculations equaled PM2.5. Pulse Jet Fabric Filter Baghouse: minimum of $174,206 per ton Mechanical Shaker Fabric Filter Baghouse: minimum of $145,172 per ton Reverse-Air Fabric Filter Baghouse: minimum of $232,274 per ton Dry ESP (Wire-Plate Type): minimum of $116,721 per ton Dry ESP (Wire-Pipe Type): minimum of $261,309 per ton Wet ESP (Wire-Plate Type): minimum of $263,153 per ton Wet ESP (Wire-Pipe Type): minimum of $348,412 per ton Venturi Scrubber: minimum of $167,000 per ton
MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2019-02-19 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | FGCTGHRSG (EUCTGHRSG1 &amp; EUCTGHRSG2) | 15.21 | Natural gas | 0 |  | Two (2) combined-cycle natural gas-fired combustion turbine generators, each with a heat recovery steam generator (CTGHRSG). Plant nominal 1,150 MW electricity production. Turbines are each rated at 3,658 MMBTU/H and HRSG duct burners are each rated at 800 MMBTU/H. The HRSGs are not capable of operating independently from the CTGs. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, inlet air conditioning, and the use of pipeline quality natural gas. | 16 | LB/H | HOURLY; EACH UNIT | BACT-PSD | SIP | N | 0 | N | 12.2 | LB/H | HOURLY; EACH UNIT W/O DUCT BURNER FIRING | 0 |  |  | 0 | 0 | N |  | The cost analysis was for the best scenario: 100 percent capture of PM2.5, where PM and PM10 calculations equaled PM2.5. Pulse Jet Fabric Filter Baghouse: minimum of $174,206 per ton Mechanical Shaker Fabric Filter Baghouse: minimum of $145,172 per ton Reverse-Air Fabric Filter Baghouse: minimum of $232,274 per ton Dry ESP (Wire-Plate Type): minimum of $116,721 per ton Dry ESP (Wire-Pipe Type): minimum of $261,309 per ton Wet ESP (Wire-Plate Type): minimum of $263,153 per ton Wet ESP (Wire-Pipe Type): minimum of $348,412 per ton Venturi Scrubber: minimum of $167,000 per ton
MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2019-02-19 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | FGCTGHRSG (EUCTGHRSG1 &amp; EUCTGHRSG2) | 15.21 | Natural gas | 0 |  | Two (2) combined-cycle natural gas-fired combustion turbine generators, each with a heat recovery steam generator (CTGHRSG). Plant nominal 1,150 MW electricity production. Turbines are each rated at 3,658 MMBTU/H and HRSG duct burners are each rated at 800 MMBTU/H. The HRSGs are not capable of operating independently from the CTGs. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, inlet air conditioning and the use of pipeline quality natural gas. | 16 | LB/H | HOURLY; EACH UNIT | BACT-PSD | SIP | N | 0 | N | 12.2 | LB/H | HOURLY; EACH UNIT W/O DUCT BURNER FIRING | 0 |  |  | 0 | 0 | N |  | The cost analysis was for the best scenario: 100 percent capture of PM2.5, where PM and PM10 calculations equaled PM2.5. Pulse Jet Fabric Filter Baghouse: minimum of $174,206 per ton Mechanical Shaker Fabric Filter Baghouse: minimum of $145,172 per ton Reverse-Air Fabric Filter Baghouse: minimum of $232,274 per ton Dry ESP (Wire-Plate Type): minimum of $116,721 per ton Dry ESP (Wire-Pipe Type): minimum of $261,309 per ton Wet ESP (Wire-Plate Type): minimum of $263,153 per ton Wet ESP (Wire-Pipe Type): minimum of $348,412 per ton Venturi Scrubber: minimum of $167,000 per ton
AK-0088 | LIQUEFACTION PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | KENAI PENNINSULA BOROUGH | AK | 99635 | USA | LISA HAAS |  | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - Permit Writer - dave.jones2@alaska.gov | AQ1539CPT01 | 4922 | 488999 | Not Found | 01/14/2020 &nbsp;ACT | 07/07/2022 &nbsp;ACT | 2022-08-04 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Liquefaction Plant is planned to encompass 921 acres, including 901 acres onshore for the liquefied natural gas (LNG) Plant as well as 20 acres offshore for the Marine Terminal. The Liquefaction Plant will be the terminus of an approximately 807-mile gas pipeline, allowing natural gas from Alaskaâ€™s North Slope to be shipped to outside markets. The stationary source will consist of structures and equipment associated with processing, storage, and loading of LNG. There will be three liquefaction trains combining to process up to approximately 20 million metric tons per annun of LNG. |  | Four Combined Cycle Gas-Fired Turbines | 15.21 | Natural Gas | 384 | MMBtu/hr | EUs 7 - 10 are combined cycle gas turbines used for power generation at LNG facility | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | pipeline quality natural gas and good combustion practices | 16 | PPMV SULFUR IN FUEL |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*WV-0032 | BROOKE COUNTY POWER PLANT | ESC BROOKE COUNTY POWER I, LLC | BROOKE | WV | 26035 | USA | ANDREW DORN | 7163121042 | DREW.DORN@ENSOLCONSORTIUM.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Engineer: Mr. Steve Pursley 304-926-0499 x1218 Steven.R.Pursley@wv.gov | R14-0035 | 4911 | 221112 | Not Found | 03/30/2018 &nbsp;ACT | 09/18/2018 &nbsp;ACT | 2018-12-20 | 2022-06-28 | A |  | Nominal 925 mWe natural gas-fired combined-cycle power plant. Small sources: Emergency Generator, Fire Water Pump, Fuel Gas Heater not included in RBLC - may request info or see permit for details. |  | GE 7HA.01 Turbine | 15.21 | Natural Gas/Ethane | 2737.7 | mmBtu/hr | Facility has 2 identical units, only 1 entry in RBLC. Nominal 462.5 mWe. All emission limits steady-state and include 424 mmBtu/hr Duct Burner in operation. Short Term startup and shutdown limits in lb/event given in permit. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Air Filter, Use of Natural Gas, Good Combustion Practices | 16.9 | LB/HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0.008 | LB/MMBTU |  | 0 | 0 | N |  | All PM is assumed to be PM2.5 or less.
MI-0442 | THOMAS TOWNSHIP ENERGY, LLC | THOMAS TOWNSHIP ENERGY, LLC | SAGINAW | MI | 48626-9409 | USA | DAN EWAN | 312-582-1504 | DEWAN@INVENERGYLLC.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions, please contact the permit engineer, Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you! | 210-18 | 4911 | 221112 | Not Found | 06/10/2019 &nbsp;ACT | 08/21/2019 &nbsp;ACT | 2019-11-18 | 2021-08-09 | A |  | New power plant | Thomas Township Energy is proposing to install two combustion turbine generators (CTG). Each CTG is connected to a heat recovery steam generator (HRSG), together referred to as a CTGHRSG. To reduce emissions of nitrogen oxides (NOx), the high-efficiency CTGHRSGs will be equipped with dry low-NOx burners and selective catalytic reduction (SCR). To reduce the emissions of carbon monoxide (CO) and volatile organic compounds (VOCs), each CTGHRSG will be equipped with an oxidation catalyst. | FGCTGHRSG | 15.21 | Natural gas | 625 | MW | Two (2) combined-cycle natural gas-fired combustion turbine generators (CTGs), each with a heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG). Each CTGHRSG has a combined nominal 625 MW electricity production (ISO) and a maximum combined heat input rating of 4,200 MMBTU/hr (HHV). Each HRSG is equipped with a natural gas-fired duct burner with a maximum rating of 560 MMBTU/hr (HHV) (ISO) to provide heat for additional steam production. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Good combustion practices, dry low NOx burners and selective catalytic reduction (SCR). | 2 | PPM | EACH; 24-HR ROLL.AVG EXCEPT START/SHUT | BACT-PSD | NSPS | N | 0 | U | 190 | LB/H | EACH; HOURLY INCLUDING STARTUP/SHUTDOWN | 0 |  |  | 0 | 0 | N |  | There are 3 emission limits within the permit and each limit applies to each unit. Emission Limit 1 = 2 ppmvd based on a 24-hour rolling average as determined each hour, except during startup and shutdown. Table 1 of 40 CFR Part 60 Subpart KKKK allows 96 ppmvd NOx at 15 percent O2 when the turbines are operating at less than 75 percent of peak load, or at temperatures less than 0 deg. F. Emission Limit 2 = 190 lb/hour and applies hourly, including startup or shutdown. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the combustion process ends at flame-off. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in special condition (SC) III.2 of the permit. Emission Limit 3 = 15 ppmvd, each unit and is based on a 30-day rolling average, except during operation less than 75 percent of peak load. Does not include startup and shutdown. Table 1 of 40 CFR Part 60 Subpart KKKK allows 96 ppmvd NOx at 15 percent O2 when the turbines are operating at less than 75 percent of peak load, or at temperatures less than 0 deg F. Thomas Township Energy does not consider wet controls, SNCR, XONON, EMxGT or NSCR to be technically feasible for the proposed equipment. Dry Low NOx Combustor Design (DLN) with SCR (80-99% NOx reduction).
MI-0447 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-648-6339 or at ByrnesM@michigan.gov for technical questions related to this permit. Thank you. | 74-18A | 4911 | 221112 | 110040958425 | 09/22/2020 &nbsp;ACT | 01/07/2021 &nbsp;ACT | 2021-06-28 | 2021-09-10 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG1 | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG1--A nominally rated 667 MMBTU/hr natural gas-fired combustion turbine generator (CTG) coupled with a heat recovery steam generator (HRSG). The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBTU/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a dry low NOx burner (DLNB), selective catalytic reduction (SCR), and oxidation catalyst. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry low NOx burners and selective catalytic reduction for NOx control for each CTG/HRSG unit. | 60 | LB/H | HOURLY; INCL STRT/SHUT IN COMBINED CYCLE | BACT-PSD | SIP | N | 0 | U | 60 | LB/H | 24-H ROLL AVG EACH OP HR; IN HRSG BYPASS | 0 |  |  | 15924 | 0 | N |  | There are 5 NOx emission limits in the permit with 2 listed above. All five will be listed here including the two above so that everything is included. Emission limit 1 = 60.0 lb/hr; hourly including startup or shutdown in combined cycle mode. Emission Limit 2 = 60.0 lb/hr based on a 24-hour rolling average as determined each operating hour. Applies in HRSG bypass mode. Emission Limit 3 = 3.0 ppmvd at 15% oxygen (O2) based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown. Emission Limit 4 = 25 ppmvd at 15% oxygen (O2) based on a 4-hour rolling average, except during operation less than 75% of peak load. Applies in HRSG bypass mode (NSPS limit). Emission Limit 5 = 25 ppmvd at 15% oxygen (O2) based on a 30-day rolling average, except during operation less than 75% of peak load. Applies in combined cycle mode (NSPS limit). The use of SCR with the DLNB is the highest ranked control system and was selected as BACT; therefore, an economic analysis was not performed.
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | Mitsubishi Hitachi Power Systems (MHPS) Combustion Turbines (P007 &amp; P008) | 15.21 | Natural gas | 3231 | MMBTU/H | Two identical MHPS Combustion Turbines 1 and 2; Mitsubishi Model M501JAC natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,231 MMBtu/hr (HHV) at 100% load and 51Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 306 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Good combustion practices and oxidation catalyst | 17.1 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 109.1 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen on a 24-hr block averaging period. 17.1 lb/h with duct burner, except startup and shutdown. 16.3 lb/h without duct burner, except startup and shutdown. 109.1 tons per rolling 12 month period for all operating modes, including startup and shutdown. 35.40 tons per rolling 12 month period for startup and shutdown periods.
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | General Electric (GE) Combustion Turbines (P005 &amp; P006) | 15.21 | Natural gas | 3459.6 | MMBTU/H | Two identical GE Combustion Turbines 1 and 2; GE model 7HA.02 natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,459.6 MMBtu/hr (HHV) at 100% load and -2Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 570.45 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate additional electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Good combustion practices and oxidation catalyst | 17.9 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 112.8 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen on a 24-hr block averaging period. 17.9 lb/h with duct burner, except startup and shutdown. 15.3 lb/h without duct burner, except startup and shutdown. 112.8 tons per rolling 12 month period for all operating modes, including startup and shutdown. 35.85 tons per rolling 12 month period for startup and shutdown periods.
LA-0391 | MAGNOLIA POWER GENERATING STATION UNIT 1 | MAGNOLIA POWER LLC | IBERVILLE | LA | 70764 | USA | WILLIAM DAVIS | 609-250-7707 | LEE.DAVIS@KINDLE-ENERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Ms. Lori Pittman, (225)219-3180 | PSD-LA-839 | 4911 | 221112 | Not Found | 09/08/2020 &nbsp;ACT | 06/03/2022 &nbsp;ACT | 2023-03-02 | 2023-05-23 | A | https://edms.deq.louisiana.gov/app/doc/view?doc=13323738 | Magnolia Power LLC (Magnolia Power) is proposing to construct and operate a power plant, Magnolia Power Generating Station Unit 1, consisting of a natural gas-fired combined cycle gas turbine (CCGT Unit) in Iberville Parish, Louisiana. The CCGT Unit (EQT001), which includes a heat recovery steam generator (HRSG) equipped with duct burners, will have a predicted net nominal output of 730 megawatts (MW) |  | Combined Cycle Gas Turbine Startup and Shutdown | 15.21 | Natural Gas | 5081 | mm BTU/h | Startup and shutdown emissions from the combined cycle gas turbine. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 18 | LB/HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0391 | MAGNOLIA POWER GENERATING STATION UNIT 1 | MAGNOLIA POWER LLC | IBERVILLE | LA | 70764 | USA | WILLIAM DAVIS | 609-250-7707 | LEE.DAVIS@KINDLE-ENERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Ms. Lori Pittman, (225)219-3180 | PSD-LA-839 | 4911 | 221112 | Not Found | 09/08/2020 &nbsp;ACT | 06/03/2022 &nbsp;ACT | 2023-03-02 | 2023-05-23 | A | https://edms.deq.louisiana.gov/app/doc/view?doc=13323738 | Magnolia Power LLC (Magnolia Power) is proposing to construct and operate a power plant, Magnolia Power Generating Station Unit 1, consisting of a natural gas-fired combined cycle gas turbine (CCGT Unit) in Iberville Parish, Louisiana. The CCGT Unit (EQT001), which includes a heat recovery steam generator (HRSG) equipped with duct burners, will have a predicted net nominal output of 730 megawatts (MW) |  | Combined Cycle Gas Turbine Startup and Shutdown | 15.21 | Natural Gas | 5081 | mm BTU/h | Startup and shutdown emissions from the combined cycle gas turbine. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 18 | LB/HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*WV-0029 | HARRISON COUNTY POWER PLANT | ESC HARRISON COUNTY POWER, LLC | HARRISON | WV | 26301 | USA | ANDREW DORN | 7163121042 | DREWDORN@ENSOLCONSORTIUM.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Engineer: Mr. Steve Pursley 304-926-0499 x1218 steven.r.pursley@wv.gov | R14-0036 | 4911 | 221112 | Not Found | 04/26/2017 &nbsp;ACT | 03/27/2018 &nbsp;ACT | 2018-06-25 | 2022-06-28 | A | https://dep.wv.gov/daq/Documents/March 2018 Permits and Evals/033-00264_PERM_R14-0036.pdf | Nominal 640 mWe natural gas-fired combined-cycle power plant. Small sources: Emergency Generator, Fire Water Pump, Fuel Gas Heater not included in RBLC - may request info or see permit for details. |  | GE 7HA.02 Turbine | 15.21 | Natural Gas | 3496.2 | mmBtu/hr | Nominal 640 mWe All emission limits steady-state and include 1000 mmBtu/hr Duct Burner in operation Short Term startup and shutdown limits in lb/event given in permit. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Air Filter, Use of Natural Gas, Good Combustion Practices | 18.2 | LB/HR |  | BACT-PSD |  | U | 0 | U | 100.1 | TONS/YEAR |  | 18.2 | LB/HR |  | 0 | 0 | N
MI-0447 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-648-6339 or at ByrnesM@michigan.gov for technical questions related to this permit. Thank you. | 74-18A | 4911 | 221112 | 110040958425 | 09/22/2020 &nbsp;ACT | 01/07/2021 &nbsp;ACT | 2021-06-28 | 2021-09-10 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG2 | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG2--A nominally rated 667 MMBTU/hr natural gas-fired CTG coupled with a HRSG. The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBTU/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a DLNB, SCR, and oxidation catalyst. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry low NOx burners and selective catalytic reduction for NOx control for each CTG/HRSG unit. | 60 | LB/H | HOURLY; INCL STRT/SHUT IN COMBINED CYCLE | BACT-PSD | NSPS , SIP | N | 0 | U | 60 | LB/H | 24-HR ROLL AVG IN HRSG BYPASS MODE | 0 |  |  | 15924 | 0 | N |  | There are 5 emission limits total for this emission unit and all will be listed here; including the two listed in the table above. Emission limit 1 = 60.0 lb/hr; hourly including startup or shutdown in combined cycle mode. Emission limit 2 = 60.0 lb/hr based on a 24-hour rolling average as determined each operating hour. Applies in HRSG bypass mode. Emission limit 3 = 3.0 ppmvd at 15% oxygen (O2); based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown. Emission limit 4 = 25 ppmvd at 15% oxygen (O2); based on a 4-hour rolling average, except during operation less than 75% of peak load. Applies in HRSG bypass mode (NSPS limit). Emission limit 5 = 25 ppmvd at 15% oxygen (O2) based on a 30-day rolling average, except during operation less than 75% of peak load. Applies in combined cycle mode (NSPS limit). The use of SCR with the DLNB is the highest ranked control system and was selected as BACT; therefore, an economic analysis was not performed.
*LA-0365 | BIG CAJUN I POWER PLANT | LOUISIANA GENERATING, LLC | POINTE COUPEE | LA | 70749 | USA | JACK LOWERY | 2256184860 | JACK.LOWERY@CLECOCAJUN.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mr. Christopher Smith (225) 219-3439 | PSD-LA-660(M-3) | 4911 | 221112 | 110010565067 | 11/06/2017 &nbsp;ACT | 06/27/2019 &nbsp;ACT | 2020-06-09 | 2021-04-01 | C |  | Electric power generating station using two natural gas fed turbines (120 MW each) |  | Combustion Turbine #1 (EQT0002, CTG-1) | 15.21 | Natural Gas | 1679 | MM BTU/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion Controls | 19 | LB/HR | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 23.31 | TPY | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | Fuel with pipeline quality natural gas and employ good combustion practices in order to control emissions of particulate matter.
*LA-0365 | BIG CAJUN I POWER PLANT | LOUISIANA GENERATING, LLC | POINTE COUPEE | LA | 70749 | USA | JACK LOWERY | 2256184860 | JACK.LOWERY@CLECOCAJUN.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mr. Christopher Smith (225) 219-3439 | PSD-LA-660(M-3) | 4911 | 221112 | 110010565067 | 11/06/2017 &nbsp;ACT | 06/27/2019 &nbsp;ACT | 2020-06-09 | 2021-04-01 | C |  | Electric power generating station using two natural gas fed turbines (120 MW each) |  | Combustion Turbine #2 (EQT0003, CTG-2) | 15.21 | Natural Gas | 1679 | MM BTU/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion Controls | 19 | LB/HR | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 23.31 | TPY | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | Fuel with pipeline quality natural gas and employ good combustion practices in order to control emissions of particulate matter.
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (South Plant): A combined cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/H (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/H (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR and an oxidation catalyst. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, inlet air conditioning and the use of pipeline quality natural gas. | 19.1 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N | 2017 | 19.1 pph is equivalent to 0.005 lb/MMBTU, which includes startup and shutdown The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. Pulse Jet Fabric Filter Baghouse: average of $334,000 per ton Mechanical Shaker Fabric Filter Baghouse: average of $370,500 per ton Reverse-Air Fabric Filter Baghouse: average of $437,000 per ton Dry ESP (Wire-Plate Type): average of $438,500 per ton Dry ESP (Wire-Pipe Type): average of $278,500 per ton Wet ESP (Wire-Plate Type): average of $528,500 per ton Wet ESP (Wire-Pipe Type): average of $403,000 per ton Venturi Scrubber: average of $1,321,000 per ton
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (North Plant): A combined-cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | Nominal 500 MW electricity production. Turbine rating of 3,080 MMBTU/hr (HHV) and HRSG duct burner rating of 755 MMBTU/hr (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/hr (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, inlet air conditioning, and the use of pipeline quality natural gas. | 19.1 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N | 2017 | (19.1 lb/h is equivalent to 0.005 lb/MMBTU which includes startup and shutdown). The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10 which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. Pulset jet fabric filter baghouse: average of $334,000 per ton. Mechanical shaker fabric filter baghouse: average of $370,500 per ton. Reverse-air fabric filter baghouse: average of $437,000 per ton. Dry ESP (Wire-plate type): average of $438,500 per ton Dry ESP (Wire-pipe type): average of $278,500 per ton Wet ESP (Wire-plate type): average of $528,500 per ton Wet ESP (Wire-pipe type): average of $403,000 per ton Venturi Scrubber: average of $1,321,000 per ton.
MI-0451 | MEC NORTH, LLC | MARSHALL ENERGY CENTER, LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 9144682402 | WLADD@DEVELOPMENTSPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Janelle Trowhill, at 517-582-5312 or at TrowhillJ1@michigan.gov for technical questions regarding this permit. Thank you. | 167-17B | 4911 | 221112 | Not Found | 12/08/2021 &nbsp;ACT | 06/23/2022 &nbsp;ACT | 2022-12-21 | 2023-04-25 | A |  | Natural gas combined-cycle power plant (two plants: north and south). | The two plants (MEC North, LLC and MEC South, LLC) will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. | EUCTGHRSG (North Plant): A combined cycle natural gas fired combustion turbine generator with heat recovery steam generator | 15.21 | Natural gas | 3064 | MMBTU/H | Throughput Information: Nominal 500 MW electricity production. Turbine rating of 3,064 MMBTU/hr (HHV) and HRSG duct burner rating of 889 MMBTU/Hr (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,064 MMBTU/hr (HHV). The HRSG is equipped with a natural gas fired duct burner, with a maximum heat input rating of 889 MMBTU/hr (HHV) and rated at 874 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, inlet air conditioning and the use of pipeline quality natural gas. | 19.1 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N | 2017 | The underlying applicable requirements for the emission limit above are BACT, NAAQS and PSD increment. (19.1 pph is equivalent to 0.005 lb/MMBTU, which includes startup and shutdown) The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. Pulse Jet Fabric Filter Baghouse: average of $334,000 per ton Mechanical Shaker Fabric Filter Baghouse: average of $370,500 per ton Reverse-Air Fabric Filter Baghouse: average of $437,000 per ton Dry ESP (Wire-Plate Type): average of $438,500 per ton Dry ESP (Wire-Pipe Type): average of $278,500 per ton Wet ESP (Wire-Plate Type): average of $528,500 per ton Wet ESP (Wire-Pipe Type): average of $403,000 per ton Venturi Scrubber: average of $1,321,000 per ton
MI-0452 | MEC SOUTH, LLC | MARSHALL ENERGY CENTER, LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 9144682402 | WLADD@DEVELOPMENTSPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer, Janelle Trowhill at TrowhillJ1@michigan.gov or at 517-582-5312. Thank you. | 168-17B | 4911 | 221112 | Not Found | 12/08/2021 &nbsp;ACT | 06/23/2022 &nbsp;ACT | 2022-12-22 | 2023-04-25 | A |  | Natural gas combined cycle power plant (Two Plants: North and South) | The two plants (MEC North, LLC and MEC South, LLC) will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. | EUCTGHRSG (South Plant): A combined-cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 3064 | MMBTU/H | Nominal 500 MW electricity production. Turbine rating of 3064 MMBTU/H (HHV) and HRSG duct burner rating of 889 MMBTU/H (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,064 MMBTU/hr (HHV). The HRSG is equipped with a natural gas fired duct burner, with a maximum heat input rating of 889 MMBTU/hr (HHV) and rated at 874 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion Practices, inlet air conditioning, and the use of pipeline quality natural gas | 19.1 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N | 2017 | (19.1 pph is equivalent to 0.005 lb/MMBTU, which includes startup and shutdown) The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. Pulse Jet Fabric Filter Baghouse: average of $334,000 per ton Mechanical Shaker Fabric Filter Baghouse: average of $370,500 per ton Reverse-Air Fabric Filter Baghouse: average of $437,000 per ton Dry ESP (Wire-Plate Type): average of $438,500 per ton Dry ESP (Wire-Pipe Type): average of $278,500 per ton Wet ESP (Wire-Plate Type): average of $528,500 per ton Wet ESP (Wire-Pipe Type): average of $403,000 per ton Venturi Scrubber: average of $1,321,000 per ton
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (South Plant): A combined cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/H (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/H (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR and an oxidation catalyst. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, inlet air conditioning, and the use of pipeline quality natural gas. | 19.1 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N | 2017 | 19.1 pph is equivalent to 0.005 lb/MMBTU, which includes startup and shutdown The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. Pulse Jet Fabric Filter Baghouse: average of $334,000 per ton Mechanical Shaker Fabric Filter Baghouse: average of $370,500 per ton Reverse-Air Fabric Filter Baghouse: average of $437,000 per ton Dry ESP (Wire-Plate Type): average of $438,500 per ton Dry ESP (Wire-Pipe Type): average of $278,500 per ton Wet ESP (Wire-Plate Type): average of $528,500 per ton Wet ESP (Wire-Pipe Type): average of $403,000 per ton Venturi Scrubber: average of $1,321,000 per ton
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (North Plant): A combined-cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | Nominal 500 MW electricity production. Turbine rating of 3,080 MMBTU/hr (HHV) and HRSG duct burner rating of 755 MMBTU/hr (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/hr (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, inlet air conditioning, and the use of pipeline quality natural gas. | 19.1 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N | 2017 | (19.1 pph is equivalent to 0.005 lb/MMBTU, which includes startup and shutdown). The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. Pulse Jet Fabric Filter Baghouse: average of $334,000 per ton Mechanical Shaker Fabric Filter Baghouse: average of $370,500 per ton Reverse-Air Fabric Filter Baghouse: average of $437,000 per ton Dry ESP (Wire-Plate Type): average of $438,500 per ton Dry ESP (Wire-Pipe Type): average of $278,500 per ton Wet ESP (Wire-Plate Type): average of $528,500 per ton Wet ESP (Wire-Pipe Type): average of $403,000 per ton Venturi Scrubber: average of $1,321,000 per ton
MI-0451 | MEC NORTH, LLC | MARSHALL ENERGY CENTER, LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 9144682402 | WLADD@DEVELOPMENTSPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Janelle Trowhill, at 517-582-5312 or at TrowhillJ1@michigan.gov for technical questions regarding this permit. Thank you. | 167-17B | 4911 | 221112 | Not Found | 12/08/2021 &nbsp;ACT | 06/23/2022 &nbsp;ACT | 2022-12-21 | 2023-04-25 | A |  | Natural gas combined-cycle power plant (two plants: north and south). | The two plants (MEC North, LLC and MEC South, LLC) will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. | EUCTGHRSG (North Plant): A combined cycle natural gas fired combustion turbine generator with heat recovery steam generator | 15.21 | Natural gas | 3064 | MMBTU/H | Throughput Information: Nominal 500 MW electricity production. Turbine rating of 3,064 MMBTU/hr (HHV) and HRSG duct burner rating of 889 MMBTU/Hr (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,064 MMBTU/hr (HHV). The HRSG is equipped with a natural gas fired duct burner, with a maximum heat input rating of 889 MMBTU/hr (HHV) and rated at 874 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, inlet air conditioning, and the use of pipeline quality natural gas. | 19.1 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N | 2017 | The underlying applicable requirements for the emission limit above are BACT, NAAQS and PSD increment. (19.1 pph is equivalent to 0.005 lb/MMBTU, which includes startup and shutdown) The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. Pulse Jet Fabric Filter Baghouse: average of $334,000 per ton Mechanical Shaker Fabric Filter Baghouse: average of $370,500 per ton Reverse-Air Fabric Filter Baghouse: average of $437,000 per ton Dry ESP (Wire-Plate Type): average of $438,500 per ton Dry ESP (Wire-Pipe Type): average of $278,500 per ton Wet ESP (Wire-Plate Type): average of $528,500 per ton Wet ESP (Wire-Pipe Type): average of $403,000 per ton Venturi Scrubber: average of $1,321,000 per ton
MI-0452 | MEC SOUTH, LLC | MARSHALL ENERGY CENTER, LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 9144682402 | WLADD@DEVELOPMENTSPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer, Janelle Trowhill at TrowhillJ1@michigan.gov or at 517-582-5312. Thank you. | 168-17B | 4911 | 221112 | Not Found | 12/08/2021 &nbsp;ACT | 06/23/2022 &nbsp;ACT | 2022-12-22 | 2023-04-25 | A |  | Natural gas combined cycle power plant (Two Plants: North and South) | The two plants (MEC North, LLC and MEC South, LLC) will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. | EUCTGHRSG (South Plant): A combined-cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 3064 | MMBTU/H | Nominal 500 MW electricity production. Turbine rating of 3064 MMBTU/H (HHV) and HRSG duct burner rating of 889 MMBTU/H (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,064 MMBTU/hr (HHV). The HRSG is equipped with a natural gas fired duct burner, with a maximum heat input rating of 889 MMBTU/hr (HHV) and rated at 874 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion Practices, inlet air conditioning, and the use of pipeline quality natural gas | 19.1 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N | 2017 | (19.1 pph is equivalent to 0.005 lb/MMBTU, which includes startup and shutdown) The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. Pulse Jet Fabric Filter Baghouse: average of $334,000 per ton Mechanical Shaker Fabric Filter Baghouse: average of $370,500 per ton Reverse-Air Fabric Filter Baghouse: average of $437,000 per ton Dry ESP (Wire-Plate Type): average of $438,500 per ton Dry ESP (Wire-Pipe Type): average of $278,500 per ton Wet ESP (Wire-Plate Type): average of $528,500 per ton Wet ESP (Wire-Pipe Type): average of $403,000 per ton Venturi Scrubber: average of $1,321,000 per ton
*MI-0445 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact Mark Mitchell at 517-582-5293 or at mitchellm7@michigan.gov. Thank you. | 75-16B | 4911 | 221112 | Not found | 08/20/2019 &nbsp;ACT | 11/26/2019 &nbsp;ACT | 2020-12-22 | 2020-12-23 | A |  | Natural gas combined cycle power plant |  | FGCTGHRSG | 15.21 | Natural gas | 3421 | MMBTU/H | 3421 MMBTU/H for each turbine 740 MMBTU/H for each duct burner for a combined throughput of 4161 MMBTU/H or 8322 MMBTU/H for both trains. Two combined-cycle natural gas-fired combustion turbine generators (CTGs) with Heat Recovery Steam Generators (HRSG) (EUCTGHRSG1 & EUCTGHRSG2 in FGCTGHRSG). The total hours for startup and shutdown for each train shall not exceed 500 hours per 12-month rolling time period. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, inlet air conditioning, and the use of pipeline quality natural gas. | 19.8 | LB/H | HOURLY; EACH CTGHRSG | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit above is for each CTGHRSG in the flexible group FGCTGHRSG. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. The dollar value year used was 2014. â€¢ Pulse Jet Fabric Filter Baghouse: minimum of $364,528 per ton â€¢ Mechanical Shaker Fabric Filter Baghouse: minimum of $404,724 per ton â€¢ Reverse-Air Fabric Filter Baghouse: minimum of $476,689 per ton â€¢ Dry ESP (Wire-Plate Type): minimum of $478,806 per ton â€¢ Dry ESP (Wire-Pipe Type): minimum of $303,809 per ton â€¢ Wet ESP (Wire-Plate Type): minimum of $576,763 per ton â€¢ Wet ESP (Wire-Pipe Type): minimum of $440,047 per ton â€¢ Venturi Scrubber: minimum of $1,445,564 per ton
*MI-0445 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact Mark Mitchell at 517-582-5293 or at mitchellm7@michigan.gov. Thank you. | 75-16B | 4911 | 221112 | Not found | 08/20/2019 &nbsp;ACT | 11/26/2019 &nbsp;ACT | 2020-12-22 | 2020-12-23 | A |  | Natural gas combined cycle power plant |  | FGCTGHRSG | 15.21 | Natural gas | 3421 | MMBTU/H | 3421 MMBTU/H for each turbine 740 MMBTU/H for each duct burner for a combined throughput of 4161 MMBTU/H or 8322 MMBTU/H for both trains. Two combined-cycle natural gas-fired combustion turbine generators (CTGs) with Heat Recovery Steam Generators (HRSG) (EUCTGHRSG1 & EUCTGHRSG2 in FGCTGHRSG). The total hours for startup and shutdown for each train shall not exceed 500 hours per 12-month rolling time period. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, inlet air conditioning, and the use of pipeline quality natural gas. | 19.8 | LB/H | HOURLY; EACH CTGHRSG | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit above is for each CTGHRSG in the flexible group FGCTGHRSG. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. The dollar value year used was 2014. â€¢ Pulse Jet Fabric Filter Baghouse: minimum of $364,528 per ton â€¢ Mechanical Shaker Fabric Filter Baghouse: minimum of $404,724 per ton â€¢ Reverse-Air Fabric Filter Baghouse: minimum of $476,689 per ton â€¢ Dry ESP (Wire-Plate Type): minimum of $478,806 per ton â€¢ Dry ESP (Wire-Pipe Type): minimum of $303,809 per ton â€¢ Wet ESP (Wire-Plate Type): minimum of $576,763 per ton â€¢ Wet ESP (Wire-Pipe Type): minimum of $440,047 per ton â€¢ Venturi Scrubber: minimum of $1,445,564 per ton
*WV-0029 | HARRISON COUNTY POWER PLANT | ESC HARRISON COUNTY POWER, LLC | HARRISON | WV | 26301 | USA | ANDREW DORN | 7163121042 | DREWDORN@ENSOLCONSORTIUM.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Engineer: Mr. Steve Pursley 304-926-0499 x1218 steven.r.pursley@wv.gov | R14-0036 | 4911 | 221112 | Not Found | 04/26/2017 &nbsp;ACT | 03/27/2018 &nbsp;ACT | 2018-06-25 | 2022-06-28 | A | https://dep.wv.gov/daq/Documents/March 2018 Permits and Evals/033-00264_PERM_R14-0036.pdf | Nominal 640 mWe natural gas-fired combined-cycle power plant. Small sources: Emergency Generator, Fire Water Pump, Fuel Gas Heater not included in RBLC - may request info or see permit for details. |  | GE 7HA.02 Turbine | 15.21 | Natural Gas | 3496.2 | mmBtu/hr | Nominal 640 mWe All emission limits steady-state and include 1000 mmBtu/hr Duct Burner in operation Short Term startup and shutdown limits in lb/event given in permit. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation Catalyst, Good Combustion Practices | 20 | LB/HR | 1-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 124 | TONS/YEAR |  | 2 | PPM |  | 0 | 0 | N
MI-0451 | MEC NORTH, LLC | MARSHALL ENERGY CENTER, LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 9144682402 | WLADD@DEVELOPMENTSPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Janelle Trowhill, at 517-582-5312 or at TrowhillJ1@michigan.gov for technical questions regarding this permit. Thank you. | 167-17B | 4911 | 221112 | Not Found | 12/08/2021 &nbsp;ACT | 06/23/2022 &nbsp;ACT | 2022-12-21 | 2023-04-25 | A |  | Natural gas combined-cycle power plant (two plants: north and south). | The two plants (MEC North, LLC and MEC South, LLC) will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. | EUCTGHRSG (North Plant): A combined cycle natural gas fired combustion turbine generator with heat recovery steam generator | 15.21 | Natural gas | 3064 | MMBTU/H | Throughput Information: Nominal 500 MW electricity production. Turbine rating of 3,064 MMBTU/hr (HHV) and HRSG duct burner rating of 889 MMBTU/Hr (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,064 MMBTU/hr (HHV). The HRSG is equipped with a natural gas fired duct burner, with a maximum heat input rating of 889 MMBTU/hr (HHV) and rated at 874 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR with DLNB (Selective catalytic reduction with Dry low NOx burners) | 2.5 | PPM | 24-HR ROLLING AVG | BACT-PSD | NSPS | N | 80 | N | 29.2 | LB/H | 24-HR ROLLING AVG | 0 |  |  | 0 | 0 | N |  | There are 4 NOx emission limits with only 2 noted in table above: Emission limit 1 above = 2 ppmvd based on a 24-hour rolling avg as determined each operating hour, except during startup and shutdown. The underlying applicable requirement (UAR) for this limit is BACT. Emission limit 2 above = 29.2 lbs/hr based on a 24-hour rolling avg as determined each operating hour, except during startup and shutdown. The UARs are BACT, NAAQS and PSD Increment. Emission limit 3 = 15 ppmvd at 15% O2 based on a 30-day rolling average as determined each operating day and does not include startup and shutdown. The UAR is NSPS KKKK. Emission limit 4 is 126.5 lbs/hr, each operating hour during startup or shutdown. The UAR for this limit is BACT, NAAQS and PSD increment. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in SC III.2. Startup and Shutdown hours are limited to 300 hours per 12 month rolling time period.
MI-0452 | MEC SOUTH, LLC | MARSHALL ENERGY CENTER, LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 9144682402 | WLADD@DEVELOPMENTSPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer, Janelle Trowhill at TrowhillJ1@michigan.gov or at 517-582-5312. Thank you. | 168-17B | 4911 | 221112 | Not Found | 12/08/2021 &nbsp;ACT | 06/23/2022 &nbsp;ACT | 2022-12-22 | 2023-04-25 | A |  | Natural gas combined cycle power plant (Two Plants: North and South) | The two plants (MEC North, LLC and MEC South, LLC) will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. | EUCTGHRSG (South Plant): A combined-cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 3064 | MMBTU/H | Nominal 500 MW electricity production. Turbine rating of 3064 MMBTU/H (HHV) and HRSG duct burner rating of 889 MMBTU/H (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,064 MMBTU/hr (HHV). The HRSG is equipped with a natural gas fired duct burner, with a maximum heat input rating of 889 MMBTU/hr (HHV) and rated at 874 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR with DLNB [Selective Catalytic Reduction with Dry Low NOx Burners] | 2 | PPM | 24-HR ROLLING AVG | BACT-PSD | NSPS , SIP | N | 80 | N | 29.2 | LB/H | 24-HR ROLLING AVG EXCEPT SU/SD | 0 |  |  | 0 | 0 | N |  | There are 4 NOx emission limits, all 4 will be described below: Emission limit 1 = 2 ppmvd based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown. The applicable requirement is BACT. Emission limit 2 = 29.2 lbs/hr based on a 24-hour rolling average as determined each operating hour except during startup and shutdown. The applicable requirements are BACT, NAAQS and PSD increment. Emission limit 3 = 15 ppmvd at 15%O2 based on a 30-day rolling average as determined each operating day. The applicable requirement is NSPS KKKK. Emission limit 4 = 126.5 lbs/hr based on an operating hour during startup or shutdown. The applicable requirements are BACT, NAAQS and PSD increment. Estimated efficiency of SCR with DLNB is a range of 80-90% Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in SC III.2. Startup and Shutdown hours are limited to 300 hours per 12 month rolling time period.
MI-0454 | LBWL-ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions about this permit, please contact the permit engineer, Lauren Magirl, at 517-582-5345, or at MagirlL@michigan.gov. Thank you. | 74-18D | 4911 | 221112 | Not Found | 10/25/2022 &nbsp;ACT | 12/20/2022 &nbsp;ACT | 2022-12-29 | 2023-05-23 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWLâ€™s existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG1 | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG1- A nominally rated 667 MMBtu/hr natural gas-fired combustion turbine generator (CTG) coupled with a heat recovery steam generator (HRSG). The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBtu/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a dry low NOx burner (DLNB), selective catalytic reduction (SCR), and oxidation catalyst. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry low NOx burners and selective catalytic reduction for NOx control for each CTG/HRSG unit. | 3 | PPM | PPMVD AT 15%O2; 24-HR ROLL AVG EXC SU/SD | BACT-PSD | SIP | N | 0 | N | 60 | LB/H | HOURLY INCL SU/SD IN COMB CYC MODE | 0 |  |  | 0 | 0 | N |  | There are 5 NOx emission limits with only 2 listed above. All 5 are detailed below: Emission limit 1 (above) = 3.0 ppmvd at 15%O2 on a 240hour rolling average as determined each operating hour, except during startup (SU) and shutdown (SD). Emission limit 2 (above) = 60.0 lbs/hr on an hourly basis including startup or shutdown in combined cycle mode. Emission limit 3 = 60.0 lbs/hr on a 24-hour rolling average as determined each operating hour. Applies in HRSG bypass mode. Emission limit 4 = 25 ppmvd at 15%O2 based on a 4-hour rolling average except during operation less than 75% of peak load. Applies in HRSG bypass mode. (NSPS limit). Emission limit 5 = 25 ppmvd at 15%O2 on a 30-day rolling average except during operation less than 75% of peak load. Applies in combined cycle mode. (NSPS limit). The use of SCR with the DLNB is the highest ranked control system and was selected as BACT; therefore, an economic analysis was not performed.
AL-0328 | PLANT BARRY | ALABAMA POWER COMPANY | MOBILE | AL | 36512 | USA | TYLER PHILLIPS |  | TYLER.PHILLIPS@ADEM.ALABAMA.GOV | 4 | AL001 | ALABAMA DEPT OF ENVIRONMENTAL MGMT | MR. DALE HURST | (334) 271-7882 | ADH@ADEM.STATE.AL.US |  | 503-1001 | 4911 | 221112 | 110000741270 | 05/01/2020 &nbsp;ACT | 11/09/2020 &nbsp;ACT | 2021-09-30 | 2022-03-04 | B |  |  |  | Two 744 MW Combined Cycle Units | 15.21 | Natural Gas | 744 | MW |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 23.8 | LB/HR | 3 HOUR AVG | BACT-PSD |  | U | 0 | N | 0.005 | LB/MMBTU | 3 HOUR AVG | 0 |  |  | 0 | 0 | N
*LA-0365 | BIG CAJUN I POWER PLANT | LOUISIANA GENERATING, LLC | POINTE COUPEE | LA | 70749 | USA | JACK LOWERY | 2256184860 | JACK.LOWERY@CLECOCAJUN.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mr. Christopher Smith (225) 219-3439 | PSD-LA-660(M-3) | 4911 | 221112 | 110010565067 | 11/06/2017 &nbsp;ACT | 06/27/2019 &nbsp;ACT | 2020-06-09 | 2021-04-01 | C |  | Electric power generating station using two natural gas fed turbines (120 MW each) |  | Combustion Turbine #1 (EQT0002, CTG-1) | 15.21 | Natural Gas | 1679 | MM BTU/hr |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N |  | 25 | PPMV | THREE HOUR ROLLING AVERAGE | BACT-PSD | OPERATING PERMIT | U | 0 | U | 102.8 | LB/HR | HOURLY MAXIMUM | 0 |  |  | 0 | 0 | N |  | Annual Maximum = 125.90 TPY CO. All PPMV measurements are corrected to 15% oxygen. PPMV limits apply when unit operates at greater than or equal to 70 Megawatt (MW). These limits are not applicable during any clock hour in which the unit operates at a load less than 70 MW.
*LA-0365 | BIG CAJUN I POWER PLANT | LOUISIANA GENERATING, LLC | POINTE COUPEE | LA | 70749 | USA | JACK LOWERY | 2256184860 | JACK.LOWERY@CLECOCAJUN.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mr. Christopher Smith (225) 219-3439 | PSD-LA-660(M-3) | 4911 | 221112 | 110010565067 | 11/06/2017 &nbsp;ACT | 06/27/2019 &nbsp;ACT | 2020-06-09 | 2021-04-01 | C |  | Electric power generating station using two natural gas fed turbines (120 MW each) |  | Combustion Turbine #2 (EQT0003, CTG-2) | 15.21 | Natural Gas | 1679 | MM BTU/hr |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N |  | 25 | PPMV | THREE HOUR ROLLING AVERAGE | BACT-PSD | OPERATING PERMIT | U | 0 | U | 102.8 | LB/HR | HOURLY MAXIMUM | 0 |  |  | 0 | 0 | N |  | Annual Maximum = 125.90 TPY CO. All PPMV measurements are corrected to 15% oxygen. PPMV limits apply when unit operates at greater than or equal to 70 Megawatt (MW). These limits are not applicable during any clock hour in which the unit operates at a load less than 70 MW.
TX-0878 | LNG EXPORT TERMINAL | PORT ARTHUR LNG, LLC | JEFFERSON | TX |  | USA | J.D. MORRIS | 713-298-5476 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Benjamin Hansen, Ph.D., P.E., (512) 239-4578, Benjamin.Hansen@tceq.texas.gov | 158420, PSDTX1572, GHGPSDTX198 | 4922 | 486210 | Not FOUND | 05/27/2020 &nbsp;ACT | 09/15/2022 &nbsp;ACT | 2019-11-07 | 2023-05-23 | A |  | Liquefied natural gas (LNG) export terminal. |  | Refrigeration Compression Turbines | 15.21 | NATURAL GAS | 26.92 | MMTON/Y | Eight GE Frame 7E gas turbines for refrigeration and compression at the site. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | good combustion practices. | 25 | PPM | 24-HR AVG | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0454 | LBWL-ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions about this permit, please contact the permit engineer, Lauren Magirl, at 517-582-5345, or at MagirlL@michigan.gov. Thank you. | 74-18D | 4911 | 221112 | Not Found | 10/25/2022 &nbsp;ACT | 12/20/2022 &nbsp;ACT | 2022-12-29 | 2023-05-23 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWLâ€™s existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG2 | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG2- A nominally rated 667 MMBtu/hr natural gas-fired CTG coupled with a HRSG. The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBtu/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a DLNB, SCR, and oxidation catalyst. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry low NOx burners and selective catalytic reduction for NOx control for each CTG/HRSG unit. | 3 | PPM | @15%OX; 24-HR ROLL AVG EXCEPT START/SHUT | BACT-PSD | NSPS | N | 0 | U | 60 | LB/H | HOURLY INCLU START/SHUT IN COMBINE CYCLE | 0 |  |  | 15924 | 0 | N | 2018 | There are 5 NOx emission limits, all of which are listed below: Emission Limit 1 = 3.0 ppmvd at 15% Oxygen (O2) on a 24-hour rolling average as determined each operating hour, except during startup and shutdown. Emission Limit 2 = 25 ppmvd at 15% Oxygen (O2) on a 4-hour rolling average, except during operation less than 75% of peak load. Applies in HRSG bypass mode (NSPS limit). Emission Limit 3 = 25 ppmvd at 15% Oxygen (O2) on a 30-day rolling average, except during operation less than 75% of peak load. Applies in combined cycle mode. (NSPS limit). Emission Limit 4 = 60.0 lb/hr on an hourly basis, including startup or shutdown in combined cycle mode. Emission Limit 5 = 60.0 lb/hr on a 24-hour rolling average as determined each operating hour. Applies in HRSG bypass mode. The use of SCR with the DLNB is the highest ranked control system and was selected as BACT; therefore, an economic analysis was not performed.
MI-0455 | MIDLAND COGENERATION VENTURE LIMITED PARTNERSHIP | MIDLAND COGENERATION VENTURE LIMITED PARTNERSHIP | MIDLAND | MI | 46540 | USA | BRIAN VOKAL | 248-980-1139 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes at 517-648-6339 or at ByrnesM@michigan.gov. Thank you. | 2023-10-23 | 4911 | 221112 | Not found | 10/12/2022 &nbsp;ACT | 02/01/2023 &nbsp;ACT | 2023-05-15 | 2023-05-23 | B |  | Electric and steam generation |  | EUCTGHRSG1 | 15.21 | Natural gas | 4197.6 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective catalytic regeneration | 2 | PPM | PPMVD AT 15%O2; 24-HR ROLL AVG EXC SU/SD | BACT-PSD | NSPS | N | 90 | N | 39.6 | LB/H | HOURLY EXCEPT SU/SD | 0 |  |  | 0 | 0 | N |  | There are 4 NOx emission limits, all listed below: Emission limit 1 = 2.0 ppmvd at 15% oxygen on a 24-hour rolling average except during SU/SD. Emission limit 2 = 39.6 lb/hr on an hourly basis except during SU/SD. Emission limit 3 = 15 ppmvd at 15% oxygen on a 4-hour rolling average except during operations less than 75% of peak load. This is a BACT + NSPS limit. Emission limit 4 = 851.2 lb/hr during SU/SD.
NJ-0088 | COGEN TECH LINDEN VENTURE LP | COGEN TECH LINDEN VENTURE LP | UNION | NJ | 7036 | USA | NATALIE SESTO | (908) 523-4320 | NATALIE.SESTO@NAES.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Permit Writer: Eleonora Kats (Eleonora.kats@dep.nj.gov) Supervisor: Yogesh Doshi (yogesh.doshi@dep.nj.gov) | 41809 / BOP170001 | 4932 | 221112 | 110066826019 | 06/08/2017 &nbsp;ACT | 07/30/2019 &nbsp;ACT | 2019-09-30 | 2021-08-09 | B |  | 1182 megawatts (MW) electric and steam generating plant | New 250 MW General Electric (GE) 7F.05 CCCT with unfired heat recovery steam generator combusting natural gas (primary fuel) and back up ULSD equivalent to 800 hours per year. | 250 MW COMBINED CYCLE COMBUSTION TURBINE FIRING NATURAL GAS | 15.21 | Natural Gas | 21042 | MMCubic ft/yr | One New 250 MW General Electric 7F.05 Combined cycle combustion turbine with a Maximum heat Input rate of Size: 2517 MMBtu/hr (HHV) at 10 degrees F, equipped with add-on controls and SCR and Oxidation Catalyst. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Selective Catalytic Reduction, Dry Low NOx, and use of Natural gas as Primary fuel | 18.3 | LB/H | AV OF THREE ONE H STACK TESTS EVERY 5 YR | BACT-PSD | NSPS , OPERATING PERMIT | Y | 0 | N | 2 | PPMVD@15%O2 | 3 H ROLLING AV BASED ON ONE H BLOCK | 0 |  |  | 0 | 0 | N |  | Subject to LAER
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | Mitsubishi Hitachi Power Systems (MHPS) Combustion Turbines (P007 &amp; P008) | 15.21 | Natural gas | 3231 | MMBTU/H | Two identical MHPS Combustion Turbines 1 and 2; Mitsubishi Model M501JAC natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,231 MMBtu/hr (HHV) at 100% load and 51Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 306 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | dry low NOx burners and an SCR system | 28 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD | NSPS | U | 0 | U | 124 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen on a 24-hr block averaging period. 28 lb/h with duct burner, except startup and shutdown. 26.7 lb/h without duct burner, except startup and shutdown. 124.0 tons per rolling 12 month period for all operating modes, including startup and shutdown. 3.22 tons per rolling 12 month period for startup and shutdown periods.
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | General Electric (GE) Combustion Turbines (P005 &amp; P006) | 15.21 | Natural gas | 3459.6 | MMBTU/H | Two identical GE Combustion Turbines 1 and 2; GE model 7HA.02 natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,459.6 MMBtu/hr (HHV) at 100% load and -2Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 570.45 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate additional electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | dry low NOx burners and an SCR system | 29.5 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD | NSPS | U | 0 | U | 139 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen on a 24-hr block averaging period. 29.5 lb/h with duct burner, except startup and shutdown. 25.1 lb/h without duct burner, except startup and shutdown. 139 tons per rolling 12 month period for all operating modes, including startup and shutdown. 12.99 tons per rolling 12 month period for startup and shutdown periods.
MI-0455 | MIDLAND COGENERATION VENTURE LIMITED PARTNERSHIP | MIDLAND COGENERATION VENTURE LIMITED PARTNERSHIP | MIDLAND | MI | 46540 | USA | BRIAN VOKAL | 248-980-1139 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes at 517-648-6339 or at ByrnesM@michigan.gov. Thank you. | 2023-10-23 | 4911 | 221112 | Not found | 10/12/2022 &nbsp;ACT | 02/01/2023 &nbsp;ACT | 2023-05-15 | 2023-05-23 | B |  | Electric and steam generation |  | EUCTGHRSG1 | 15.21 | Natural gas | 4197.6 | MMBTU/H |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of pipeline quality natural gas and good combustion practices. | 34.4 | LB/H | HOURLY | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Baghouse: average of $35,112 per ton Dry ESP: average of $48,511 per ton Wet ESP: average of $120,515 per ton Wet Scrubber: average of $40,720 per ton
MI-0455 | MIDLAND COGENERATION VENTURE LIMITED PARTNERSHIP | MIDLAND COGENERATION VENTURE LIMITED PARTNERSHIP | MIDLAND | MI | 46540 | USA | BRIAN VOKAL | 248-980-1139 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes at 517-648-6339 or at ByrnesM@michigan.gov. Thank you. | 2023-10-23 | 4911 | 221112 | Not found | 10/12/2022 &nbsp;ACT | 02/01/2023 &nbsp;ACT | 2023-05-15 | 2023-05-23 | B |  | Electric and steam generation |  | EUCTGHRSG1 | 15.21 | Natural gas | 4197.6 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of pipeline quality natural gas and good combustion practices. | 34.4 | LB/H | HOURLY | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Baghouse: average of $35,112 per ton Dry ESP: average of $48,511 per ton Wet ESP: average of $120,515 per ton Wet Scrubber: average of $40,720 per ton
MI-0455 | MIDLAND COGENERATION VENTURE LIMITED PARTNERSHIP | MIDLAND COGENERATION VENTURE LIMITED PARTNERSHIP | MIDLAND | MI | 46540 | USA | BRIAN VOKAL | 248-980-1139 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes at 517-648-6339 or at ByrnesM@michigan.gov. Thank you. | 2023-10-23 | 4911 | 221112 | Not found | 10/12/2022 &nbsp;ACT | 02/01/2023 &nbsp;ACT | 2023-05-15 | 2023-05-23 | B |  | Electric and steam generation |  | EUCTGHRSG1 | 15.21 | Natural gas | 4197.6 | MMBTU/H |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of pipeline quality natural gas and good combustion practices. | 34.4 | LB/H | HOURLY | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Baghouse: average of $35,112 per ton Dry ESP: average of $48,511 per ton Wet ESP: average of $120,515 per ton Wet Scrubber: average of $40,720 per ton
WI-0300 | NEMADJI TRAIL ENERGY CENTER | NEMADJI TRAIL ENERGY CENTER | DOUGLAS | WI | 54880 | USA |  |  |  | 5 | WI001 | WISCONSIN DEPT OF NATURAL RESOURCES; AIR MGMT. PROGRAM | MS. KRISTIN HART | (608)266-6876 | kristin.hart@wisconsin.gov |  | 18-MMC-168 | 4911 | 221121 | Not Found | 06/30/2020 &nbsp;ACT | 09/01/2020 &nbsp;ACT | 2022-06-27 | 2022-09-16 | A | https://dnr.wi.gov/cias/am/amexternal/AM_DownloadObject.aspx?id=1011796 | Natural gas-fired power plant |  | Natural-Gas-Fired Combined-Cycle Turbine (P01) | 15.21 | Natural Gas | 4671 | MMBTU/H | One Natural-Gas-Fired Siemens SGT6-8000 H Combined-Cycle Turbine with Natural Gas-Fired Duct Burner and Diesel Fuel Oil Back-Up [Maximum continuous rating: 4,671 MMBtu/hr higher heating value (HHV) when combusting natural gas, 4,027 MMBtu/hr, HHV when combusting diesel fuel oil], Selective Catalytic Reduction (SCR) (C01a) and Oxidation Catalyst (C01b) | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Only pipeline quality natural gas and diesel fuel oil may be combusted and use good combustion control according to the manufacturerâ€™s recommendations. | 36.3 | LB/H | NATURAL GAS, DUCT FIRING | BACT-PSD |  | U | 0 | U | 21.8 | LB/H | NATURAL GAS, W/O DUCT FIRING | 0 |  |  | 0 | 0 | N |  | Other limits: PM10 may not exceed 54.5 lb/hr when firing diesel fuel oil and with duct firing. PM10 may not exceed 39.4 lb/hr when firing diesel fuel oil and without duct firing. Note: The limits include front and back half PM, PM10, and PM2.5 emissions, take into account emissions from the ammonium sulfate produced from sulfur and ammonia slip that could be emitted as PM, PM10, and PM2.5 emissions, and include the duct burner emissions.
WI-0300 | NEMADJI TRAIL ENERGY CENTER | NEMADJI TRAIL ENERGY CENTER | DOUGLAS | WI | 54880 | USA |  |  |  | 5 | WI001 | WISCONSIN DEPT OF NATURAL RESOURCES; AIR MGMT. PROGRAM | MS. KRISTIN HART | (608)266-6876 | kristin.hart@wisconsin.gov |  | 18-MMC-168 | 4911 | 221121 | Not Found | 06/30/2020 &nbsp;ACT | 09/01/2020 &nbsp;ACT | 2022-06-27 | 2022-09-16 | A | https://dnr.wi.gov/cias/am/amexternal/AM_DownloadObject.aspx?id=1011796 | Natural gas-fired power plant |  | Natural-Gas-Fired Combined-Cycle Turbine (P01) | 15.21 | Natural Gas | 4671 | MMBTU/H | One Natural-Gas-Fired Siemens SGT6-8000 H Combined-Cycle Turbine with Natural Gas-Fired Duct Burner and Diesel Fuel Oil Back-Up [Maximum continuous rating: 4,671 MMBtu/hr higher heating value (HHV) when combusting natural gas, 4,027 MMBtu/hr, HHV when combusting diesel fuel oil], Selective Catalytic Reduction (SCR) (C01a) and Oxidation Catalyst (C01b) | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Only combust pipeline quality natural gas and diesel fuel oil and use good combustion control according to the manufacturerâ€™s recommendations. | 36.3 | LB/H | NATURAL GAS, DUCT FIRING | BACT-PSD |  | U | 0 | U | 21.8 | LB/H | NATURAL GAS, W/O DUCT FIRING | 0 |  |  | 0 | 0 | N |  | PM2.5 may not exceed 54.5 lb/hr when firing diesel fuel oil and with duct firing. PM2.5 may not exceed 39.4 lb/hr when firing diesel fuel oil and without duct firing. Note: The above limits include front and back half PM, PM10, and PM2.5 emissions, take into account emissions from the ammonium sulfate produced from sulfur and ammonia slip that could be emitted as PM, PM10, and PM2.5 emissions, and include the duct burner emissions.
WI-0300 | NEMADJI TRAIL ENERGY CENTER | NEMADJI TRAIL ENERGY CENTER | DOUGLAS | WI | 54880 | USA |  |  |  | 5 | WI001 | WISCONSIN DEPT OF NATURAL RESOURCES; AIR MGMT. PROGRAM | MS. KRISTIN HART | (608)266-6876 | kristin.hart@wisconsin.gov |  | 18-MMC-168 | 4911 | 221121 | Not Found | 06/30/2020 &nbsp;ACT | 09/01/2020 &nbsp;ACT | 2022-06-27 | 2022-09-16 | A | https://dnr.wi.gov/cias/am/amexternal/AM_DownloadObject.aspx?id=1011796 | Natural gas-fired power plant |  | Natural-Gas-Fired Combined-Cycle Turbine (P01) | 15.21 | Natural Gas | 4671 | MMBTU/H | One Natural-Gas-Fired Siemens SGT6-8000 H Combined-Cycle Turbine with Natural Gas-Fired Duct Burner and Diesel Fuel Oil Back-Up [Maximum continuous rating: 4,671 MMBtu/hr higher heating value (HHV) when combusting natural gas, 4,027 MMBtu/hr, HHV when combusting diesel fuel oil], Selective Catalytic Reduction (SCR) (C01a) and Oxidation Catalyst (C01b) | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Only combust pipeline quality natural gas and diesel fuel oil and use good combustion control according to the manufacturerâ€™s recommendations. | 36.3 | LB/H | NATURAL GAS, DUCT FIRING | BACT-PSD |  | U | 0 | U | 21.8 | LB/H | NATURAL GAS, W/O DUCT FIRING | 0 |  |  | 0 | 0 | N |  | Other limits: PM may not exceed 54.5 lb/hr when firing diesel fuel oil and with duct firing. (f) PM may not exceed 39.4 lb/hr when firing diesel fuel oil and without duct firing. Note: The limits include front and back half PM, PM10, and PM2.5 emissions, take into account emissions from the ammonium sulfate produced from sulfur and ammonia slip that could be emitted as PM, PM10, and PM2.5 emissions, and include the duct burner emissions.
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | Siemens Combustion Turbine - Startup &amp; Shutdown | 15.21 | Natural Gas | 35000 | MMCF/YR | Startup and Shutdown | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst and good combustion practices | 37 | LB/TURBINE/EVENT | COLD START 55 MIN OR LESS | BACT-PSD | SIP | N | 0 | N | 34 | LB/TURBINE/EVENT | WARM START 55 MIN OR LESS | 0 |  |  | 0 | 0 | N |  | 34 lb/turbine/event hot start - 50 minutes or less 56 lb/turbine/event shutdown - 38 minutes or less Alternative emission limits apply during startup and shutdown. Compliance is based on compliance with CO limits, determined by CEMS
KS-0041 | HOLLYFRONTIER EL DORADO REFINERY | HOLLYFRONTIER EL DORADO REFINING LLC | BUTLER | KS | 67042 | USA | RACHEL HENRY | 316-321-8283 | RACHEL.HENRY@HOLLYFRONTIER.COM | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov |  | CSD00080 V1.0 | 2911 | 324110 | 110000446134 | 04/29/2019 &nbsp;ACT | 10/30/2019 &nbsp;ACT | 2020-08-25 | 2023-03-27 | D |  | Petroleum Refinery located in Butler County, KS. Facility processes include distillation, cracking, reforming, isomerization, alkylation, hydrotreating, and coking. Products include a variety of grades of gasoline, fuel oils, and other fuels, along with petroleum coke and commercial grade sulfur. Products stored on-site and transported through pipeline, and by railcar and commercial trucking. By-products include petroleum coke and asphalt. The facility operates a cogeneration system that fires sweet natual gas to produce electric power and steam primarily for consumption within the facility. | This permit is for planned debottle-necking operations. Facility plans to remove operational constraints in order to operate at an increased rate and produce additional product. The following new equipment will be installed: charge heater and boiler for fluid catalytic creacking unit (FCCU), auxiliary air heater for the cogeneration plant, crude heater, crude tank, gasoline storage tank, slop oil tank, gas oil tank, and fugitive components. Modifications will be made to seven process heaters and boilers, four compressor engines, the FCCU, and the cogeneration combustion turbine. There will also be modifications made to four stationary engines subject to NSPS JJJJ (4J). The Tail Gas Treatment Unit 2, will not be physically changed but will be operated continuously (increase in operational hours). Lastly, an increase in maximum-fired duty of 70 MMBtu/hr will be made to units B306 and B307 and have been added to the PSD permit as modified heaters. Facility proposed a single heat input limit for the units B306, B307, and B-NewCrudeHeater (B308) of 381.3 MMBtu/hr. | L3804 | 15.21 | Refinery Fuel Gas | 456.5 | MMBTU/H | Cogeneration Combustion Turbine, equipped with Heat Recovery Steam Generator and steam/water injection. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Proper combustion and operation | 40 | PPMVD | 3-HOUR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emission limits should be corrected to 15% O2.
WI-0300 | NEMADJI TRAIL ENERGY CENTER | NEMADJI TRAIL ENERGY CENTER | DOUGLAS | WI | 54880 | USA |  |  |  | 5 | WI001 | WISCONSIN DEPT OF NATURAL RESOURCES; AIR MGMT. PROGRAM | MS. KRISTIN HART | (608)266-6876 | kristin.hart@wisconsin.gov |  | 18-MMC-168 | 4911 | 221121 | Not Found | 06/30/2020 &nbsp;ACT | 09/01/2020 &nbsp;ACT | 2022-06-27 | 2022-09-16 | A | https://dnr.wi.gov/cias/am/amexternal/AM_DownloadObject.aspx?id=1011796 | Natural gas-fired power plant |  | Natural Gas-Fired Combined-Cycle Turbine (P01) Start-up and Shutdown (Natural Gas) | 15.21 | Natural Gas | 0 |  | One Natural-Gas-Fired Siemens SGT6-8000H Combined-Cycle Turbine with Natural Gas-Fired Duct Burner and Diesel Fuel Oil Back-Up [Maximum continuous rating: 4,671 MMBtu/hr higher heating value (HHV) when combusting natural gas, 4,027 MMBtu/hr, HHV when combusting diesel fuel oil | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 43.6 | LB/START-UP |  | BACT-PSD |  | U | 0 | U | 10.9 | LB/SHUTDOWN |  | 0 |  |  | 0 | 0 | N |  | Total start-up and shutdown emissions: 16.6 T/YR. (based on 1525 hours per year for start-up and shutdown, combined, for natural gas operation)
WI-0300 | NEMADJI TRAIL ENERGY CENTER | NEMADJI TRAIL ENERGY CENTER | DOUGLAS | WI | 54880 | USA |  |  |  | 5 | WI001 | WISCONSIN DEPT OF NATURAL RESOURCES; AIR MGMT. PROGRAM | MS. KRISTIN HART | (608)266-6876 | kristin.hart@wisconsin.gov |  | 18-MMC-168 | 4911 | 221121 | Not Found | 06/30/2020 &nbsp;ACT | 09/01/2020 &nbsp;ACT | 2022-06-27 | 2022-09-16 | A | https://dnr.wi.gov/cias/am/amexternal/AM_DownloadObject.aspx?id=1011796 | Natural gas-fired power plant |  | Natural Gas-Fired Combined-Cycle Turbine (P01) Start-up and Shutdown (Natural Gas) | 15.21 | Natural Gas | 0 |  | One Natural-Gas-Fired Siemens SGT6-8000H Combined-Cycle Turbine with Natural Gas-Fired Duct Burner and Diesel Fuel Oil Back-Up [Maximum continuous rating: 4,671 MMBtu/hr higher heating value (HHV) when combusting natural gas, 4,027 MMBtu/hr, HHV when combusting diesel fuel oil | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 43.6 | LB/START-UP |  | BACT-PSD |  | U | 0 | U | 10.9 | LB/SHUTDOWN |  | 0 |  |  | 0 | 0 | N |  | Total start-up and shutdown emissions: 16.6 T/YR. (based on 1525 hours per year for start-up and shutdown, combined, for natural gas operation)
WI-0300 | NEMADJI TRAIL ENERGY CENTER | NEMADJI TRAIL ENERGY CENTER | DOUGLAS | WI | 54880 | USA |  |  |  | 5 | WI001 | WISCONSIN DEPT OF NATURAL RESOURCES; AIR MGMT. PROGRAM | MS. KRISTIN HART | (608)266-6876 | kristin.hart@wisconsin.gov |  | 18-MMC-168 | 4911 | 221121 | Not Found | 06/30/2020 &nbsp;ACT | 09/01/2020 &nbsp;ACT | 2022-06-27 | 2022-09-16 | A | https://dnr.wi.gov/cias/am/amexternal/AM_DownloadObject.aspx?id=1011796 | Natural gas-fired power plant |  | Natural Gas-Fired Combined-Cycle Turbine (P01) Start-up and Shutdown (Natural Gas) | 15.21 | Natural Gas | 0 |  | One Natural-Gas-Fired Siemens SGT6-8000H Combined-Cycle Turbine with Natural Gas-Fired Duct Burner and Diesel Fuel Oil Back-Up [Maximum continuous rating: 4,671 MMBtu/hr higher heating value (HHV) when combusting natural gas, 4,027 MMBtu/hr, HHV when combusting diesel fuel oil | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 43.6 | LB/START-UP |  | BACT-PSD |  | U | 0 | U | 10.9 | LB/SHUTDOWN |  | 0 |  |  | 0 | 0 | N |  | Total start-up and shutdown emissions: 16.6 T/YR. (based on 1525 hours per year for start-up and shutdown, combined, for natural gas operation)
TX-0908 | NEWMAN POWER STATION | EL PASO ELECTRIC COMPANY | EL PASO | TX |  | USA | DANIEL PEREZ | 915-543-4166 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | N284, PSDTX1090M1, GHGPSDTX199 | 3511 | 221112 | not found | 08/26/2020 &nbsp;ACT | 08/27/2021 &nbsp;ACT | 2020-10-26 | 2022-03-08 | D |  | a new natural gas simple cycle turbine along with ancillary equipment. |  | Simple Cycle Turbine | 15.21 | natural gas | 230 | MW | Mitsubishi 501 G Series | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry Low NOx Burners and SCR | 2.5 | PPMVD |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | GE Combustion Turbine - Option 1 - Normal Operation | 15.21 | natural gas | 34000 | MMCF/YR | Option 1: Two on one configuration: 3,482 MMBtu/hr combustion turbine with 475 MMBtu/hr duct-fired HRSG. Emission limits reflect the operation of one turbine with or without duct firing. | Nitrogen Oxides (NOx) | Other - 40 CFR 60, Methods 7E or 20 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | dry, low NOx burners and selective catalytic reduction | 2 | PPMVD @ 15% O2 | 1 H AV | BACT-PSD | NSPS , SIP | N | 0 | N | 141.3 | T/YR | 12 MO ROLLING TOTAL | 0 |  |  | 0 | 0 | N |  | Alternative emission limits apply during tuning, water washing, startup and shutdown. CEMS required.
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | Siemens Combusion Turbine - Option 2 - Normal Operation | 15.21 | Natural Gas | 35000 | MMCF/YR | Option 2: Two on one configuration: 3,116 MMBtu/hr combustion turbine with 991 MMBtu/hr duct-fired HRSG. Emission limits reflect the operation of one turbine with or without duct firing. | Nitrogen Oxides (NOx) | Other - 40 CFR 60, METHODS 7E OR 20 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | DRY, LOW NOx BURNERS & SCR | 2 | PPMVD @ 15% O2 | 1 H AV | BACT-PSD | NSPS , SIP | N | 0 | N | 141.4 | T/YR | 12 MO ROLLING TOTAL | 0 |  |  | 0 | 0 | N |  | Alternative emission limits apply during tuning, water washing, startup and shutdown. CEMS required.
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | Siemens Combustion Turbine - Startup &amp; Shutdown | 15.21 | Natural Gas | 35000 | MMCF/YR | Startup and Shutdown | Nitrogen Oxides (NOx) | Other - 40 CFR 60, Methods 7E or 20 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | dry, low NOx burners and SCR | 95 | LB/TURBINE/EVENT | COLD START 55 MIN OR LESS | BACT-PSD | NSPS , SIP | N | 0 | N | 117 | LB/TURBINE/EVENT | WARM START 55 MIN OR LESS | 0 |  |  | 0 | 0 | N |  | 8 lb/turbine/event hot start - 50 minutes or less 51 lb/turbine/event shut down - 38 minutes or less These limits apply during startup and shutdown, which are defined in the permit. Compliance based on CEMS.
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | GE Combustion Turbine - Startup and Shutdown | 15.21 | natural gas | 34000 | MMCF/YR | Startup and Shutdown | Nitrogen Oxides (NOx) | Other - 40 CFR 60, Methods 7E or 20 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry, low NOx burners and SCR | 273 | LB/TURBINE/EVENT | COLD START 60 MIN OR LESS | BACT-PSD | NSPS , SIP | N | 0 | N | 163 | LB/TURBINE/EVENT | WARM START 50 MIN OR LESS | 0 |  |  | 0 | 0 | N |  | 105 lb/turbine/event hot start - 30 minutes or less 18 lb/turbine/event shut down - 30 minutes or less These limits apply during startup and shutdown, which are defined in the permit. Determined by CEMS.
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | GE Combustion Turbine - Startup and Shutdown | 15.21 | natural gas | 34000 | MMCF/YR | Startup and Shutdown | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst and good combustion practices | 60 | LB/TURBINE/EVENT | COLD START 60 MIN OR LESS | BACT-PSD | SIP | N | 0 | N | 0 | LB/TURBINE/EVENT | WARM START 50 MIN OR LESS | 0 |  |  | 0 | 0 | N |  | 14 lb/turbine/event hot start - 30 minutes or less 65 lb/turbine/event shutdown - 30 minutes or less Alternative emission limits apply during startup and shutdown. Compliance is based on compliance with CO limits, determined by CEMS.
WI-0300 | NEMADJI TRAIL ENERGY CENTER | NEMADJI TRAIL ENERGY CENTER | DOUGLAS | WI | 54880 | USA |  |  |  | 5 | WI001 | WISCONSIN DEPT OF NATURAL RESOURCES; AIR MGMT. PROGRAM | MS. KRISTIN HART | (608)266-6876 | kristin.hart@wisconsin.gov |  | 18-MMC-168 | 4911 | 221121 | Not Found | 06/30/2020 &nbsp;ACT | 09/01/2020 &nbsp;ACT | 2022-06-27 | 2022-09-16 | A | https://dnr.wi.gov/cias/am/amexternal/AM_DownloadObject.aspx?id=1011796 | Natural gas-fired power plant |  | Natural-Gas-Fired Combined-Cycle Turbine (P01) Start-Up and Shutdown (diesel) | 15.21 | Natural Gas | 0 |  | One Natural-Gas-Fired Siemens SGT6-8000H Combined-Cycle Turbine with Natural Gas-Fired Duct Burner and Diesel Fuel Oil Back-Up [Maximum continuous rating: 4,671 MMBtu/hr higher heating value (HHV) when combusting natural gas, 4,027 MMBtu/hr, HHV when combusting diesel fuel oil], | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 78.9 | LB/START-UP |  | BACT-PSD |  | U | 0 | U | 19.7 | LB/SHUTDOWN |  | 0 |  |  | 0 | 0 | N |  | Total start-up and shutdown emissions: 2.1 T/YR. (based on 42 start-ups and 42 shutdowns per year using diesel)
WI-0300 | NEMADJI TRAIL ENERGY CENTER | NEMADJI TRAIL ENERGY CENTER | DOUGLAS | WI | 54880 | USA |  |  |  | 5 | WI001 | WISCONSIN DEPT OF NATURAL RESOURCES; AIR MGMT. PROGRAM | MS. KRISTIN HART | (608)266-6876 | kristin.hart@wisconsin.gov |  | 18-MMC-168 | 4911 | 221121 | Not Found | 06/30/2020 &nbsp;ACT | 09/01/2020 &nbsp;ACT | 2022-06-27 | 2022-09-16 | A | https://dnr.wi.gov/cias/am/amexternal/AM_DownloadObject.aspx?id=1011796 | Natural gas-fired power plant |  | Natural-Gas-Fired Combined-Cycle Turbine (P01) Start-Up and Shutdown (diesel) | 15.21 | Natural Gas | 0 |  | One Natural-Gas-Fired Siemens SGT6-8000H Combined-Cycle Turbine with Natural Gas-Fired Duct Burner and Diesel Fuel Oil Back-Up [Maximum continuous rating: 4,671 MMBtu/hr higher heating value (HHV) when combusting natural gas, 4,027 MMBtu/hr, HHV when combusting diesel fuel oil], | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 78.9 | LB/START-UP |  | BACT-PSD |  | U | 0 | U | 19.7 | LB/SHUTDOWN |  | 0 |  |  | 0 | 0 | N |  | Total start-up and shutdown emissions: 2.1 T/YR. (based on 42 start-ups and 42 shutdowns per year using diesel)
WI-0300 | NEMADJI TRAIL ENERGY CENTER | NEMADJI TRAIL ENERGY CENTER | DOUGLAS | WI | 54880 | USA |  |  |  | 5 | WI001 | WISCONSIN DEPT OF NATURAL RESOURCES; AIR MGMT. PROGRAM | MS. KRISTIN HART | (608)266-6876 | kristin.hart@wisconsin.gov |  | 18-MMC-168 | 4911 | 221121 | Not Found | 06/30/2020 &nbsp;ACT | 09/01/2020 &nbsp;ACT | 2022-06-27 | 2022-09-16 | A | https://dnr.wi.gov/cias/am/amexternal/AM_DownloadObject.aspx?id=1011796 | Natural gas-fired power plant |  | Natural-Gas-Fired Combined-Cycle Turbine (P01) Start-Up and Shutdown (diesel) | 15.21 | Natural Gas | 0 |  | One Natural-Gas-Fired Siemens SGT6-8000H Combined-Cycle Turbine with Natural Gas-Fired Duct Burner and Diesel Fuel Oil Back-Up [Maximum continuous rating: 4,671 MMBtu/hr higher heating value (HHV) when combusting natural gas, 4,027 MMBtu/hr, HHV when combusting diesel fuel oil], | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 78.9 | LB/START-UP |  | BACT-PSD |  | U | 0 | U | 19.7 | LB/SHUTDOWN |  | 0 |  |  | 0 | 0 | N |  | Total start-up and shutdown emissions: 2.1 T/YR. (based on 42 start-ups and 42 shutdowns per year using diesel)
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | Siemens Combustion Turbine - Tuning &amp; Water Washing | 15.21 | Natural Gas | 35000 | MMCF/YR | Alternative operating scenario: during periods of tuning and water washing | Nitrogen Oxides (NOx) | Other - 40 CFR 60, Methods 7E or 20 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | dry, low NOx burners and SCR | 564 | LB/TURBINE CAL DAY | 24 HR AV | BACT-PSD | NSPS , SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | This limit applies during tuning (limited to 18 hours/event) and water washing (limited to 60 minutes/event). Determined by CEMS.
AK-0085 | GAS TREATMENT PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | NORTH SLOPE BOROUGH | AK | 99734 | USA | LISA HAAS | 907.947.9353 | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - 907.465.5122 - dave.jones2@alaska.gov | AQ1524CPT01 | 4922 | 486210 | None Found | 01/25/2019 &nbsp;ACT | 08/13/2020 &nbsp;ACT | 2020-08-14 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Gas Treatment Plant (GTP) is part of one integrated liquefied natural gas (LNG) project to bring natural gas from Alaskaâ€™s North Slope to international markets in the form of LNG, as well as for in-state deliveries in the form of natural gas. The GTP will take gas from the Prudhoe Bay Unit and the Point Thomson Unit and treat/process the gas, before it is sent 807 miles through a 42-inch diameter pipeline to a liquefaction facility in Nikiski on Alaskaâ€™s Kenai Peninsula for export in foreign commerce. The emissions units at the stationary source will include cogeneration gas-fired turbines with supplemental firing duct burners for gas compression, simple cycle gas-fired turbines for power generation, gas-fired heaters for building and process heat, as well as flares for control of excess gas. In addition, the GTP will include a diesel-fired black start generator, several diesel-fired firewater pumps and emergency generators, and storage tanks for diesel and gasoline fuels. |  | Six (6) Cogeneration Gas-Fired Turbines (Treated Gas Compressor Turbines) | 15.21 | Natural Gas | 576 | MMBtu/hr | 576 MMBtu/hr includes turbine and supplemental duct burner for waste heat recovery unit for cogeneration. EUs 1-6, Treat Gas Compressor Turbines. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Good combustion practices and clean burning fuel low sulfur natural gas | 96 | PPMV SULFUR IN FUEL | PRIOR TO COMPLETING TREATMENT TRAINS | BACT-PSD |  | U | 0 | U | 16 | PPMV SULFUR IN FUEL | AFTER COMPLETING TREATMENT TRAINS | 0 |  |  | 0 | 0 | N |  | Potential SO2 emissions of 37.84 tpy and 6.32 tpy per turbine including supplemental firing duct burners for WHRU @ 96ppmv and 16 ppmv total sulfur in fuel respectively.
AK-0085 | GAS TREATMENT PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | NORTH SLOPE BOROUGH | AK | 99734 | USA | LISA HAAS | 907.947.9353 | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - 907.465.5122 - dave.jones2@alaska.gov | AQ1524CPT01 | 4922 | 486210 | None Found | 01/25/2019 &nbsp;ACT | 08/13/2020 &nbsp;ACT | 2020-08-14 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Gas Treatment Plant (GTP) is part of one integrated liquefied natural gas (LNG) project to bring natural gas from Alaskaâ€™s North Slope to international markets in the form of LNG, as well as for in-state deliveries in the form of natural gas. The GTP will take gas from the Prudhoe Bay Unit and the Point Thomson Unit and treat/process the gas, before it is sent 807 miles through a 42-inch diameter pipeline to a liquefaction facility in Nikiski on Alaskaâ€™s Kenai Peninsula for export in foreign commerce. The emissions units at the stationary source will include cogeneration gas-fired turbines with supplemental firing duct burners for gas compression, simple cycle gas-fired turbines for power generation, gas-fired heaters for building and process heat, as well as flares for control of excess gas. In addition, the GTP will include a diesel-fired black start generator, several diesel-fired firewater pumps and emergency generators, and storage tanks for diesel and gasoline fuels. |  | Six (6) Cogeneration Gas-Fired Turbines (CO2 Compressor Turbines)) | 15.21 | Natural Gas | 431 | MMBtu/hr | 431 MMBtu/hr includes turbine and supplemental duct burner for waste heat recovery unit for cogeneration. EUs 7-12, CO2 Compressor Turbines. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Good combustion practices and clean burning fuel low sulfur natural gas | 96 | PPMV SULFUR IN FUEL | PRIOR TO COMPLETING TREATMENT TRAINS | BACT-PSD |  | U | 0 | U | 16 | PPMV SULFUR IN FUEL | AFTER COMPLETING TREATMENT TRAINS | 0 |  |  | 0 | 0 | N |  | Potential SO2 emissions of 28.50 tpy and 4.76 tpy per turbine including supplemental firing duct burners for WHRU @ 96ppmv and 16 ppmv total sulfur in fuel respectively.
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | GE Combustion Turbine - Tuning &amp; Water Washing | 15.21 | natural gas | 34000 | MMCF/YR | Alternative operating scenario: during periods of tuning and water washing | Nitrogen Oxides (NOx) | Other - 40 CFR 60, Methods 7E or 20 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | dry, low NOx burners and SCR | 638 | LB/TURBINE/CAL DAY | 24 HR AV | BACT-PSD | NSPS , SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | This limit applies during tuning (limited to 18 hours/event) and water washing (limited to 60 minutes/event). Determined by CEMS.
VA-0332 | CHICKAHOMINY POWER LLC | CHICKAHOMINY POWER LLC | CHARLES CITY | VA | 23030 | USA | IRFAN ALI | (703) 226-0192 | IRFANKALI@BALICO.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer: Alison K. Sinclair Phone: (804)-527-5155 Email: Alison.Sinclair@deq.virginia.gov | 52610-1 | 4911 | 221112 | Not Found | 11/05/2018 &nbsp;ACT | 06/24/2019 &nbsp;ACT | 2019-08-07 | 2021-05-19 | A |  | Natural gas-fired combined cycle power plant, three 1 x1 configuration, 310 MW each, no duct firing, air cooled with two 84 MMBtu/H natural gas-fired auxiliary boilers, three fuel gas heaters, an emergency generator, fire water pump, and circuit breakers. | The proposed project will be a new combined-cycle electrical power generating facility utilizing three power blocks consisting of a combustion turbine with a heat recovery steam generator (HRSG) and a reheat condensing steam turbine generator (three 1 x 1 configuration). The turbine model proposed is a MHPS M501JAC turbine. The project will have a nominal net generating capacity of 1,650 MW. The proposed fuel for the turbines is pipeline-quality natural gas. Emissions from the turbines will be controlled by the use of low carbon fuels and high efficiency design (for GHG), clean fuels and GCPs (for PM, PM10 and PM2.5), SCR and dry low NOx burners (for NOx), and oxidation catalyst (for CO and VOC). Other equipment at the site, including two natural gas-fired auxiliary boilers, three fuel gas heaters, a diesel-fired emergency fire water pump, and a diesel-fired emergency generator, are also proposed and will be subject to emission controls. Natural gas piping components and electrical circuit breakers potentially emit GHG pollutants (expressed as carbon dioxide equivalents, or CO2e) and they will also be covered in the permit. This facility is not proposing duct firing in the HRSGs and is proposing air-cooled turbines that will not require cooling towers. | Three (3) Mitsubishi Hitachi Power Systems combustion turbine generators | 15.21 | natural gas | 35000 | MMCF/YR | One on one configuration: 4,066 MMBtu/H combustion turbine. Emission limits reflect the operation of each of the three turbines. | Nitrogen Oxides (NOx) | Other - 40 CFR 60, Methods 7E or 20 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Controlled by dry, low NOx burners and selective catalytic reduction (SCR). | 2 | PPMVD 15% O2 | 1 HR AVG | BACT-PSD | NSPS , SIP | N | 0 | N | 128.4 | TONS/YR | 12-MO ROLLING AVG | 0 |  |  | 0 | 0 | N |  | Alternative short-term emission limits apply during tuning, startup and shutdown. CEMS required.
AK-0085 | GAS TREATMENT PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | NORTH SLOPE BOROUGH | AK | 99734 | USA | LISA HAAS | 907.947.9353 | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - 907.465.5122 - dave.jones2@alaska.gov | AQ1524CPT01 | 4922 | 486210 | None Found | 01/25/2019 &nbsp;ACT | 08/13/2020 &nbsp;ACT | 2020-08-14 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Gas Treatment Plant (GTP) is part of one integrated liquefied natural gas (LNG) project to bring natural gas from Alaskaâ€™s North Slope to international markets in the form of LNG, as well as for in-state deliveries in the form of natural gas. The GTP will take gas from the Prudhoe Bay Unit and the Point Thomson Unit and treat/process the gas, before it is sent 807 miles through a 42-inch diameter pipeline to a liquefaction facility in Nikiski on Alaskaâ€™s Kenai Peninsula for export in foreign commerce. The emissions units at the stationary source will include cogeneration gas-fired turbines with supplemental firing duct burners for gas compression, simple cycle gas-fired turbines for power generation, gas-fired heaters for building and process heat, as well as flares for control of excess gas. In addition, the GTP will include a diesel-fired black start generator, several diesel-fired firewater pumps and emergency generators, and storage tanks for diesel and gasoline fuels. |  | Six (6) Cogeneration Gas-Fired Turbines (Treated Gas Compressor Turbines) | 15.21 | Natural Gas | 576 | MMBtu/hr | 576 MMBtu/hr includes turbine and supplemental duct burner for waste heat recovery unit for cogeneration. EUs 1-6, Treat Gas Compressor Turbines. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices and clean burning fuel (NG) | 117.1 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Potential CO2e emissions of 294,924 tpy per turbine including supplemental firing duct burners for WHRU. The 117.1 lb/MMBtu emission rate is the carbon dioxide equivalent (CO2e) emissions rates for burning natural gas in 40 CFR Part 98: Mandatory Greenhouse Gas Reporting. The total CO2e emissions rate is calculated with the equation CO2(1) + CH4(25) + N2O(298).
AK-0085 | GAS TREATMENT PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | NORTH SLOPE BOROUGH | AK | 99734 | USA | LISA HAAS | 907.947.9353 | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - 907.465.5122 - dave.jones2@alaska.gov | AQ1524CPT01 | 4922 | 486210 | None Found | 01/25/2019 &nbsp;ACT | 08/13/2020 &nbsp;ACT | 2020-08-14 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Gas Treatment Plant (GTP) is part of one integrated liquefied natural gas (LNG) project to bring natural gas from Alaskaâ€™s North Slope to international markets in the form of LNG, as well as for in-state deliveries in the form of natural gas. The GTP will take gas from the Prudhoe Bay Unit and the Point Thomson Unit and treat/process the gas, before it is sent 807 miles through a 42-inch diameter pipeline to a liquefaction facility in Nikiski on Alaskaâ€™s Kenai Peninsula for export in foreign commerce. The emissions units at the stationary source will include cogeneration gas-fired turbines with supplemental firing duct burners for gas compression, simple cycle gas-fired turbines for power generation, gas-fired heaters for building and process heat, as well as flares for control of excess gas. In addition, the GTP will include a diesel-fired black start generator, several diesel-fired firewater pumps and emergency generators, and storage tanks for diesel and gasoline fuels. |  | Six (6) Cogeneration Gas-Fired Turbines (CO2 Compressor Turbines)) | 15.21 | Natural Gas | 431 | MMBtu/hr | 431 MMBtu/hr includes turbine and supplemental duct burner for waste heat recovery unit for cogeneration. EUs 7-12, CO2 Compressor Turbines. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices and clean burning fuel (NG) | 117.1 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Potential CO2e emissions of 221,962 tpy per turbine including supplemental firing duct burners for WHRU. The 117.1 lb/MMBtu emission rate is the carbon dioxide equivalent (CO2e) emissions rates for burning natural gas in 40 CFR Part 98: Mandatory Greenhouse Gas Reporting. The total CO2e emissions rate is calculated with the equation CO2(1) + CH4(25) + N2O(298).
AK-0088 | LIQUEFACTION PLANT | ALASKA GASLINE DEVELOPMENT CORPORATION | KENAI PENNINSULA BOROUGH | AK | 99635 | USA | LISA HAAS |  | LHAAS@AGDC.US | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dave Jones - Permit Writer - dave.jones2@alaska.gov | AQ1539CPT01 | 4922 | 488999 | Not Found | 01/14/2020 &nbsp;ACT | 07/07/2022 &nbsp;ACT | 2022-08-04 | 2022-08-16 | A | https://dec.alaska.gov/Applications/Air/airtoolsweb/AirPermitsApprovalsAndPublicNotices | The Liquefaction Plant is planned to encompass 921 acres, including 901 acres onshore for the liquefied natural gas (LNG) Plant as well as 20 acres offshore for the Marine Terminal. The Liquefaction Plant will be the terminus of an approximately 807-mile gas pipeline, allowing natural gas from Alaskaâ€™s North Slope to be shipped to outside markets. The stationary source will consist of structures and equipment associated with processing, storage, and loading of LNG. There will be three liquefaction trains combining to process up to approximately 20 million metric tons per annun of LNG. |  | Four Combined Cycle Gas-Fired Turbines | 15.21 | Natural Gas | 384 | MMBtu/hr | EUs 7 - 10 are combined cycle gas turbines used for power generation at LNG facility | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices and burning clean fuels (natural gas) | 117.1 | LB/MMBTU | 3-HOURS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
WI-0306 | WPL- RIVERSIDE ENERGY CENTER | WPL- RIVERSIDE ENERGY CENTER | ROCK | WI | 53511 | USA |  |  |  | 5 | WI001 | WISCONSIN DEPT OF NATURAL RESOURCES; AIR MGMT. PROGRAM | MS. KRISTIN HART | (608)266-6876 | kristin.hart@wisconsin.gov |  | 19-POY-212 | 4911 | 221112 | 110016895519 | 01/23/2020 &nbsp;ACT | 02/28/2020 &nbsp;ACT | 2022-07-14 | 2022-09-16 | D | https://dnr.wi.gov/cias/am/amexternal/AM_DownloadObject.aspx?id=941584 | Electric Power Generation |  | Natural Gas Fired Combustion Turbine (P20, P21) Phase I Commissioning | 15.21 | Natural Gas | 2208 | MMBTU/H | Natural gas fired combustion turbine with heat recovery steam generator (HRSG). Phase I commissioning is the period of initial cranking and steam blows when starting a turbine for the first time. Total fuel input (natural gas) to the turbines may not exceed 882 million cubic feet for both turbines combined and 1.20 million cubic feet in any hour for a single turbine. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 118 | LB CO2/MMBTU | HEAT INPUT | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0834 | MONTGOMERY COUNTY POWER STATIOIN | ENTERGY TEXAS INC | MONTGOMERY | TX |  | USA | CHRISTOPHER BURKE | 281-297-3369 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., 512-239-2175 laura.gibson@tceq.texas.gov | N256, PSDTX1510, AND GHGPSDTX1 | 4911 | 221112 | Not Found | 01/18/2018 &nbsp;ACT | 03/30/2018 &nbsp;ACT | 2018-04-26 | 2019-02-19 | A |  |  |  | Combined Cycle Turbine | 15.21 | NATURAL GAS | 2635 | MMBTU/HR/UNIT | Two Mitsubishi M501GAC turbines (without fast start) | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | PIPELINE NATURAL GAS, GOOD COMBUSTION | 125.7 | TON/YR |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK & TTTT, MACT YYYY
TX-0834 | MONTGOMERY COUNTY POWER STATIOIN | ENTERGY TEXAS INC | MONTGOMERY | TX |  | USA | CHRISTOPHER BURKE | 281-297-3369 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., 512-239-2175 laura.gibson@tceq.texas.gov | N256, PSDTX1510, AND GHGPSDTX1 | 4911 | 221112 | Not Found | 01/18/2018 &nbsp;ACT | 03/30/2018 &nbsp;ACT | 2018-04-26 | 2019-02-19 | A |  |  |  | Combined Cycle Turbine | 15.21 | NATURAL GAS | 2635 | MMBTU/HR/UNIT | Two Mitsubishi M501GAC turbines (without fast start) | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | PIPELINE NATURAL GAS, GOOD COMBUSTION | 125.7 | TON/YR |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK & TTTT, MACT YYYY
TX-0834 | MONTGOMERY COUNTY POWER STATIOIN | ENTERGY TEXAS INC | MONTGOMERY | TX |  | USA | CHRISTOPHER BURKE | 281-297-3369 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., 512-239-2175 laura.gibson@tceq.texas.gov | N256, PSDTX1510, AND GHGPSDTX1 | 4911 | 221112 | Not Found | 01/18/2018 &nbsp;ACT | 03/30/2018 &nbsp;ACT | 2018-04-26 | 2019-02-19 | A |  |  |  | Combined Cycle Turbine | 15.21 | NATURAL GAS | 2635 | MMBTU/HR/UNIT | Two Mitsubishi M501GAC turbines (without fast start) | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | PIPELINE NATURAL GAS, GOOD COMBUSTION | 125.7 | TON/YR |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK & TTTT, MACT YYYY
WI-0306 | WPL- RIVERSIDE ENERGY CENTER | WPL- RIVERSIDE ENERGY CENTER | ROCK | WI | 53511 | USA |  |  |  | 5 | WI001 | WISCONSIN DEPT OF NATURAL RESOURCES; AIR MGMT. PROGRAM | MS. KRISTIN HART | (608)266-6876 | kristin.hart@wisconsin.gov |  | 19-POY-212 | 4911 | 221112 | 110016895519 | 01/23/2020 &nbsp;ACT | 02/28/2020 &nbsp;ACT | 2022-07-14 | 2022-09-16 | D | https://dnr.wi.gov/cias/am/amexternal/AM_DownloadObject.aspx?id=941584 | Electric Power Generation |  | Natural Gas Fired Combustion Turbine (P20, P21) Phase II Commissioning | 15.21 | Natural Gas | 2208 | MMBTU/H | Natural gas fired combustion turbine with heat recovery steam generator (HRSG). Phase II commissioning is the period when synchronizing the turbine through SCR tuning after Phase I. Total fuel input (natural gas) to the turbines may not exceed 1,960 Million cubic feet for both turbines combined. Oxidation catalyst must run at all times during Phase II commissioning. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N |  | 150 | PPMVD, 15% OXYGEN | AVG. ANY 24-HR OPERATIONAL PERIOD | BACT-PSD |  | U | 0 | U | 1500 | LB | IN ANY HOUR | 0 |  |  | 0 | 0 | N |  | Carbon monoxide emissions may not exceed the limits from either turbine for the first 240 hours of Phase II operation of that turbine. After 240 hours, emissions limitation from prior permits apply.
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | GE Combustion Turbine - Tuning &amp; Water Washing | 15.21 | natural gas | 34000 | MMCF/YR | Alternative operating scenario: during periods of tuning and water washing | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practices | 194 | LB/TURBINE/DAY | 24 HR AV | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | This limit applies during tuning (limited to 18 hours/event) and water washing (limited to 60 minutes/event). Determined by CEMS.
VA-0332 | CHICKAHOMINY POWER LLC | CHICKAHOMINY POWER LLC | CHARLES CITY | VA | 23030 | USA | IRFAN ALI | (703) 226-0192 | IRFANKALI@BALICO.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer: Alison K. Sinclair Phone: (804)-527-5155 Email: Alison.Sinclair@deq.virginia.gov | 52610-1 | 4911 | 221112 | Not Found | 11/05/2018 &nbsp;ACT | 06/24/2019 &nbsp;ACT | 2019-08-07 | 2021-05-19 | A |  | Natural gas-fired combined cycle power plant, three 1 x1 configuration, 310 MW each, no duct firing, air cooled with two 84 MMBtu/H natural gas-fired auxiliary boilers, three fuel gas heaters, an emergency generator, fire water pump, and circuit breakers. | The proposed project will be a new combined-cycle electrical power generating facility utilizing three power blocks consisting of a combustion turbine with a heat recovery steam generator (HRSG) and a reheat condensing steam turbine generator (three 1 x 1 configuration). The turbine model proposed is a MHPS M501JAC turbine. The project will have a nominal net generating capacity of 1,650 MW. The proposed fuel for the turbines is pipeline-quality natural gas. Emissions from the turbines will be controlled by the use of low carbon fuels and high efficiency design (for GHG), clean fuels and GCPs (for PM, PM10 and PM2.5), SCR and dry low NOx burners (for NOx), and oxidation catalyst (for CO and VOC). Other equipment at the site, including two natural gas-fired auxiliary boilers, three fuel gas heaters, a diesel-fired emergency fire water pump, and a diesel-fired emergency generator, are also proposed and will be subject to emission controls. Natural gas piping components and electrical circuit breakers potentially emit GHG pollutants (expressed as carbon dioxide equivalents, or CO2e) and they will also be covered in the permit. This facility is not proposing duct firing in the HRSGs and is proposing air-cooled turbines that will not require cooling towers. | Three (3) Mitsubishi Hitachi Power Systems Combustion | 15.21 | natural gas | 35000 | MMCF/YR | Alternative operating scenario: during periods of tuning | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practices | 214 | LB/TURBINE/DAY | 24 HR TOTAL | BACT-PSD | SIP , NSPS | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | This limit applies during tuning (limited to 18 hours/event). Determined by CEMS.
VA-0332 | CHICKAHOMINY POWER LLC | CHICKAHOMINY POWER LLC | CHARLES CITY | VA | 23030 | USA | IRFAN ALI | (703) 226-0192 | IRFANKALI@BALICO.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer: Alison K. Sinclair Phone: (804)-527-5155 Email: Alison.Sinclair@deq.virginia.gov | 52610-1 | 4911 | 221112 | Not Found | 11/05/2018 &nbsp;ACT | 06/24/2019 &nbsp;ACT | 2019-08-07 | 2021-05-19 | A |  | Natural gas-fired combined cycle power plant, three 1 x1 configuration, 310 MW each, no duct firing, air cooled with two 84 MMBtu/H natural gas-fired auxiliary boilers, three fuel gas heaters, an emergency generator, fire water pump, and circuit breakers. | The proposed project will be a new combined-cycle electrical power generating facility utilizing three power blocks consisting of a combustion turbine with a heat recovery steam generator (HRSG) and a reheat condensing steam turbine generator (three 1 x 1 configuration). The turbine model proposed is a MHPS M501JAC turbine. The project will have a nominal net generating capacity of 1,650 MW. The proposed fuel for the turbines is pipeline-quality natural gas. Emissions from the turbines will be controlled by the use of low carbon fuels and high efficiency design (for GHG), clean fuels and GCPs (for PM, PM10 and PM2.5), SCR and dry low NOx burners (for NOx), and oxidation catalyst (for CO and VOC). Other equipment at the site, including two natural gas-fired auxiliary boilers, three fuel gas heaters, a diesel-fired emergency fire water pump, and a diesel-fired emergency generator, are also proposed and will be subject to emission controls. Natural gas piping components and electrical circuit breakers potentially emit GHG pollutants (expressed as carbon dioxide equivalents, or CO2e) and they will also be covered in the permit. This facility is not proposing duct firing in the HRSGs and is proposing air-cooled turbines that will not require cooling towers. | Three (3) Mitsubishi Hitachi Power Systems combustion turbine generators | 15.21 | natural gas | 35000 | MMCF/YR | Startup and Shutdown | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst and good combustion practices | 216 | LB/TURBINE/EVENT | COLD START 42 MIN OR LESS | BACT-PSD | NSPS , SIP | N | 0 | N | 216 | LB/TURBINE/EVENT | WARM START 42 MIN OR LESS | 0 |  |  | 0 | 0 | N |  | 168 lb/turbine/event hot start - 42 minutes or less 216 lb/turbine/event shutdown - 42 minutes or less Alternative emission limits apply during startup and shutdown. Compliance is based on compliance with CO limits, determined by CEMS.
TX-0834 | MONTGOMERY COUNTY POWER STATIOIN | ENTERGY TEXAS INC | MONTGOMERY | TX |  | USA | CHRISTOPHER BURKE | 281-297-3369 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., 512-239-2175 laura.gibson@tceq.texas.gov | N256, PSDTX1510, AND GHGPSDTX1 | 4911 | 221112 | Not Found | 01/18/2018 &nbsp;ACT | 03/30/2018 &nbsp;ACT | 2018-04-26 | 2019-02-19 | A |  |  |  | COMBINED CYCLE TURBINE MSS REDUCED LOAD | 15.21 | NATURAL GAS | 0 |  | 9 HOURS STARTUP, 1 HOUR SHUTDOWN | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | minimizing duration of startup / shutdown events, engaging the pollution control equipment as soon as practicable (based on vendor recommendations and guarantees), and meeting the emissions limits on the MAERT | 223 | TON/H |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK & TTTT, MACT YYYY
VA-0332 | CHICKAHOMINY POWER LLC | CHICKAHOMINY POWER LLC | CHARLES CITY | VA | 23030 | USA | IRFAN ALI | (703) 226-0192 | IRFANKALI@BALICO.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer: Alison K. Sinclair Phone: (804)-527-5155 Email: Alison.Sinclair@deq.virginia.gov | 52610-1 | 4911 | 221112 | Not Found | 11/05/2018 &nbsp;ACT | 06/24/2019 &nbsp;ACT | 2019-08-07 | 2021-05-19 | A |  | Natural gas-fired combined cycle power plant, three 1 x1 configuration, 310 MW each, no duct firing, air cooled with two 84 MMBtu/H natural gas-fired auxiliary boilers, three fuel gas heaters, an emergency generator, fire water pump, and circuit breakers. | The proposed project will be a new combined-cycle electrical power generating facility utilizing three power blocks consisting of a combustion turbine with a heat recovery steam generator (HRSG) and a reheat condensing steam turbine generator (three 1 x 1 configuration). The turbine model proposed is a MHPS M501JAC turbine. The project will have a nominal net generating capacity of 1,650 MW. The proposed fuel for the turbines is pipeline-quality natural gas. Emissions from the turbines will be controlled by the use of low carbon fuels and high efficiency design (for GHG), clean fuels and GCPs (for PM, PM10 and PM2.5), SCR and dry low NOx burners (for NOx), and oxidation catalyst (for CO and VOC). Other equipment at the site, including two natural gas-fired auxiliary boilers, three fuel gas heaters, a diesel-fired emergency fire water pump, and a diesel-fired emergency generator, are also proposed and will be subject to emission controls. Natural gas piping components and electrical circuit breakers potentially emit GHG pollutants (expressed as carbon dioxide equivalents, or CO2e) and they will also be covered in the permit. This facility is not proposing duct firing in the HRSGs and is proposing air-cooled turbines that will not require cooling towers. | Three (3) Mitsubishi Hitachi Power Systems combustion turbine generators | 15.21 | natural gas | 35000 | MMCF/YR | Startup and Shutdown | Nitrogen Oxides (NOx) | Other - 40 CFR 60, Methods 7E or 20 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | dry, low NOx burners and selective catalytic reduction | 60 | LB/TURBINE/EVENT | COLD START-42 MINUTES OR LESS | BACT-PSD | SIP , NSPS | N | 0 | N | 0 | LB/TURBINE/EVENT | COLD START-42 MINUTES OR LESS | 0 |  |  | 0 | 0 | N |  | 42 lb/turbine/event hot start - 42 minutes or less 20 lb/turbine/event shut down - 15 minutes or less These limits apply during startup and shutdown, which are defined in the permit. Determined by CEMS.
VA-0332 | CHICKAHOMINY POWER LLC | CHICKAHOMINY POWER LLC | CHARLES CITY | VA | 23030 | USA | IRFAN ALI | (703) 226-0192 | IRFANKALI@BALICO.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer: Alison K. Sinclair Phone: (804)-527-5155 Email: Alison.Sinclair@deq.virginia.gov | 52610-1 | 4911 | 221112 | Not Found | 11/05/2018 &nbsp;ACT | 06/24/2019 &nbsp;ACT | 2019-08-07 | 2021-05-19 | A |  | Natural gas-fired combined cycle power plant, three 1 x1 configuration, 310 MW each, no duct firing, air cooled with two 84 MMBtu/H natural gas-fired auxiliary boilers, three fuel gas heaters, an emergency generator, fire water pump, and circuit breakers. | The proposed project will be a new combined-cycle electrical power generating facility utilizing three power blocks consisting of a combustion turbine with a heat recovery steam generator (HRSG) and a reheat condensing steam turbine generator (three 1 x 1 configuration). The turbine model proposed is a MHPS M501JAC turbine. The project will have a nominal net generating capacity of 1,650 MW. The proposed fuel for the turbines is pipeline-quality natural gas. Emissions from the turbines will be controlled by the use of low carbon fuels and high efficiency design (for GHG), clean fuels and GCPs (for PM, PM10 and PM2.5), SCR and dry low NOx burners (for NOx), and oxidation catalyst (for CO and VOC). Other equipment at the site, including two natural gas-fired auxiliary boilers, three fuel gas heaters, a diesel-fired emergency fire water pump, and a diesel-fired emergency generator, are also proposed and will be subject to emission controls. Natural gas piping components and electrical circuit breakers potentially emit GHG pollutants (expressed as carbon dioxide equivalents, or CO2e) and they will also be covered in the permit. This facility is not proposing duct firing in the HRSGs and is proposing air-cooled turbines that will not require cooling towers. | Three (3) Mitsubishi Hitachi Power Systems Combustion | 15.21 | natural gas | 35000 | MMCF/YR | Alternative operating scenario: during periods of tuning | Nitrogen Oxides (NOx) | Other - 40 CFR 60, Methods 7E or 20 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | dry, low NOx burners and selective catalytic reduction | 703 | LB/TURBINE/CAL. DAY | 24 HR TOTAL | BACT-PSD | NSPS , SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | This limit applies during tuning (limited to 18 hours/event). Determined by CEMS.
VA-0334 | DOMINION ENERGY - BRUNSWICK | VIRGINIA ELECTRIC AND POWER COMPANY | BRUNSWICK | VA | 23856 | USA | ROBERT SAWYER |  |  | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | For technical information about this facility, please contact the Air Permit writer, Alison Sinclar, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52404-5 | 4911 | 221112 | 110070060282 | 04/09/2019 &nbsp;ACT | 12/01/2020 &nbsp;ACT | 2021-03-29 | 2022-03-08 | B |  | Natural gas-fired combined cycle power plant. | The Dominion Brunswick County Power station received its initial PSD permit to construct and operate on March 12, 2013. At the time of the issuance of that permit, alternative operating scenarios for combustion turbines, such as tuning and online turbine blade washing had not been developed. This permit includes alternative emission limits for the Brunswick plant during tuning and online water washing. There is no increase in annual emissions from the turbines due to the inclusion of alternative short term emission limits for NOx and CO during tuning and water-washing. | COMBUSTION TURBINE GENERATORS, (3) with Alternate Operating Scenario - Turbine Tuning | 15.21 | natural gas | 3442 | MMBTU/H | Three Mitsubishi M501 GAC combustion turbine generators with HRSG duct burners. For the purpose of this permit, tuning is defined as the manipulation of the units and associated emission controls to ensure optimized operation and minimized emissions. No tuning event shall last more than 18 consecutive hours. Annual tuning events shall be limited to 96 hours per CT per 12-month rolling period. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Dry, low NOx burners and selective catalytic reduction (SCR) with a NOx performance of 2.0 ppmvd at 15% O2. | 604 | LBS | CALENDAR DAY/PER TURBINE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NOx will be continually monitored with CEMS and the facility must track the duration and frequency of tuning events for the turbines, including date and times. The NOx CEMS must be operational during these events, as well as the SCR.
VA-0334 | DOMINION ENERGY - BRUNSWICK | VIRGINIA ELECTRIC AND POWER COMPANY | BRUNSWICK | VA | 23856 | USA | ROBERT SAWYER |  |  | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | For technical information about this facility, please contact the Air Permit writer, Alison Sinclar, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52404-5 | 4911 | 221112 | 110070060282 | 04/09/2019 &nbsp;ACT | 12/01/2020 &nbsp;ACT | 2021-03-29 | 2022-03-08 | B |  | Natural gas-fired combined cycle power plant. | The Dominion Brunswick County Power station received its initial PSD permit to construct and operate on March 12, 2013. At the time of the issuance of that permit, alternative operating scenarios for combustion turbines, such as tuning and online turbine blade washing had not been developed. This permit includes alternative emission limits for the Brunswick plant during tuning and online water washing. There is no increase in annual emissions from the turbines due to the inclusion of alternative short term emission limits for NOx and CO during tuning and water-washing. | COMBUSTION TURBINE GENERATORS, (3) with Alternate Operating Scenario - Turbine Blade Water Washing | 15.21 | Natural Gas | 3442 | MMBTU/H | Three Mitsubishi M501 GAC combustion turbine generators with HRSG duct burners. On-line water washing is defined as spraying water through the turbine while a unit is operating for the purpose of cleaning the CT compressor blades. No on-line water wash event shall last for more than 60 minutes in a calendar day. Annual on-line water wash events shall not exceed 52 hours per CT per 12-month rolling period. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Dry, low NOx burners and selective catalytic reduction (SCR) with a NOx performance of 2.0 ppmvd at 15% O2. | 604 | LBS | CALENDAR DAY/PER TURBINE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NOx will be continually monitored with CEMS and the facility must track the duration and frequency of water washing events for the turbines, including date and times. The NOx CEMS must be operational during these events, as well as the SCR.
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | Siemens Combustion Turbine - Tuning &amp; Water Washing | 15.21 | Natural Gas | 35000 | MMCF/YR | Alternative operating scenario: during periods of tuning and water washing | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practices | 309 | LB/TURBINE/DAY | 24 HR AV | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | This limit applies during tuning (limited to 18 hours/event) and water washing (limited to 60 minutes/event). Determined by CEMS.
WI-0300 | NEMADJI TRAIL ENERGY CENTER | NEMADJI TRAIL ENERGY CENTER | DOUGLAS | WI | 54880 | USA |  |  |  | 5 | WI001 | WISCONSIN DEPT OF NATURAL RESOURCES; AIR MGMT. PROGRAM | MS. KRISTIN HART | (608)266-6876 | kristin.hart@wisconsin.gov |  | 18-MMC-168 | 4911 | 221121 | Not Found | 06/30/2020 &nbsp;ACT | 09/01/2020 &nbsp;ACT | 2022-06-27 | 2022-09-16 | A | https://dnr.wi.gov/cias/am/amexternal/AM_DownloadObject.aspx?id=1011796 | Natural gas-fired power plant |  | Natural-Gas-Fired Combined-Cycle Turbine (P01) | 15.21 | Natural Gas | 4671 | MMBTU/H | One Natural-Gas-Fired Siemens SGT6-8000 H Combined-Cycle Turbine with Natural Gas-Fired Duct Burner and Diesel Fuel Oil Back-Up [Maximum continuous rating: 4,671 MMBtu/hr higher heating value (HHV) when combusting natural gas, 4,027 MMBtu/hr, HHV when combusting diesel fuel oil], Selective Catalytic Reduction (SCR) (C01a) and Oxidation Catalyst (C01b) | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Selective Catalytic Reduction (SCR), low-NOx burners, Water injection when firing diesel fuel oil. | 2 | PPM AT 15% O2 | 24-HR ROLLING AVG., NATURAL GAS | BACT-PSD |  | U | 85 | U | 6 | PPM AT 15% O2 | 24-HR ROLLING AVG., DIESEL | 0 |  |  | 0 | 0 | N |  | Except during start-up and shutdown
WI-0299 | WPL- RIVERSIDE ENERGY CENTER | WPL- RIVERSIDE ENERGY CENTER | ROCK | WI | 53511 | USA |  |  |  | 5 | WI001 | WISCONSIN DEPT OF NATURAL RESOURCES; AIR MGMT. PROGRAM | MS. KRISTIN HART | (608)266-6876 | kristin.hart@wisconsin.gov |  | 19-POY-151 | 4911 | 221112 | 110016895519 | 07/13/2020 &nbsp;ACT | 08/20/2020 &nbsp;ACT | 2022-06-21 | 2022-09-16 | D | https://dnr.wi.gov/cias/am/amexternal/AM_DownloadObject.aspx?id=1008031 | Electric Power Generation |  | Natural gas fired combustion turbine with heat recovery steam generator (P20, P21) | 15.21 | Natural Gas | 250 | MMBTU/H | Two (2) combustion turbines rated at 168MW (based on average base load conditions at 59 ËšF). Each heat recovery steam generator includes a selective catalytic reduction system and an oxidation catalyst. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 350 | T | DURING ANY DOCUMENTED STARTUP EVENT | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
VA-0334 | DOMINION ENERGY - BRUNSWICK | VIRGINIA ELECTRIC AND POWER COMPANY | BRUNSWICK | VA | 23856 | USA | ROBERT SAWYER |  |  | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | For technical information about this facility, please contact the Air Permit writer, Alison Sinclar, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52404-5 | 4911 | 221112 | 110070060282 | 04/09/2019 &nbsp;ACT | 12/01/2020 &nbsp;ACT | 2021-03-29 | 2022-03-08 | B |  | Natural gas-fired combined cycle power plant. | The Dominion Brunswick County Power station received its initial PSD permit to construct and operate on March 12, 2013. At the time of the issuance of that permit, alternative operating scenarios for combustion turbines, such as tuning and online turbine blade washing had not been developed. This permit includes alternative emission limits for the Brunswick plant during tuning and online water washing. There is no increase in annual emissions from the turbines due to the inclusion of alternative short term emission limits for NOx and CO during tuning and water-washing. | COMBUSTION TURBINE GENERATORS, (3) with Alternate Operating Scenario - Turbine Tuning | 15.21 | natural gas | 3442 | MMBTU/H | Three Mitsubishi M501 GAC combustion turbine generators with HRSG duct burners. For the purpose of this permit, tuning is defined as the manipulation of the units and associated emission controls to ensure optimized operation and minimized emissions. No tuning event shall last more than 18 consecutive hours. Annual tuning events shall be limited to 96 hours per CT per 12-month rolling period. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Oxidation catalyst and good combustion practices. | 416 | LBS | CALENDAR DAY/PER TURBINE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | CO will be continually monitored with CEMS and the facility must track the duration and frequency of tuning events for the turbines, including date and times. The CO CEMS must be operational during these events, as well as the Oxidation Catalyst controls.
VA-0334 | DOMINION ENERGY - BRUNSWICK | VIRGINIA ELECTRIC AND POWER COMPANY | BRUNSWICK | VA | 23856 | USA | ROBERT SAWYER |  |  | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | For technical information about this facility, please contact the Air Permit writer, Alison Sinclar, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52404-5 | 4911 | 221112 | 110070060282 | 04/09/2019 &nbsp;ACT | 12/01/2020 &nbsp;ACT | 2021-03-29 | 2022-03-08 | B |  | Natural gas-fired combined cycle power plant. | The Dominion Brunswick County Power station received its initial PSD permit to construct and operate on March 12, 2013. At the time of the issuance of that permit, alternative operating scenarios for combustion turbines, such as tuning and online turbine blade washing had not been developed. This permit includes alternative emission limits for the Brunswick plant during tuning and online water washing. There is no increase in annual emissions from the turbines due to the inclusion of alternative short term emission limits for NOx and CO during tuning and water-washing. | COMBUSTION TURBINE GENERATORS, (3) with Alternate Operating Scenario - Turbine Blade Water Washing | 15.21 | Natural Gas | 3442 | MMBTU/H | Three Mitsubishi M501 GAC combustion turbine generators with HRSG duct burners. On-line water washing is defined as spraying water through the turbine while a unit is operating for the purpose of cleaning the CT compressor blades. No on-line water wash event shall last for more than 60 minutes in a calendar day. Annual on-line water wash events shall not exceed 52 hours per CT per 12-month rolling period. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Oxidation catalyst and good combustion practices. | 416 | LBS | CALENDAR DAY/PER TURBINE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | CO will be continually monitored with CEMS and the facility must track the duration and frequency of water washing events for the turbines, including date and times. The CO CEMS must be operational during these events, as well as the Oxidation Catalyst controls.
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | Siemens Combustion Turbine - Startup &amp; Shutdown | 15.21 | Natural Gas | 35000 | MMCF/YR | Startup and Shutdown | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practices | 434 | LB/TURBINE/EVENT | COLD START 55 MIN OR LESS | BACT-PSD | SIP | N | 0 | N | 397 | LB/TURBINE/EVENT | WARM START 55 MIN OR LESS | 0 |  |  | 0 | 0 | N |  | 36 lb/turbine/event hot start - 50 minutes or less 184 lb/turbine/event shutdown - 38 minutes or less These limits apply during startup and shutdown. CEMS required.
VA-0332 | CHICKAHOMINY POWER LLC | CHICKAHOMINY POWER LLC | CHARLES CITY | VA | 23030 | USA | IRFAN ALI | (703) 226-0192 | IRFANKALI@BALICO.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer: Alison K. Sinclair Phone: (804)-527-5155 Email: Alison.Sinclair@deq.virginia.gov | 52610-1 | 4911 | 221112 | Not Found | 11/05/2018 &nbsp;ACT | 06/24/2019 &nbsp;ACT | 2019-08-07 | 2021-05-19 | A |  | Natural gas-fired combined cycle power plant, three 1 x1 configuration, 310 MW each, no duct firing, air cooled with two 84 MMBtu/H natural gas-fired auxiliary boilers, three fuel gas heaters, an emergency generator, fire water pump, and circuit breakers. | The proposed project will be a new combined-cycle electrical power generating facility utilizing three power blocks consisting of a combustion turbine with a heat recovery steam generator (HRSG) and a reheat condensing steam turbine generator (three 1 x 1 configuration). The turbine model proposed is a MHPS M501JAC turbine. The project will have a nominal net generating capacity of 1,650 MW. The proposed fuel for the turbines is pipeline-quality natural gas. Emissions from the turbines will be controlled by the use of low carbon fuels and high efficiency design (for GHG), clean fuels and GCPs (for PM, PM10 and PM2.5), SCR and dry low NOx burners (for NOx), and oxidation catalyst (for CO and VOC). Other equipment at the site, including two natural gas-fired auxiliary boilers, three fuel gas heaters, a diesel-fired emergency fire water pump, and a diesel-fired emergency generator, are also proposed and will be subject to emission controls. Natural gas piping components and electrical circuit breakers potentially emit GHG pollutants (expressed as carbon dioxide equivalents, or CO2e) and they will also be covered in the permit. This facility is not proposing duct firing in the HRSGs and is proposing air-cooled turbines that will not require cooling towers. | Three (3) Mitsubishi Hitachi Power Systems combustion turbine generators | 15.21 | natural gas | 35000 | MMCF/YR | Startup and Shutdown | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practices | 444 | LB/TURBINE/EVENT | COLD START 42 MIN OR LESS | BACT-PSD | SIP | N | 0 | N | 396 | LB/TURBINE/EVENT | WARM START 42 MIN OR LESS | 0 |  |  | 0 | 0 | N |  | 252 lb/turbine/event hot start - 42 minutes or less 156 lb/turbine/event shutdown - 42 minutes or less These limits apply during startup and shutdown. CEMS required.
LA-0391 | MAGNOLIA POWER GENERATING STATION UNIT 1 | MAGNOLIA POWER LLC | IBERVILLE | LA | 70764 | USA | WILLIAM DAVIS | 609-250-7707 | LEE.DAVIS@KINDLE-ENERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Ms. Lori Pittman, (225)219-3180 | PSD-LA-839 | 4911 | 221112 | Not Found | 09/08/2020 &nbsp;ACT | 06/03/2022 &nbsp;ACT | 2023-03-02 | 2023-05-23 | A | https://edms.deq.louisiana.gov/app/doc/view?doc=13323738 | Magnolia Power LLC (Magnolia Power) is proposing to construct and operate a power plant, Magnolia Power Generating Station Unit 1, consisting of a natural gas-fired combined cycle gas turbine (CCGT Unit) in Iberville Parish, Louisiana. The CCGT Unit (EQT001), which includes a heat recovery steam generator (HRSG) equipped with duct burners, will have a predicted net nominal output of 730 megawatts (MW) |  | Combined Cycle Gas Turbine Startup and Shutdown | 15.21 | Natural Gas | 5081 | mm BTU/h | Startup and shutdown emissions from the combined cycle gas turbine. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices. | 520 | LB/HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
WI-0300 | NEMADJI TRAIL ENERGY CENTER | NEMADJI TRAIL ENERGY CENTER | DOUGLAS | WI | 54880 | USA |  |  |  | 5 | WI001 | WISCONSIN DEPT OF NATURAL RESOURCES; AIR MGMT. PROGRAM | MS. KRISTIN HART | (608)266-6876 | kristin.hart@wisconsin.gov |  | 18-MMC-168 | 4911 | 221121 | Not Found | 06/30/2020 &nbsp;ACT | 09/01/2020 &nbsp;ACT | 2022-06-27 | 2022-09-16 | A | https://dnr.wi.gov/cias/am/amexternal/AM_DownloadObject.aspx?id=1011796 | Natural gas-fired power plant |  | Natural Gas-Fired Combined-Cycle Turbine (P01) Start-up and Shutdown (Natural Gas) | 15.21 | Natural Gas | 0 |  | One Natural-Gas-Fired Siemens SGT6-8000H Combined-Cycle Turbine with Natural Gas-Fired Duct Burner and Diesel Fuel Oil Back-Up [Maximum continuous rating: 4,671 MMBtu/hr higher heating value (HHV) when combusting natural gas, 4,027 MMBtu/hr, HHV when combusting diesel fuel oil | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 335 | LB/START-UP |  | BACT-PSD |  | U | 0 | U | 59 | LB/SHUTDOWN |  | 0 |  |  | 0 | 0 | N |  | Total start-up and shutdown emissions: 108.3 T/YR. (based on 1525 hours per year for start-up and shutdown, combined, for natural gas operation)
WI-0300 | NEMADJI TRAIL ENERGY CENTER | NEMADJI TRAIL ENERGY CENTER | DOUGLAS | WI | 54880 | USA |  |  |  | 5 | WI001 | WISCONSIN DEPT OF NATURAL RESOURCES; AIR MGMT. PROGRAM | MS. KRISTIN HART | (608)266-6876 | kristin.hart@wisconsin.gov |  | 18-MMC-168 | 4911 | 221121 | Not Found | 06/30/2020 &nbsp;ACT | 09/01/2020 &nbsp;ACT | 2022-06-27 | 2022-09-16 | A | https://dnr.wi.gov/cias/am/amexternal/AM_DownloadObject.aspx?id=1011796 | Natural gas-fired power plant |  | Natural-Gas-Fired Combined-Cycle Turbine (P01) Start-Up and Shutdown (diesel) | 15.21 | Natural Gas | 0 |  | One Natural-Gas-Fired Siemens SGT6-8000H Combined-Cycle Turbine with Natural Gas-Fired Duct Burner and Diesel Fuel Oil Back-Up [Maximum continuous rating: 4,671 MMBtu/hr higher heating value (HHV) when combusting natural gas, 4,027 MMBtu/hr, HHV when combusting diesel fuel oil], | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 860 | LB/START-UP |  | BACT-PSD |  | U | 0 | U | 108 | LB/SHUTDOWN |  | 0 |  |  | 0 | 0 | N |  | Total start-up and shutdown emissions: 20.3 T/YR. (based on 42 start-ups and 42 shutdowns per year using diesel)
WI-0306 | WPL- RIVERSIDE ENERGY CENTER | WPL- RIVERSIDE ENERGY CENTER | ROCK | WI | 53511 | USA |  |  |  | 5 | WI001 | WISCONSIN DEPT OF NATURAL RESOURCES; AIR MGMT. PROGRAM | MS. KRISTIN HART | (608)266-6876 | kristin.hart@wisconsin.gov |  | 19-POY-212 | 4911 | 221112 | 110016895519 | 01/23/2020 &nbsp;ACT | 02/28/2020 &nbsp;ACT | 2022-07-14 | 2022-09-16 | D | https://dnr.wi.gov/cias/am/amexternal/AM_DownloadObject.aspx?id=941584 | Electric Power Generation |  | Natural Gas Fired Combustion Turbine (P20, P21) Phase II Commissioning | 15.21 | Natural Gas | 2208 | MMBTU/H | Natural gas fired combustion turbine with heat recovery steam generator (HRSG). Phase II commissioning is the period when synchronizing the turbine through SCR tuning after Phase I. Total fuel input (natural gas) to the turbines may not exceed 1,960 Million cubic feet for both turbines combined. Oxidation catalyst must run at all times during Phase II commissioning. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 55 | PPMVD, 15% OXYGEN | AVG. ANY 24-HR OPERATIONAL PERIOD | BACT-PSD |  | U | 0 | U | 476 | LB | IN ANY HOUR | 0 |  |  | 0 | 0 | N |  | Nitrogen oxide emissions may not exceed the limit from any turbine.
WI-0306 | WPL- RIVERSIDE ENERGY CENTER | WPL- RIVERSIDE ENERGY CENTER | ROCK | WI | 53511 | USA |  |  |  | 5 | WI001 | WISCONSIN DEPT OF NATURAL RESOURCES; AIR MGMT. PROGRAM | MS. KRISTIN HART | (608)266-6876 | kristin.hart@wisconsin.gov |  | 19-POY-212 | 4911 | 221112 | 110016895519 | 01/23/2020 &nbsp;ACT | 02/28/2020 &nbsp;ACT | 2022-07-14 | 2022-09-16 | D | https://dnr.wi.gov/cias/am/amexternal/AM_DownloadObject.aspx?id=941584 | Electric Power Generation |  | Natural Gas Fired Combustion Turbine (P20, P21)- Startup operation during Phase II Commissioning | 15.21 | Natural Gas | 2208 |  | Natural gas fired combustion turbine with heat recovery steam generator (HRSG). Phase II commissioning is the period when synchronizing the turbine through SCR tuning after Phase I. Startup is defined as the beginning of firing natural gas in the combustion turbine until the turbine/HRSG train reaches the minimum emissions compliance load, or the intended operating load if lower than the minimum emission compliance load. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 55 | PPMVD, 15% OXYGEN | AVG. ANY 24-HR OPERATIONAL PERIOD | BACT-PSD |  | U | 0 | U | 476 | LB | IN ANY HOUR | 0 |  |  | 0 | 0 | N
WI-0306 | WPL- RIVERSIDE ENERGY CENTER | WPL- RIVERSIDE ENERGY CENTER | ROCK | WI | 53511 | USA |  |  |  | 5 | WI001 | WISCONSIN DEPT OF NATURAL RESOURCES; AIR MGMT. PROGRAM | MS. KRISTIN HART | (608)266-6876 | kristin.hart@wisconsin.gov |  | 19-POY-212 | 4911 | 221112 | 110016895519 | 01/23/2020 &nbsp;ACT | 02/28/2020 &nbsp;ACT | 2022-07-14 | 2022-09-16 | D | https://dnr.wi.gov/cias/am/amexternal/AM_DownloadObject.aspx?id=941584 | Electric Power Generation |  | Natural Gas Fired Combustion Turbine (P20, P21) Phase I Commissioning | 15.21 | Natural Gas | 2208 | MMBTU/H | Natural gas fired combustion turbine with heat recovery steam generator (HRSG). Phase I commissioning is the period of initial cranking and steam blows when starting a turbine for the first time. Total fuel input (natural gas) to the turbines may not exceed 882 million cubic feet for both turbines combined and 1.20 million cubic feet in any hour for a single turbine. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 110 | PPMVD, 15% OXYGEN | AVG. ANY 24-HR OPERATIONAL PERIOD | BACT-PSD |  | U | 0 | U | 335.4 | LB | IN ANY HOUR | 0 |  |  | 0 | 0 | N
MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2019-02-19 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | FGCTGHRSG (EUCTGHRSG1 &amp; EUCTGHRSG2)--Startup &amp; Shutdown | 15.21 | Natural gas | 0 |  | This section is the startup and shutdown emission limits for FGCTGHRSG. Two 3,658 MMBTU/H natural gas-fired combustion turbine generators (CTGs) coupled with heat recovery steam generators (HRSGs). The HRSGs are equipped with natural gas-fired duct burners rated at 800 MMBTU/H to provide heat for additional steam production. The HRSGs are not capable of operating independently from the CTGs. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst technology and good combustion practices. | 791.5 | LB/H | EACH UNIT; OPERATING HOUR DURING S.S. | BACT-PSD |  | N | 85 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit is 791.5 LB/H, per operating hour during startup or shutdown. The limit applies to each unit. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in Special Condition III.2 in the permit.
VA-0332 | CHICKAHOMINY POWER LLC | CHICKAHOMINY POWER LLC | CHARLES CITY | VA | 23030 | USA | IRFAN ALI | (703) 226-0192 | IRFANKALI@BALICO.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer: Alison K. Sinclair Phone: (804)-527-5155 Email: Alison.Sinclair@deq.virginia.gov | 52610-1 | 4911 | 221112 | Not Found | 11/05/2018 &nbsp;ACT | 06/24/2019 &nbsp;ACT | 2019-08-07 | 2021-05-19 | A |  | Natural gas-fired combined cycle power plant, three 1 x1 configuration, 310 MW each, no duct firing, air cooled with two 84 MMBtu/H natural gas-fired auxiliary boilers, three fuel gas heaters, an emergency generator, fire water pump, and circuit breakers. | The proposed project will be a new combined-cycle electrical power generating facility utilizing three power blocks consisting of a combustion turbine with a heat recovery steam generator (HRSG) and a reheat condensing steam turbine generator (three 1 x 1 configuration). The turbine model proposed is a MHPS M501JAC turbine. The project will have a nominal net generating capacity of 1,650 MW. The proposed fuel for the turbines is pipeline-quality natural gas. Emissions from the turbines will be controlled by the use of low carbon fuels and high efficiency design (for GHG), clean fuels and GCPs (for PM, PM10 and PM2.5), SCR and dry low NOx burners (for NOx), and oxidation catalyst (for CO and VOC). Other equipment at the site, including two natural gas-fired auxiliary boilers, three fuel gas heaters, a diesel-fired emergency fire water pump, and a diesel-fired emergency generator, are also proposed and will be subject to emission controls. Natural gas piping components and electrical circuit breakers potentially emit GHG pollutants (expressed as carbon dioxide equivalents, or CO2e) and they will also be covered in the permit. This facility is not proposing duct firing in the HRSGs and is proposing air-cooled turbines that will not require cooling towers. | Three (3) Mitsubishi Hitachi Power Systems combustion turbine generators | 15.21 | natural gas | 35000 | MMCF/YR | One on one configuration: 4,066 MMBtu/H combustion turbine. Emission limits reflect the operation of each of the three turbines. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy efficient combustion practices and low GHG fuels | 812 | LB/CO2E/MW-H | 12 MO ROLLING TOTAL | BACT-PSD | NSPS , SIP | N | 0 | N | 6452 | BTU/KW-H NET HHV | INITIAL HEAR RATE TEST | 0 |  |  | 0 | 0 | N |  | Compliance with the lb/Mw-hr limit can be based on CO2 CEMs or calculations, monthly by summing the CO2e emissions and dividing by the electrical energy output. Compliance with the heat rate limit (Btu/kW-hr) is based on an initial heat rate test on power block. Additional, incremental heat rate values and emission limits apply during the life of the turbines. Annual CO2-e emission limits for each turbine are 2,123,519 tons/year.
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | GE Combustion Turbine - Startup and Shutdown | 15.21 | natural gas | 34000 | MMCF/YR | Startup and Shutdown | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practice | 840 | LB/TURBINE/EVENT | COLD START 60 MIN OR LESS | BACT-PSD | SIP | N | 0 | N | 188 | LB/TURBINE/EVENT | WARM START 50 MIN OR LESS | 0 |  |  | 0 | 0 | N |  | 180 lb/turbine/event hot start - 30 minutes or less 100 lb/turbine/event shutdown - 30 minutes or less These limits apply during startup and shutdown. CEMS required.
IL-0133 | LINCOLN LAND ENERGY CENTER | LINCOLN LAND ENERGY CENTER (A/K/A EMBERCLEAR) | SANGAMON | IL | 62558 | USA | JIM PALUMBO | 888-582-4460 X 55 | JPALUMBO@EMBERCLEAR.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov |  | 18040008 | 4911 | 221112 | Not Found | 09/30/2021 &nbsp;ACT | 07/29/2022 &nbsp;ACT | 2022-08-26 | 2022-12-06 | A | www2.illinois.gov/epa/public-notices/boa-notices/pages/archive.aspx | The proposed facility is designed to generate baseload power. It will consist of two combined-cycle generating units, with each a Siemens combustion turbine (3,647 mmBtu/hr) and a heat recovery steam generator (HRSG) with duct burners (35 mmBtu/hr); fired by natural gas only. Other units at the facility include an auxiliary boiler, engines, piping and piping components, circuit breakers and roadways. | Additional facility-wide pollutants, in tons/year: PM10/PM 2.5: 131.7 and 131.6 (respectively); sulfuric acid mist (SAM): 17.2; greenhouse gasses (GHG): 3,586,918 | Combined-Cycle Combustion Turbines | 15.21 | Natural Gas | 3647 | mmBtu/hour | Combined-cycle comustion turbines and heat recovery steam generators (HRSG) with a 35 mmBtu/hr duct burner. Turbine inlets would have evaporative cooling systems to cool the inlet air during warm weather to increase power output. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Inherently lower-polluting design, good combustion practices and operational energy efficiency | 850 | LB/MW-HR (GROSS) | 12 CONSECUTIVE OPERATING MONTHS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Compliance is based on quantification procedures of 40 CFR 98 Subpart D except where testing for nitrous oxide (N2O) and methane (CH4) are higher than in 40 CFR 98 Subpart D, emission factors based on these tests shall be used.
WI-0300 | NEMADJI TRAIL ENERGY CENTER | NEMADJI TRAIL ENERGY CENTER | DOUGLAS | WI | 54880 | USA |  |  |  | 5 | WI001 | WISCONSIN DEPT OF NATURAL RESOURCES; AIR MGMT. PROGRAM | MS. KRISTIN HART | (608)266-6876 | kristin.hart@wisconsin.gov |  | 18-MMC-168 | 4911 | 221121 | Not Found | 06/30/2020 &nbsp;ACT | 09/01/2020 &nbsp;ACT | 2022-06-27 | 2022-09-16 | A | https://dnr.wi.gov/cias/am/amexternal/AM_DownloadObject.aspx?id=1011796 | Natural gas-fired power plant |  | Natural-Gas-Fired Combined-Cycle Turbine (P01) | 15.21 | Natural Gas | 4671 | MMBTU/H | One Natural-Gas-Fired Siemens SGT6-8000 H Combined-Cycle Turbine with Natural Gas-Fired Duct Burner and Diesel Fuel Oil Back-Up [Maximum continuous rating: 4,671 MMBtu/hr higher heating value (HHV) when combusting natural gas, 4,027 MMBtu/hr, HHV when combusting diesel fuel oil], Selective Catalytic Reduction (SCR) (C01a) and Oxidation Catalyst (C01b) | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | B | Efficient turbine design, only combust pipeline quality natural gas and diesel fuel oil, Oxidation Catalyst | 850 | LB CO2/MW-H | 12-MO ROLLING AVG., NATURAL GAS | BACT-PSD |  | U | 90 | U | 1180 | LB CO2/MW-H | 12-MO ROLLING AVG, DIESEL | 0 |  |  | 0 | 0 | N |  | Shall be equipped with oxygen monitors as part of a continuous emissions monitoring (CEM) system.
WI-0306 | WPL- RIVERSIDE ENERGY CENTER | WPL- RIVERSIDE ENERGY CENTER | ROCK | WI | 53511 | USA |  |  |  | 5 | WI001 | WISCONSIN DEPT OF NATURAL RESOURCES; AIR MGMT. PROGRAM | MS. KRISTIN HART | (608)266-6876 | kristin.hart@wisconsin.gov |  | 19-POY-212 | 4911 | 221112 | 110016895519 | 01/23/2020 &nbsp;ACT | 02/28/2020 &nbsp;ACT | 2022-07-14 | 2022-09-16 | D | https://dnr.wi.gov/cias/am/amexternal/AM_DownloadObject.aspx?id=941584 | Electric Power Generation |  | Natural Gas Fired Combustion Turbine (P20, P21)- Startup operation during Phase I Commissioning | 15.21 | Natural Gas | 2208 | MMBTU/H | Two natural gas fired combustion turbine with heat recovery steam generator (HRSG). Phase I commissioning is the period of initial cranking and steam blows when starting a turbine for the first time. Startup is defined as the beginning of firing natural gas in the combustion turbine until the turbine/HRSG train reaches the minimum emissions compliance load, or the intended operating load if lower than the minimum emission compliance load. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 110 | PPMVD, 15% OXYGEN | AVG. ANY 24-HR OPERATIONAL PERIOD | BACT-PSD |  | U | 0 | U | 335.4 | LB | IN ANY HOUR | 0 |  |  | 0 | 0 | N
FL-0371 | SHADY HILLS COMBINED CYCLE FACILITY | SHADY HILLS ENERGY CENTER, LLC | PASCO | FL | 34610 | USA | ROY BELDEN |  | ROY.BELDEN@GE.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 1010524-003-AC (PSD-FL-444A) | 4911 | 221112 | 110012581820 | 04/02/2021 &nbsp;ACT | 06/07/2021 &nbsp;ACT | 2021-11-19 | 2022-03-04 | U | https://depedms.dep.state.fl.us:443/Oculus/servlet/shell?command=hitlist&[freeText=]&[folderName=]&[profile=Permitting_Authorization]&[creator=]&[entityType=any]&[createdDateTo=]&[catalog=75]&[searchBy=Profile]&[sortBy=Document Date]&[createdDate=]&{County=_EQ_PASCO}&{District=_EQ_SWD}&{Facility-Site ID=_EQ_AIR_1010524}&{Document Type=_EQ_PERMIT - FINAL}&{Facility Type=_LK_N/A}&{Application Number=_EQ_1010524003} | The Shady Hills Combined Cycle Facility (SHCCF), a new 573-megawatt (MW) (winter) 1-on-1 combined cycle electrical generating facility to be owned and operated by Shady Hills Energy Center, LLC, which will be located at 14350 Merchant Energy Way, Spring Hill, Florida. The proposed work will be conducted on an approximately 14-acre parcel east of and located adjacent to the existing Shady Hills Generating Station (SHGS) power plant, which is owned and operated by Shady Hills Power Company, L.L.C. |  | GE 7HA.02 Combustion Turbine and HRSG with Duct Firing | 15.21 | Natural Gas | 3622.1 | MMBtu/hour | Throughput based on a compressor inlet air temperature of 59Â° F, the higher heating value (HHV) of natural gas, and 100% load | Carbon Dioxide Equivalent (CO2e) | Other - CEMS or fuel-use monitoring | (Greenhouse Gasses (GHG)) | CO2e | P | Low-emitting fuel | 875 | LB/MWH | 12-MO ROLLING (PRIMARY BACT) | BACT-PSD | NSPS | U | 0 | U | 1000 | LB/MWH | 12-MO ROLLING (NSPS TTTT SECONDARY | 0 |  |  | 0 | 0 | N
LA-0391 | MAGNOLIA POWER GENERATING STATION UNIT 1 | MAGNOLIA POWER LLC | IBERVILLE | LA | 70764 | USA | WILLIAM DAVIS | 609-250-7707 | LEE.DAVIS@KINDLE-ENERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Ms. Lori Pittman, (225)219-3180 | PSD-LA-839 | 4911 | 221112 | Not Found | 09/08/2020 &nbsp;ACT | 06/03/2022 &nbsp;ACT | 2023-03-02 | 2023-05-23 | A | https://edms.deq.louisiana.gov/app/doc/view?doc=13323738 | Magnolia Power LLC (Magnolia Power) is proposing to construct and operate a power plant, Magnolia Power Generating Station Unit 1, consisting of a natural gas-fired combined cycle gas turbine (CCGT Unit) in Iberville Parish, Louisiana. The CCGT Unit (EQT001), which includes a heat recovery steam generator (HRSG) equipped with duct burners, will have a predicted net nominal output of 730 megawatts (MW) |  | Combined Cycle Gas Turbine w/ Duct Burners and HRSG | 15.21 | Natural Gas | 5081 | mm BTU/h | Normal operating rate is 4930 MMBTU/h. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Use of gaseous fuel (pipeline-quality natural gas), thermally efficient turbines, and good combustion practices. | 875 | LB/MW-H | ANNUAL AVERAGE | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | GE Combustion Turbine - Option 1 - Normal Operation | 15.21 | natural gas | 34000 | MMCF/YR | Option 1: Two on one configuration: 3,482 MMBtu/hr combustion turbine with 475 MMBtu/hr duct-fired HRSG. Emission limits reflect the operation of one turbine with or without duct firing. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy efficient combustion practices and low GHG fuels | 883 | LB CO2E/MW-H | 12 MO ROLLING TOTAL | BACT-PSD | NSPS , SIP | N | 0 | N | 6745 | BTU/KW-H NET HHV | INITIAL HEAT RATE TEST | 0 |  |  | 0 | 0 | N |  | Compliance with the lb/Mw-hr limit can be based on CO2 CEMs or calculations, monthly by summing the CO2e emissions and dividing by the electrical energy output. Complianc with the heat rate limit (Btu/kW-hr) is based on an initial heat rate test on power block.
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)718-9967 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | Siemens Combusion Turbine - Option 2 - Normal Operation | 15.21 | Natural Gas | 35000 | MMCF/YR | Option 2: Two on one configuration: 3,116 MMBtu/hr combustion turbine with 991 MMBtu/hr duct-fired HRSG. Emission limits reflect the operation of one turbine with or without duct firing. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy efficient combustion practices and low GHG fuels | 883 | LB CO2E/MW H | 12 MO ROLLING TOTAL | BACT-PSD | NSPS , SIP | N | 0 | N | 6625 | BTU/KW H NET HHV | INITIAL HEAT RATE TEST | 0 |  |  | 0 | 0 | N |  | Compliance with the LB/MW H limit can be based on CO2 CEMS or calculations, monthly by summing the CO2e emissions & dividing the electrical energy output. Compliance with the heat rate limit (BTU/KW H) is based on an initial heat rate test on power block.
TX-0834 | MONTGOMERY COUNTY POWER STATIOIN | ENTERGY TEXAS INC | MONTGOMERY | TX |  | USA | CHRISTOPHER BURKE | 281-297-3369 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., 512-239-2175 laura.gibson@tceq.texas.gov | N256, PSDTX1510, AND GHGPSDTX1 | 4911 | 221112 | Not Found | 01/18/2018 &nbsp;ACT | 03/30/2018 &nbsp;ACT | 2018-04-26 | 2019-02-19 | A |  |  |  | Combined Cycle Turbine | 15.21 | NATURAL GAS | 2635 | MMBTU/HR/UNIT | Two Mitsubishi M501GAC turbines (without fast start) | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | PIPELINE QUALITY NATURAL GAS, GOOD COMBUSTION PRACTICES | 884 | LB/MWH |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK & TTTT, MACT YYYY
WI-0300 | NEMADJI TRAIL ENERGY CENTER | NEMADJI TRAIL ENERGY CENTER | DOUGLAS | WI | 54880 | USA |  |  |  | 5 | WI001 | WISCONSIN DEPT OF NATURAL RESOURCES; AIR MGMT. PROGRAM | MS. KRISTIN HART | (608)266-6876 | kristin.hart@wisconsin.gov |  | 18-MMC-168 | 4911 | 221121 | Not Found | 06/30/2020 &nbsp;ACT | 09/01/2020 &nbsp;ACT | 2022-06-27 | 2022-09-16 | A | https://dnr.wi.gov/cias/am/amexternal/AM_DownloadObject.aspx?id=1011796 | Natural gas-fired power plant |  | Natural Gas-Fired Combined-Cycle Turbine (P01) Start-up and Shutdown (Natural Gas) | 15.21 | Natural Gas | 0 |  | One Natural-Gas-Fired Siemens SGT6-8000H Combined-Cycle Turbine with Natural Gas-Fired Duct Burner and Diesel Fuel Oil Back-Up [Maximum continuous rating: 4,671 MMBtu/hr higher heating value (HHV) when combusting natural gas, 4,027 MMBtu/hr, HHV when combusting diesel fuel oil | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 950 | LB/START-UP |  | BACT-PSD |  | U | 0 | U | 40 | LB/SHUTDOWN |  | 0 |  |  | 0 | 0 | N |  | Total start-up and shutdown emissions: 117.8 T/YR. (based on 1525 hours per year for start-up and shutdown, combined, for natural gas operation)
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | General Electric (GE) Combustion Turbines (P005 &amp; P006) | 15.21 | Natural gas | 3459.6 | MMBTU/H | Two identical GE Combustion Turbines 1 and 2; GE model 7HA.02 natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,459.6 MMBtu/hr (HHV) at 100% load and -2Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 570.45 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate additional electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Carbon Dioxide Equivalent (CO2e) | Other - Method 3A for CO2 | (Greenhouse Gasses (GHG)) | CO2e | P | High efficient combustion technology | 1000 | LB/MW-H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD | NSPS | U | 0 | U | 1012.4 | LB/MW-H | WITHOUT DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | With duct burners: 450 kg per MW-h of gross energy output (1,000 lbs/MW-h) on a 12-operating-month rolling average basis, or, if a petition is granted, CO2 emissions shall not exceed 470 kg per MW-h of net energy output (1,030 lbs/MW-h) on a 12-operating-month rolling average basis. [40 CFR 60.5520(a)-(c) and Table 2 of 40 CFR Part 60, Subpart TTTT] Without duct burners: 1,012.4 lbs/MW-hr gross energy output at full load ISO conditions when firing natural gas. Gross energy output is defined as the gross power output of the generators before accounting for any balance of plant loads. 2,499,820 t/yr of CO2e emissions per rolling, 12-month period.
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | Mitsubishi Hitachi Power Systems (MHPS) Combustion Turbines (P007 &amp; P008) | 15.21 | Natural gas | 3231 | MMBTU/H | Two identical MHPS Combustion Turbines 1 and 2; Mitsubishi Model M501JAC natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,231 MMBtu/hr (HHV) at 100% load and 51Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 306 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Carbon Dioxide Equivalent (CO2e) | Other - Method 3A for CO2 | (Greenhouse Gasses (GHG)) | CO2e | P | High efficient combustion technology | 1000 | LB/MW-H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD | NSPS | U | 0 | U | 976 | LB/MW-H | WITHOUT DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | With duct burners: 450 kg per MW-h of gross energy output (1,000 lbs/MW-h) on a 12-operating-month rolling average basis, or, if a petition is granted, CO2 emissions shall not exceed 470 kg per MW-h of net energy output (1,030 lbs/MW-h) on a 12-operating-month rolling average basis. [40 CFR 60.5520(a)-(c) and Table 2 of 40 CFR Part 60, Subpart TTTT] Without duct burners: 976.0 lbs/MW-hr gross energy output at full load ISO conditions when firing natural gas. Gross energy output is defined as the gross power output of the generators before accounting for any balance of plant loads. 2,342,643 tons of CO2e emissions per rolling, 12-month period.
MI-0432 | NEW COVERT GENERATING FACILITY | NEW COVERT GENERATING COMPANY, LLC | VAN BUREN | MI | 49043 | USA | JOHN REESE | 212-792-0897 | JREESE@EASTERNGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 186-17 | 4911 | 221112 | Not Found | 04/17/2018 &nbsp;ACT | 07/30/2018 &nbsp;ACT | 2018-08-13 | 2019-02-19 | C |  | Power plant | The equipment consists of three advanced firing temperature Mitsubishi 501G combustion turbines, three heat recovery steam generators supplemented with gas-fired duct burners each with a max firing rate of 256 million British thermal units per hour (MMBtu/hr), three steam turbine generators. Auxiliary equipment includes three mechanical draft evaporative cooling towers, one natural gas auxiliary boiler, one diesel emergency generator, one diesel fire water pump, one aqueous parts cleaner, and one gas heater. | FG-TURB/DB1-3--Startup/Shutdown Operations | 15.21 | Natural gas | 1230 | MW | Three (3) combined-cycle combustion turbine (CT) / heat recovery steam generator (HRSG) trains. Each CT is a natural gas fired Mitsubishi model 501G, equipped with dry low NOx combustor and inlet air evaporative cooling. Each HRSG includes a natural gas fired duct burner with a 256 MMBTU/Hr heat input capacity and a dry low NOx burner. This scenario identifies the emission limits applicable during startup and shutdown operations. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst technology and good combustion practices. | 1164 | LB/H | EACH CT/HRSG TRAIN; STARTUP/SHUTDOWN | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emission limit 1 above is 1164 lb/hr each operating hour during startup or shutdown for each individual CT/HRSG train in the flexible group. Startup is defined as the period of time from detection of a flame signal until the unit reaches steady state operation (i.e. loads greater than 50 percent). Shutdown is defined as beginning when the turbine output is lowered to the point that steady state operation can no longer be assured (i.e. loads less than 50 percent), and ending when a flame-off signal is detected.
LA-0391 | MAGNOLIA POWER GENERATING STATION UNIT 1 | MAGNOLIA POWER LLC | IBERVILLE | LA | 70764 | USA | WILLIAM DAVIS | 609-250-7707 | LEE.DAVIS@KINDLE-ENERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Ms. Lori Pittman, (225)219-3180 | PSD-LA-839 | 4911 | 221112 | Not Found | 09/08/2020 &nbsp;ACT | 06/03/2022 &nbsp;ACT | 2023-03-02 | 2023-05-23 | A | https://edms.deq.louisiana.gov/app/doc/view?doc=13323738 | Magnolia Power LLC (Magnolia Power) is proposing to construct and operate a power plant, Magnolia Power Generating Station Unit 1, consisting of a natural gas-fired combined cycle gas turbine (CCGT Unit) in Iberville Parish, Louisiana. The CCGT Unit (EQT001), which includes a heat recovery steam generator (HRSG) equipped with duct burners, will have a predicted net nominal output of 730 megawatts (MW) |  | Combined Cycle Gas Turbine Startup and Shutdown | 15.21 | Natural Gas | 5081 | mm BTU/h | Startup and shutdown emissions from the combined cycle gas turbine. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices. | 1620 | LB/HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
WI-0306 | WPL- RIVERSIDE ENERGY CENTER | WPL- RIVERSIDE ENERGY CENTER | ROCK | WI | 53511 | USA |  |  |  | 5 | WI001 | WISCONSIN DEPT OF NATURAL RESOURCES; AIR MGMT. PROGRAM | MS. KRISTIN HART | (608)266-6876 | kristin.hart@wisconsin.gov |  | 19-POY-212 | 4911 | 221112 | 110016895519 | 01/23/2020 &nbsp;ACT | 02/28/2020 &nbsp;ACT | 2022-07-14 | 2022-09-16 | D | https://dnr.wi.gov/cias/am/amexternal/AM_DownloadObject.aspx?id=941584 | Electric Power Generation |  | Natural Gas Fired Combustion Turbine (P20, P21) Phase I Commissioning | 15.21 | Natural Gas | 2208 | MMBTU/H | Natural gas fired combustion turbine with heat recovery steam generator (HRSG). Phase I commissioning is the period of initial cranking and steam blows when starting a turbine for the first time. Total fuel input (natural gas) to the turbines may not exceed 882 million cubic feet for both turbines combined and 1.20 million cubic feet in any hour for a single turbine. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N |  | 1750 | PPMVD, 15% OXYGEN | AVG. ANY 24-HR OPERATIONAL | BACT-PSD |  | U | 0 | U | 3203 | LB | IN ANY HOUR | 0 |  |  | 0 | 0 | N
*TN-0164 | TVA - JOHNSONVILLE COGENERATION | TENNESSEE VALLEY AUTHORITY | HUMPHREYS | TN | 37134 | USA | JACK BYARS | (423) 751-2666 | JGBYARS@TVA.GOV | 4 | TN001 | TENN.DEPT. OF ENVIRONMENT & CONSERVATION, DIV OF AIR POLLUTION CONTROL | LACEY HARDIN | (615) 532-0545 | Lacey.Hardin@tn.gov |  | 972969 | 4911 | 221112 | 110070502905 | 09/26/2017 &nbsp;ACT | 02/01/2018 &nbsp;ACT | 2019-03-21 | 2019-03-21 | D |  | Combustion turbines and combined cycle plant | Permit 972969 adds startup and shutdown limits to the requirements established in PSD permit 970816F. | Dual-fuel CT and HRSG with duct burner | 15.21 | Natural Gas | 1020 | MMBtu/hr | Rated input capacity is 1020 MMBtu/hr (CT) and 319 MMBtu/hr (duct burner) when burning natural gas and 1084 MMBtu/hr when burning #2 oil. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion design & practices | 1800 | LB/MWH | 12-MONTH MOVING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
WI-0300 | NEMADJI TRAIL ENERGY CENTER | NEMADJI TRAIL ENERGY CENTER | DOUGLAS | WI | 54880 | USA |  |  |  | 5 | WI001 | WISCONSIN DEPT OF NATURAL RESOURCES; AIR MGMT. PROGRAM | MS. KRISTIN HART | (608)266-6876 | kristin.hart@wisconsin.gov |  | 18-MMC-168 | 4911 | 221121 | Not Found | 06/30/2020 &nbsp;ACT | 09/01/2020 &nbsp;ACT | 2022-06-27 | 2022-09-16 | A | https://dnr.wi.gov/cias/am/amexternal/AM_DownloadObject.aspx?id=1011796 | Natural gas-fired power plant |  | Natural-Gas-Fired Combined-Cycle Turbine (P01) Start-Up and Shutdown (diesel) | 15.21 | Natural Gas | 0 |  | One Natural-Gas-Fired Siemens SGT6-8000H Combined-Cycle Turbine with Natural Gas-Fired Duct Burner and Diesel Fuel Oil Back-Up [Maximum continuous rating: 4,671 MMBtu/hr higher heating value (HHV) when combusting natural gas, 4,027 MMBtu/hr, HHV when combusting diesel fuel oil], | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 2951 | LB/START-UP |  | BACT-PSD |  | U | 0 | U | 122 | LB/SHUTDOWN |  | 0 |  |  | 0 | 0 | N |  | Total start-up and shutdown emissions: 64.5 T/YR. (based on 42 start-ups and 42 shutdowns per year using diesel)
TX-0834 | MONTGOMERY COUNTY POWER STATIOIN | ENTERGY TEXAS INC | MONTGOMERY | TX |  | USA | CHRISTOPHER BURKE | 281-297-3369 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., 512-239-2175 laura.gibson@tceq.texas.gov | N256, PSDTX1510, AND GHGPSDTX1 | 4911 | 221112 | Not Found | 01/18/2018 &nbsp;ACT | 03/30/2018 &nbsp;ACT | 2018-04-26 | 2019-02-19 | A |  |  |  | COMBINED CYCLE TURBINE MSS REDUCED LOAD | 15.21 | NATURAL GAS | 0 |  | 9 HOURS STARTUP, 1 HOUR SHUTDOWN | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | minimizing duration of startup / shutdown events, engaging the pollution control equipment as soon as practicable (based on vendor recommendations and guarantees), and meeting the emissions limits on the MAERT | 8000 | LB/H |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK & TTTT, MACT YYYY
WI-0300 | NEMADJI TRAIL ENERGY CENTER | NEMADJI TRAIL ENERGY CENTER | DOUGLAS | WI | 54880 | USA |  |  |  | 5 | WI001 | WISCONSIN DEPT OF NATURAL RESOURCES; AIR MGMT. PROGRAM | MS. KRISTIN HART | (608)266-6876 | kristin.hart@wisconsin.gov |  | 18-MMC-168 | 4911 | 221121 | Not Found | 06/30/2020 &nbsp;ACT | 09/01/2020 &nbsp;ACT | 2022-06-27 | 2022-09-16 | A | https://dnr.wi.gov/cias/am/amexternal/AM_DownloadObject.aspx?id=1011796 | Natural gas-fired power plant |  | Natural Gas-Fired Combined-Cycle Turbine (P01) Start-up and Shutdown (Natural Gas) | 15.21 | Natural Gas | 0 |  | One Natural-Gas-Fired Siemens SGT6-8000H Combined-Cycle Turbine with Natural Gas-Fired Duct Burner and Diesel Fuel Oil Back-Up [Maximum continuous rating: 4,671 MMBtu/hr higher heating value (HHV) when combusting natural gas, 4,027 MMBtu/hr, HHV when combusting diesel fuel oil | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N |  | 11066 | LB/START-UP |  | BACT-PSD |  | U | 0 | U | 463 | LB/SHUTDOWN |  | 0 |  |  | 0 | 0 | N |  | Total start-up and shutdown emissions: 1369 T/YR. (based on 1525 hours per year for start-up and shutdown, combined, for natural gas operation)
WI-0300 | NEMADJI TRAIL ENERGY CENTER | NEMADJI TRAIL ENERGY CENTER | DOUGLAS | WI | 54880 | USA |  |  |  | 5 | WI001 | WISCONSIN DEPT OF NATURAL RESOURCES; AIR MGMT. PROGRAM | MS. KRISTIN HART | (608)266-6876 | kristin.hart@wisconsin.gov |  | 18-MMC-168 | 4911 | 221121 | Not Found | 06/30/2020 &nbsp;ACT | 09/01/2020 &nbsp;ACT | 2022-06-27 | 2022-09-16 | A | https://dnr.wi.gov/cias/am/amexternal/AM_DownloadObject.aspx?id=1011796 | Natural gas-fired power plant |  | Natural-Gas-Fired Combined-Cycle Turbine (P01) Start-Up and Shutdown (diesel) | 15.21 | Natural Gas | 0 |  | One Natural-Gas-Fired Siemens SGT6-8000H Combined-Cycle Turbine with Natural Gas-Fired Duct Burner and Diesel Fuel Oil Back-Up [Maximum continuous rating: 4,671 MMBtu/hr higher heating value (HHV) when combusting natural gas, 4,027 MMBtu/hr, HHV when combusting diesel fuel oil], | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N |  | 25846 | LB/START-UP |  | BACT-PSD |  | U | 0 | U | 1227 | LB/SHUTDOWN |  | 0 |  |  | 0 | 0 | N |  | Total start-up and shutdown emissions: 569 T/YR. (based on 42 start-ups and 42 shutdowns per year using diesel)
*WV-0032 | BROOKE COUNTY POWER PLANT | ESC BROOKE COUNTY POWER I, LLC | BROOKE | WV | 26035 | USA | ANDREW DORN | 7163121042 | DREW.DORN@ENSOLCONSORTIUM.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Engineer: Mr. Steve Pursley 304-926-0499 x1218 Steven.R.Pursley@wv.gov | R14-0035 | 4911 | 221112 | Not Found | 03/30/2018 &nbsp;ACT | 09/18/2018 &nbsp;ACT | 2018-12-20 | 2022-06-28 | A |  | Nominal 925 mWe natural gas-fired combined-cycle power plant. Small sources: Emergency Generator, Fire Water Pump, Fuel Gas Heater not included in RBLC - may request info or see permit for details. |  | GE 7HA.01 Turbine | 15.21 | Natural Gas/Ethane | 2737.7 | mmBtu/hr | Facility has 2 identical units, only 1 entry in RBLC. Nominal 462.5 mWe. All emission limits steady-state and include 424 mmBtu/hr Duct Burner in operation. Short Term startup and shutdown limits in lb/event given in permit. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Use of Natural Gas, Model GE7HA | 417382 | LB/HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 829 | LB/MW-HR |  | 0 | 0 | N
MI-0441 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, for technical questions regarding this permit. She may be reached at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 74-18 | 4911 | 221112 | 110040958425 | 10/16/2018 &nbsp;ACT | 12/21/2018 &nbsp;ACT | 2019-10-18 | 2021-08-09 | D |  | Natural gas combined-cycle power plant. | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG2--A 667 MMBTU/H natural gas fired CTG with a HRSG. | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG2 is a nominally rated 667 MMBTU/H natural gas fired CTG coupled with a HRSG. The HRSG is equipped with a natural gas fired duct burner rated at 204 MMBTU/h to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a DLNB, SCR and oxidation catalyst. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | low carbon fuel (pipeline quality natural gas), good combustion practices and energy efficiency measures. | 430349 | T/YR | 12-MO ROLLING TIME PERIOD | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Carbon capture and sequestration (CCS) would not be economically feasible based upon a qualitative assessment based upon the CTG/HRSG train analysis.
MI-0441 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, for technical questions regarding this permit. She may be reached at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 74-18 | 4911 | 221112 | 110040958425 | 10/16/2018 &nbsp;ACT | 12/21/2018 &nbsp;ACT | 2019-10-18 | 2021-08-09 | D |  | Natural gas combined-cycle power plant. | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG1--A 667 MMBTU/H NG fired combustion turbine generator coupled with a heat recovery steam generator (HRSG) | 15.21 | Natural gas | 667 | MMBTU/H | A nominally rated 667 MMBTU/hr natural gas-fired combustion turbine generator (CTG) coupled with a heat recovery steam generator (HRSG). The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBTU/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a dry low NOx burner (DLNB), selective catalytic reduction (SCR) and oxidation catalyst. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Low carbon fuel (pipeline quality natural gas), good combustion practices and energy efficiency measures. | 430349 | T/YR | 12-MO ROLLING TIME PERIOD | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit applies during all operating modes. Carbon capture and sequestration (CCS) would not be economically feasible based upon a qualitative assessment based upon the CTG/HRSG train analysis.
MI-0447 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-648-6339 or at ByrnesM@michigan.gov for technical questions related to this permit. Thank you. | 74-18A | 4911 | 221112 | 110040958425 | 09/22/2020 &nbsp;ACT | 01/07/2021 &nbsp;ACT | 2021-06-28 | 2021-09-10 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG1 | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG1--A nominally rated 667 MMBTU/hr natural gas-fired combustion turbine generator (CTG) coupled with a heat recovery steam generator (HRSG). The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBTU/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a dry low NOx burner (DLNB), selective catalytic reduction (SCR), and oxidation catalyst. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Low carbon fuel (pipeline quality natural gas), good combustion practices, and energy efficiency measures. | 430349 | T/YR | 12-MO ROLLING TIME PERIOD | BACT-PSD | NSPS | N | 0 | U | 1000 | LB/MW-H | 12 OPERAT.MO ROLL AVG. | 0 |  |  | 0 | 0 | N |  | Emission limit 1 (above) = 430,349 tons/year based on a 12-month rolling time period as determined at the end of each calendar month. Applies during all operating modes. Emission limit 2 (above) = 1,000 lb/MW-h gross energy output based on 12-operating month rolling average as determined at the end of each calendar month. Applies during all operating modes. Carbon capture and sequestration (CCS) would not be economically feasible based upon a qualitative assessment based upon the CTG/HRSG train analysis.
MI-0447 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-648-6339 or at ByrnesM@michigan.gov for technical questions related to this permit. Thank you. | 74-18A | 4911 | 221112 | 110040958425 | 09/22/2020 &nbsp;ACT | 01/07/2021 &nbsp;ACT | 2021-06-28 | 2021-09-10 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG2 | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG2--A nominally rated 667 MMBTU/hr natural gas-fired CTG coupled with a HRSG. The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBTU/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a DLNB, SCR, and oxidation catalyst. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Low carbon fuel (pipeline quality natural gas), good combustion practices, and energy efficiency measures. | 430349 | T/YR | 12-MO ROLLING TIME PERIOD | BACT-PSD | NSPS | N | 0 | U | 1000 | LB/MW-H | 12-OPERATING MO ROLL AVG | 0 |  |  | 0 | 0 | N |  | Emission limit 1 (above) = 430,349 tons/year based on a 12-month rolling time period as determined at the end of each calendar month. Applies during all operating modes. Emission limit (above) = 1,000 lb/MW-hour gross energy output; based on a 12-operating month rolling average, as determined at the end of each calendar month. Applies during all operating modes. Carbon capture and sequestration (CCS) would not be economically feasible based upon a qualitative assessment based upon the CTG/HRSG train analysis.
MI-0454 | LBWL-ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions about this permit, please contact the permit engineer, Lauren Magirl, at 517-582-5345, or at MagirlL@michigan.gov. Thank you. | 74-18D | 4911 | 221112 | Not Found | 10/25/2022 &nbsp;ACT | 12/20/2022 &nbsp;ACT | 2022-12-29 | 2023-05-23 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWLâ€™s existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG1 | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG1- A nominally rated 667 MMBtu/hr natural gas-fired combustion turbine generator (CTG) coupled with a heat recovery steam generator (HRSG). The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBtu/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a dry low NOx burner (DLNB), selective catalytic reduction (SCR), and oxidation catalyst. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | low carbon fuel (pipeline quality natural gas), good combustion practices, and energy efficiency measures. | 430349 | T/YR | 12-MO ROLLING TIME PERIOD; DUR. ALL MODE | BACT-PSD | NSPS | N | 0 | N | 1000 | LB/MWH | 12 OPERATING MONTH ROLLING AVG | 0 |  |  | 0 | 0 | N |  | Emission limit 1 above = 430,349 tons/yr based on a 12-month rolling time period as determined at the end of each calendar month. Applies during all operating modes. Emission limit 2 above = 1000 lb/MWh gross energy output on a 12-operating month rolling average, as determined at the end of each calendar month. Applies during all operating modes. Carbon capture and sequestration (CCS) would not be economically feasible based upon a qualitative assessment based upon the CTG/HRSG train analysis.
MI-0454 | LBWL-ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions about this permit, please contact the permit engineer, Lauren Magirl, at 517-582-5345, or at MagirlL@michigan.gov. Thank you. | 74-18D | 4911 | 221112 | Not Found | 10/25/2022 &nbsp;ACT | 12/20/2022 &nbsp;ACT | 2022-12-29 | 2023-05-23 | D |  | Natural gas combined-cycle power plant | The proposed new plant will be replacing the electrical generating capacity of both BWLâ€™s existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG2 | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG2- A nominally rated 667 MMBtu/hr natural gas-fired CTG coupled with a HRSG. The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBtu/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a DLNB, SCR, and oxidation catalyst. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Low carbon fuel (pipeline quality natural gas), good combustion practices, and energy efficiency measures. | 430349 | T/YR | 12-MO ROLLING TIME PERIOD | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emission limit 1 = 430,349 tons/year based on a 12-month rolling time period as determined at the end of each calendar month. Applies during all operating modes. Carbon capture and sequestration (CCS) would not be economically feasible based upon a qualitative assessment based upon the CTG/HRSG train analysis.
TX-0878 | LNG EXPORT TERMINAL | PORT ARTHUR LNG, LLC | JEFFERSON | TX |  | USA | J.D. MORRIS | 713-298-5476 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Benjamin Hansen, Ph.D., P.E., (512) 239-4578, Benjamin.Hansen@tceq.texas.gov | 158420, PSDTX1572, GHGPSDTX198 | 4922 | 486210 | Not FOUND | 05/27/2020 &nbsp;ACT | 09/15/2022 &nbsp;ACT | 2019-11-07 | 2023-05-23 | A |  | Liquefied natural gas (LNG) export terminal. |  | Refrigeration Compression Turbines | 15.21 | NATURAL GAS | 26.92 | MMTON/Y | Eight GE Frame 7E gas turbines for refrigeration and compression at the site. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Equipment specifications & work practices - Good combustion practices and use of low carbon fuel | 504000 | TON/Y |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*WV-0029 | HARRISON COUNTY POWER PLANT | ESC HARRISON COUNTY POWER, LLC | HARRISON | WV | 26301 | USA | ANDREW DORN | 7163121042 | DREWDORN@ENSOLCONSORTIUM.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Engineer: Mr. Steve Pursley 304-926-0499 x1218 steven.r.pursley@wv.gov | R14-0036 | 4911 | 221112 | Not Found | 04/26/2017 &nbsp;ACT | 03/27/2018 &nbsp;ACT | 2018-06-25 | 2022-06-28 | A | https://dep.wv.gov/daq/Documents/March 2018 Permits and Evals/033-00264_PERM_R14-0036.pdf | Nominal 640 mWe natural gas-fired combined-cycle power plant. Small sources: Emergency Generator, Fire Water Pump, Fuel Gas Heater not included in RBLC - may request info or see permit for details. |  | GE 7HA.02 Turbine | 15.21 | Natural Gas | 3496.2 | mmBtu/hr | Nominal 640 mWe All emission limits steady-state and include 1000 mmBtu/hr Duct Burner in operation Short Term startup and shutdown limits in lb/event given in permit. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Use of Natural Gas, Model GE7HA | 528543 | LB/HR |  | BACT-PSD | NSPS | U | 0 | U | 2315020 | TONS/YEAR |  | 826 | LB/MW-HR |  | 0 | 0 | N
WI-0300 | NEMADJI TRAIL ENERGY CENTER | NEMADJI TRAIL ENERGY CENTER | DOUGLAS | WI | 54880 | USA |  |  |  | 5 | WI001 | WISCONSIN DEPT OF NATURAL RESOURCES; AIR MGMT. PROGRAM | MS. KRISTIN HART | (608)266-6876 | kristin.hart@wisconsin.gov |  | 18-MMC-168 | 4911 | 221121 | Not Found | 06/30/2020 &nbsp;ACT | 09/01/2020 &nbsp;ACT | 2022-06-27 | 2022-09-16 | A | https://dnr.wi.gov/cias/am/amexternal/AM_DownloadObject.aspx?id=1011796 | Natural gas-fired power plant |  | Natural Gas-Fired Combined-Cycle Turbine (P01) Start-up and Shutdown (Natural Gas) | 15.21 | Natural Gas | 0 |  | One Natural-Gas-Fired Siemens SGT6-8000H Combined-Cycle Turbine with Natural Gas-Fired Duct Burner and Diesel Fuel Oil Back-Up [Maximum continuous rating: 4,671 MMBtu/hr higher heating value (HHV) when combusting natural gas, 4,027 MMBtu/hr, HHV when combusting diesel fuel oil | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 939573 | LB/START-UP |  | BACT-PSD |  | U | 0 | U | 234893 | LB/SHUTDOWN |  | 0 |  |  | 0 | 0 | N |  | Total start-up and shutdown emissions: 358,212 T/YR. (based on 1525 hours per year for start-up and shutdown, combined, for natural gas operation)
MI-0439 | JACKSON GENERATING STATION | CONSUMERS ENERGY COMPANY | JACKSON | MI | 49203-2174 | USA | BRIAN LABBY | 989-667-5008 | BRIAN.LABBY@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, at 517-284-6790 or at byrnesm@michigan.gov, for technical questions regarding this permit. Thank you. | 118-18 | 4911 | 221112 | 110015804511 | 11/29/2018 &nbsp;ACT | 04/02/2019 &nbsp;ACT | 2019-05-20 | 2019-06-19 | C |  | Natural gas combined-cycle power plant |  | FGLMDB1-6 (6 combined cycle natural gas fired CTG each equipped with a HRSG) | 15.21 | natural gas | 420 | MW | FGLMDB1-6 is 6 combined cycle natural gas fired combustion turbine generators (CTG) each equipped with a heat recovery steam generator (HRSG). Nominal rating 420 MW. Each combustion turbine (CT) is a GE LM6000 with a rating of 440 MMBTU/HR (HHV) and a duct burner rating of 222 MMBTU/HR (HHV). A combined cycle natural gas fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 420 MW electricity production. The HRSG is not capable of operating independently from the CTG. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Use of low carbon fuel (natural gas), good combustion practices, and energy efficiency measures. | 1000257 | T/YR | 12-MONTH ROLLING TIME PERIOD | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Energy efficiency measures involve the installation of combined cycle units, following vendor recommended maintenance practices, the minimization of heat loss, and automated instrumentation and controls for efficient combustion. Emission limit = 1,000,257 tons/yr applied to all stacks combined on a 12-month rolling time period basis. This limit applies during periods of startup and shutdown.
LA-0364 | FG LA COMPLEX | FG LA LLC | ST. JAMES | LA | 70086 | USA | KUAN-MING PEMG | 2813026850 | KMPEMG@FPCC.COM.TW | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mr. Anthony Randall, (225)219-3180 | PSD-LA-812 | 2869 | 325110 | Not Found | 01/14/2019 &nbsp;ACT | 01/06/2020 &nbsp;ACT | 2020-05-05 | 2021-08-09 | A | https://edms.deq.louisiana.gov/app/doc/view.aspx?doc=11998450&ob=yes&child=yes | The FG LA complex will produce ethylene, propylene, ethylene glycol, high density polyethylene, low density polyethylene, linear low-density polyethylene and polypropylene. To support the operation of these production plants, the complex will also include electric power and steam generating units (Utility), wastewater treatment (Central Wastewater Treatment Plant), storage and loading operations (Logistics), and associated flare systems. | FG LA was issued PSD-LA-812 to construct the FG LA Complex which involves the construction of fourteen facilities permitted under fourteen Title V Permits to manufacture ethylene and propylene, ultimately producing high and low density polyethylene, propylene, and ethylene glycol. | Cogeneration Units | 15.21 | Natural Gas | 2222 | mm btu/h | Throughput is maximum operating rate. 2139 MM BTU/hr normal operating rate. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Use of natural gas as fuel, energy-efficient design options, and operational/maintenance practices. | 1096666 | TONS/YR |  | BACT-PSD | NSPS , NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0432 | NEW COVERT GENERATING FACILITY | NEW COVERT GENERATING COMPANY, LLC | VAN BUREN | MI | 49043 | USA | JOHN REESE | 212-792-0897 | JREESE@EASTERNGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 186-17 | 4911 | 221112 | Not Found | 04/17/2018 &nbsp;ACT | 07/30/2018 &nbsp;ACT | 2018-08-13 | 2019-02-19 | C |  | Power plant | The equipment consists of three advanced firing temperature Mitsubishi 501G combustion turbines, three heat recovery steam generators supplemented with gas-fired duct burners each with a max firing rate of 256 million British thermal units per hour (MMBtu/hr), three steam turbine generators. Auxiliary equipment includes three mechanical draft evaporative cooling towers, one natural gas auxiliary boiler, one diesel emergency generator, one diesel fire water pump, one aqueous parts cleaner, and one gas heater. | FG-TURB/DB1-3 (3 combined cycle combustion turbine and heat recovery steam generator trains) | 15.21 | Natural gas | 1230 | MW | Three (3) combined-cycle combustion turbine (CT) / heat recovery steam generator (HRSG) trains. Each CT is a natural gas fired Mitsubishi model 501G, equipped with dry low NOx combustor and inlet air evaporative cooling. Each HRSG includes a natural gas fired duct burner with a 256 MMBtu/hr heat input capacity and a dry low NOx burner. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Several energy efficiency measures and the use of natural gas. | 1425081 | T/YR | EACH CT/HRSG TRAIN; 12-MO. ROLL TIME PER | BACT-PSD |  | N | 0 | N | 7978 | BTU/KW-H | EACH CT/HRSG TRAIN; 12-MO ROLL AVG | 0 |  |  | 0 | 0 | N |  | Emission limit 1 above is 1,425,081 T/YR based on a 12-month rolling time period as determined at the end of each calendar month for each individual CT/HRSG. Emission limit 2 above is 7,978 BTU/KW-H (HHV) and is the Net Heat Rate on a 12-month rolling average basis for each individual CT/HRSG. CCS was estimated to cost over $75 per ton of CO2 removed, with an estimated annual cost of over $321 million to remove 4.24 million tons per year. Thus, this option was ruled out as economically infeasible.
WI-0300 | NEMADJI TRAIL ENERGY CENTER | NEMADJI TRAIL ENERGY CENTER | DOUGLAS | WI | 54880 | USA |  |  |  | 5 | WI001 | WISCONSIN DEPT OF NATURAL RESOURCES; AIR MGMT. PROGRAM | MS. KRISTIN HART | (608)266-6876 | kristin.hart@wisconsin.gov |  | 18-MMC-168 | 4911 | 221121 | Not Found | 06/30/2020 &nbsp;ACT | 09/01/2020 &nbsp;ACT | 2022-06-27 | 2022-09-16 | A | https://dnr.wi.gov/cias/am/amexternal/AM_DownloadObject.aspx?id=1011796 | Natural gas-fired power plant |  | Natural-Gas-Fired Combined-Cycle Turbine (P01) Start-Up and Shutdown (diesel) | 15.21 | Natural Gas | 0 |  | One Natural-Gas-Fired Siemens SGT6-8000H Combined-Cycle Turbine with Natural Gas-Fired Duct Burner and Diesel Fuel Oil Back-Up [Maximum continuous rating: 4,671 MMBtu/hr higher heating value (HHV) when combusting natural gas, 4,027 MMBtu/hr, HHV when combusting diesel fuel oil], | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1639929 | LB/START-UP |  | BACT-PSD |  | U | 0 | U | 409982 | LB/SHUTDOWN |  | 0 |  |  | 0 | 0 | N |  | Total start-up and shutdown emissions: 43,048 T/YR. (based on 42 start-ups and 42 shutdowns per year using diesel)
*MI-0445 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact Mark Mitchell at 517-582-5293 or at mitchellm7@michigan.gov. Thank you. | 75-16B | 4911 | 221112 | Not found | 08/20/2019 &nbsp;ACT | 11/26/2019 &nbsp;ACT | 2020-12-22 | 2020-12-23 | A |  | Natural gas combined cycle power plant |  | FGCTGHRSG | 15.21 | Natural gas | 3421 | MMBTU/H | 3421 MMBTU/H for each turbine 740 MMBTU/H for each duct burner for a combined throughput of 4161 MMBTU/H or 8322 MMBTU/H for both trains. Two combined-cycle natural gas-fired combustion turbine generators (CTGs) with Heat Recovery Steam Generators (HRSG) (EUCTGHRSG1 & EUCTGHRSG2 in FGCTGHRSG). The total hours for startup and shutdown for each train shall not exceed 500 hours per 12-month rolling time period. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices, inlet air conditioning, and the use of pipeline quality natural gas. | 1911481 | T/YR | 12-MO ROLLING TIME PERIOD; EACH CTGHRSG | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit above is 1,911,481 tons/year based upon a 12-month rolling time period as determined at the end of each calendar month. The limit applies to each CTGHRSG. The proposed permit also contains a 802 lb CO2 per MW-hour (lb/MWh) emission limit that serves as BACT due to energy efficiency, which is equivalent to a net heat rate of 6,855 Btu/kW-hr per 2x1 block and is more stringent than the required NSPS limit of the same units. The amine-based CCS technologies were used since these are generally considered to be the most feasible near-term deployable technology for possible future CO2 removal. CCS is assumed to be about 90 percent effective. Using the lowest capital cost range, the estimated capital cost for CCS for the proposed project is approximately $629,000,000. The cost of a pipeline to transport the CO2 was added to the result to estimate the total capital cost of the CO2 control system. The operating and maintenance and indirect operating costs were estimated to be around $53,000,000. Based on 90 percent CO2 removal and the control being applied to the facility-wide emissions, not just the CTG/HRSG trains, the resulting cost is estimated to be $30/ton and was not considered economically feasible.
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (South Plant): A combined cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/H (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/H (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR and an oxidation catalyst. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy efficiency measures and the use of a low carbon fuel (pipeline quality natural gas). | 1978297 | T/YR | 12-MO ROLLING TIME PERIOD | BACT-PSD |  | N | 0 | N | 806 | LB/MW-H | 12-OPERATING MONTH ROLL AVG BASIS | 0 |  |  | 0 | 0 | N |  | For emission limit 2 (806 LB/MW-H) it is based on a 12-operating month rolling average basis as determined at the end of each operating calendar month (basis is BACT & NSPS TTTT). Compliance is determined monthly at the end of the initial and each subsequent 12-operating month period. The first month of the initial compliance period is defined in 40 CFR 60.5525(c)(1)(i). The amine-based CCS technologies were used since these are generally considered to be the most feasible near-term deployable technology for possible future CO2 removal. CCS is assumed to be about 90 percent effective. Using the lowest capital cost range, the estimated capital cost for CCS for the proposed project is approximately $393 million, including the cost of a pipeline to transport the CO2 and the cost of the CO2 control system. The cost per ton was close to $100/ton, which was not considered economically feasible.
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (North Plant): A combined-cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | Nominal 500 MW electricity production. Turbine rating of 3,080 MMBTU/hr (HHV) and HRSG duct burner rating of 755 MMBTU/hr (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/hr (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy efficiency measures and the use of a low carbon fuel (pipeline quality natural gas). | 1978297 | T/YR | 12-MO ROLL TIME PERIOD | BACT-PSD |  | N | 0 | N | 806 | LB/MWH | 12- OPERATING MONTH ROLL AVG | 0 |  |  | 0 | 0 | N |  | Emission limit 2 is 806 LB/MWH based on 12-operating month rolling average basis as determined at the end of each operating calendar month. Compliance is determined monthly at the end of the initial and each subsequent 12-operating month period. The first month of the initial compliance period is defined in 40 CFR 60.5525(c)(1)(i). The amine-based CCS technologies were used since these are generally considered to be the most feasible near-term deployable technology for possible future CO2 removal. CCS is assumed to be about 90 percent effective. Using the lowest capital cost range, the estimated capital cost for CCS for the proposed project is approximately $393 million, including the cost of a pipeline to transport the CO2 and the cost of the CO2 control system. The cost per ton was close to $100/ton, which was not considered economically feasible.
MI-0451 | MEC NORTH, LLC | MARSHALL ENERGY CENTER, LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 9144682402 | WLADD@DEVELOPMENTSPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Janelle Trowhill, at 517-582-5312 or at TrowhillJ1@michigan.gov for technical questions regarding this permit. Thank you. | 167-17B | 4911 | 221112 | Not Found | 12/08/2021 &nbsp;ACT | 06/23/2022 &nbsp;ACT | 2022-12-21 | 2023-04-25 | A |  | Natural gas combined-cycle power plant (two plants: north and south). | The two plants (MEC North, LLC and MEC South, LLC) will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. | EUCTGHRSG (North Plant): A combined cycle natural gas fired combustion turbine generator with heat recovery steam generator | 15.21 | Natural gas | 3064 | MMBTU/H | Throughput Information: Nominal 500 MW electricity production. Turbine rating of 3,064 MMBTU/hr (HHV) and HRSG duct burner rating of 889 MMBTU/Hr (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,064 MMBTU/hr (HHV). The HRSG is equipped with a natural gas fired duct burner, with a maximum heat input rating of 889 MMBTU/hr (HHV) and rated at 874 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy efficiency measures and the use of a low carbon fuel (pipeline quality natural gas) | 2001019 | T/YR | 12-MO ROLLING TIME PERIOD | BACT-PSD | NSPS | N | 0 | N | 806 | LB/MWH | 12 OPERATING MONTH ROLLING AVG | 0 |  |  | 0 | 0 | N |  | Emission limit 1 above = 2,001,019 T/YR based on a 12-month rolling time period as determined at the end of each calendar month. The underlying applicable requirement is BACT. Emission limit 2 above = 806 lb/MWh and is based on a 12-operating month rolling average basis as determined at the end of each operating calendar month. The underlying applicable requirements are BACT and NSPS TTTT. Compliance is determined monthly at the end of the initial and each subsequent 12-operating month period. The first month of the initial compliance period is defined in 40 CFR 60.5525(c)(1)(i). The amine-based CCS technologies were used since these are generally considered to be the most feasible near-term deployable technology for possible future CO2 removal. CCS is assumed to be about 90 percent effective. Using the lowest capital cost range, the estimated capital cost for CCS for the proposed project is approximately $393 million, including the cost of a pipeline to transport the CO2 and the cost of the CO2 control system. The cost per ton was close to $100/ton, which was not considered economically feasible.
MI-0452 | MEC SOUTH, LLC | MARSHALL ENERGY CENTER, LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 9144682402 | WLADD@DEVELOPMENTSPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer, Janelle Trowhill at TrowhillJ1@michigan.gov or at 517-582-5312. Thank you. | 168-17B | 4911 | 221112 | Not Found | 12/08/2021 &nbsp;ACT | 06/23/2022 &nbsp;ACT | 2022-12-22 | 2023-04-25 | A |  | Natural gas combined cycle power plant (Two Plants: North and South) | The two plants (MEC North, LLC and MEC South, LLC) will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. | EUCTGHRSG (South Plant): A combined-cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 3064 | MMBTU/H | Nominal 500 MW electricity production. Turbine rating of 3064 MMBTU/H (HHV) and HRSG duct burner rating of 889 MMBTU/H (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,064 MMBTU/hr (HHV). The HRSG is equipped with a natural gas fired duct burner, with a maximum heat input rating of 889 MMBTU/hr (HHV) and rated at 874 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy Efficiency Measures and the use of a low carbon fuel (pipeline quality natural gas) | 2001019 | T/YR | 12-MO ROLLING TIME PERIOD | BACT-PSD |  | N | 0 | N | 806 | LB/MWH | 12 OPERATING MONTH ROLLING AVG | 0 |  |  | 0 | 0 | N |  | Emission limit 2 = 806 lb/MWh based on a 12-operating month rolling average basis as determined at the end of each operating calendar month. Compliance is determined monthly at the end of the initial and each subsequent 12 operating month period. The first month of the initial compliance period is defined in 40 CFR 60.5525(c)(1)(i). The amine-based CCS technologies were used since these are generally considered to be the most feasible near-term deployable technology for possible future CO2 removal. CCS is assumed to be about 90 percent effective. Using the lowest capital cost range, the estimated capital cost for CCS for the proposed project is approximately $393 million, including the cost of a pipeline to transport the CO2 and the cost of the CO2 control system. The cost per ton was close to $100/ton, which was not considered economically feasible.
MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2019-02-19 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | FGCTGHRSG (EUCTGHRSG1 &amp; EUCTGHRSG2) | 15.21 | Natural gas | 0 |  | Two (2) combined-cycle natural gas-fired combustion turbine generators, each with a heat recovery steam generator (CTGHRSG). Plant nominal 1,150 MW electricity production. Turbines are each rated at 3,658 MMBTU/H and HRSG duct burners are each rated at 800 MMBTU/H. The HRSGs are not capable of operating independently from the CTGs. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy efficiency measures | 2042773 | T/YR | 12-MO ROLLING TIME PERIOD; EACH UNIT | BACT-PSD | NSPS | N | 0 | N | 794 | LB/MW-H | 12-OPER MO ROLL AVG; EACH UNIT | 0 |  |  | 0 | 0 | N |  | The estimated cost of CCS is over $70,000,000 per year. This does not take into account the large parasitic load caused by a CCS system. For emission limit 2 above (794 LB/MW-H), compliance is determined monthly at the end of the initial and each subsequent 12-operating month period. The first month of the initial compliance period is defined in 40 CFR 60.5525(c)(1)(i).
MI-0455 | MIDLAND COGENERATION VENTURE LIMITED PARTNERSHIP | MIDLAND COGENERATION VENTURE LIMITED PARTNERSHIP | MIDLAND | MI | 46540 | USA | BRIAN VOKAL | 248-980-1139 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes at 517-648-6339 or at ByrnesM@michigan.gov. Thank you. | 2023-10-23 | 4911 | 221112 | Not found | 10/12/2022 &nbsp;ACT | 02/01/2023 &nbsp;ACT | 2023-05-15 | 2023-05-23 | B |  | Electric and steam generation |  | EUCTGHRSG1 | 15.21 | Natural gas | 4197.6 | MMBTU/H |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Low carbon fuel, good combustion practices, energy efficiency measures. | 2375313 | T/YR | 12-MO ROLLING TIME PERIOD | BACT-PSD |  | N | 0 | N | 1000 | LB/MWH | 12-OPERATING MONTH ROLLING AVG; NSPS LIM | 0 |  |  | 0 | 0 | N |  | Emission limit 2 is 1,000 lb/MWh gross energy output on a 12-operating month rolling average.
LA-0391 | MAGNOLIA POWER GENERATING STATION UNIT 1 | MAGNOLIA POWER LLC | IBERVILLE | LA | 70764 | USA | WILLIAM DAVIS | 609-250-7707 | LEE.DAVIS@KINDLE-ENERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Ms. Lori Pittman, (225)219-3180 | PSD-LA-839 | 4911 | 221112 | Not Found | 09/08/2020 &nbsp;ACT | 06/03/2022 &nbsp;ACT | 2023-03-02 | 2023-05-23 | A | https://edms.deq.louisiana.gov/app/doc/view?doc=13323738 | Magnolia Power LLC (Magnolia Power) is proposing to construct and operate a power plant, Magnolia Power Generating Station Unit 1, consisting of a natural gas-fired combined cycle gas turbine (CCGT Unit) in Iberville Parish, Louisiana. The CCGT Unit (EQT001), which includes a heat recovery steam generator (HRSG) equipped with duct burners, will have a predicted net nominal output of 730 megawatts (MW) |  | Combined Cycle Gas Turbine Startup and Shutdown | 15.21 | Natural Gas | 5081 | mm BTU/h | Startup and shutdown emissions from the combined cycle gas turbine. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices. | 2528349 | T/YR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | BACT limit is 2,528,340 tons/yr and includes emissions during normal operating mode.
LA-0331 | CALCASIEU PASS LNG PROJECT | VENTURE GLOBAL CALCASIEU PASS, LLC | CAMERON | LA | 70631 | USA | GRAHAM MCARTHUR | 202-759-6741 | GMCARTHUR@VGLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Ms. Mei Wu, (225)219-3180 | PDS-LA-805 | 4925 | 221210 | Not Found | 06/25/2018 &nbsp;ACT | 09/21/2018 &nbsp;ACT | 2019-02-14 | 2019-06-19 | A |  | New Liquefied Natural Gas (LNG) production, storage, and export terminal. | Application Received September 2, 2015. | Combined Cycle Combustion Turbines (CCCT1 to CCCT5) | 15.21 | Natural Gas | 921 | MM BTU/h |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Combust low carbon fuel gas and good combustion practices | 2602275 | T/YR | ANNUAL TOTAL | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Annual Total for 5 Combined Cycle Turbines
MI-0442 | THOMAS TOWNSHIP ENERGY, LLC | THOMAS TOWNSHIP ENERGY, LLC | SAGINAW | MI | 48626-9409 | USA | DAN EWAN | 312-582-1504 | DEWAN@INVENERGYLLC.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions, please contact the permit engineer, Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you! | 210-18 | 4911 | 221112 | Not Found | 06/10/2019 &nbsp;ACT | 08/21/2019 &nbsp;ACT | 2019-11-18 | 2021-08-09 | A |  | New power plant | Thomas Township Energy is proposing to install two combustion turbine generators (CTG). Each CTG is connected to a heat recovery steam generator (HRSG), together referred to as a CTGHRSG. To reduce emissions of nitrogen oxides (NOx), the high-efficiency CTGHRSGs will be equipped with dry low-NOx burners and selective catalytic reduction (SCR). To reduce the emissions of carbon monoxide (CO) and volatile organic compounds (VOCs), each CTGHRSG will be equipped with an oxidation catalyst. | FGCTGHRSG | 15.21 | Natural gas | 625 | MW | Two (2) combined-cycle natural gas-fired combustion turbine generators (CTGs), each with a heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG). Each CTGHRSG has a combined nominal 625 MW electricity production (ISO) and a maximum combined heat input rating of 4,200 MMBTU/hr (HHV). Each HRSG is equipped with a natural gas-fired duct burner with a maximum rating of 560 MMBTU/hr (HHV) (ISO) to provide heat for additional steam production. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy efficiency measures | 2739722 | T/YR | 12-MONTH ROLLING TIME PERIOD; EACH UNIT | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | CCS was ruled out as economically infeasible.
IL-0130 | JACKSON ENERGY CENTER | JACKSON GENERATION, LLC | WILL | IL | 60421 | USA | JAMES KIEFER | 847-908-2833 | JKEIFER@POWERUSA.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov |  | 17040013 | 4911 | 221112 | Not Found | 04/04/2017 &nbsp;ACT | 12/31/2018 &nbsp;ACT | 2019-07-23 | 2020-04-16 | A |  | The proposed facility is designed to generate baseload power. It will consist of two combined-cycle generating units, each with a combustion turbine and associated heat recovery steam generator (HRSG). The turbines would only burn natural gas. Other units include an auxiliary boiler, fuel heater, emergency engines, natural gas piping and components, circuit breakers and roadways | Additional pollutants: Sulfuric Acid Mist: 48 tons/year; GHG as CO2e: 4,752,085 tons/year | Combined-Cycle Combustion Turbine | 15.21 | Natural Gas | 3864 | mmBtu/hr | Combined-cycle combustion turbines with heat recovery steam generator (HRSG). Turbines will have inlet evaporative cooling systems to cool inlet air during warm weather to increase power output. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Equipment design and proper operation | 4733910 | TONS/YEAR | 12-MONTH ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | CO2 emissions of each turbine shall not exceed 1,000 lb/MWh of gross energy output, or, alternatively, 1,030 lb/MWh of net energy output on a 12-month rolling average basis.